## Table1
Master Question No | Country receiving Question | Topic | Page number | Question
1 | Bulgaria | 1 | 7 | Periodic safety review / re-evaluation of natural hazards (ENSREG recommendation 2.2): ENSREG underlined the importance of periodic safety review and the necessity to re-evaluate natural hazards and provisions at least every 10 years. The last seismic hazard assessment for the Kozloduy site was performed 1990-1992. Has a re-assessment of external hazards (seismic, flooding, extreme weather) been performed since that time? If yes, what are the results of these studies? If no, what are the plans for such re-assessments?
2 | Czech Republic | 1 | 10 | 1.1 Seismic upgrade of NPP Dukovany to 0.10g PGAH (ENSREG recommendation 3.1.1.1.1; Activity No. 1): The original level of the design basis earthquake for the NPP Dukovany is given by PGAH=0.06g based on an assessment in 1985. In order to meet IAEA's minimum seismic design requirements the level has been set to 0.10g in 1995. Although the site went through a PSR in 2006/2007 and a license extension, upgrading to 0.10g has not been completed at that time, and it was still ongoing during the Stress Tests. What is the time schedule expected by ČEZ to finalize the upgrade?
3 | Czech Republic | 1 | 12 | 1.2 Resistance of the Fire Brigade Buildings against severe natural events (ENSREG recommendation 3.1.1.1.6 and 3.1.1.1.14; Activity Nos. 2, 3, 84): Analyses of the robustness of the fire brigade buildings (Dukovany and Temelin) with respect to earthquake and severe weather are currently addressed. The topic appears important as the functionality of the on-site fire brigades is required for severe accident management. What is the time schedule to finalize the upgrade of the resilience of the fire brigades? What is the status of the interim solutions initiated in 2011 (storage of equipment in tents)?
4 | Czech Republic | 1 | 9 | 1.3 Periodic safety review / re-evaluation of natural hazards (ENSREG recommendation 2.3): ENSREG underlined the importance of periodic safety review and the necessity to re-evaluate natural hazards and provisions at least every 10 years. Do the Czech regulations require regular re-assessments of natural hazards in accordance with the ENSREG recommendation?
5 | Czech Republic | 1 | 11-12 | 1.4 Design basis and safety case for severe weather (ENSREG recommendation 3.1.1). ENSREG recommends to use a return frequency of 10-4 per annum for plant reviews/back-fitting with respect to external hazards safety cases. Have the loads from severe weather phenomena that correspond to these return frequencies been determined from appropriate hazard assessments? Have the correspondig loads been used to determine the back-fitting requirements for the NPPs Dukovany and Temelin?
6 | Czech Republic | 2 | 69 | Action 18, 19. What are the design basis for the implemented SBO DGs (seismic resistance, resistance against other external hazards, spectrum of sequences to be protected against)? Have the procedures for starting and connecting the SBO DGs to each safety bus been developed, verified, and tested? How long would it take to connect those SBO DGs to the essential loads?
7 | Czech Republic | 2 | 70 | Action 27, 32. Where will the indications from the SFP monitoring system be available (MCR, ECR)? How will a reliable power supply for the SFP monitoring systems and for PAMS be ensured?
8 | Czech Republic | 2 | 76 | Action 74. What were the results of the analysis of off-site power connections reinforcement? What are the proposed solutions (if any) and the schedule for their design, licensing and implementation?
9 | Czech Republic | 2 | 76 | Action 75. What were the results/conclusions of the batteries capacity real load test?
10 | Czech Republic | 3 | 7/73 | For ETE, stabilization of the molten core in case of a severe accident is to be achieved by ex-vessel cooling. According to the NAcP, this strategy is considered to be effective in terms of maintaining containment integrity. Implementation is to be completed by 2022. The implementation of ex-vessel cooling at ETE requires major back-fitting (e.g. establishment of a spilling area); the details of the design have yet to be elaborated. Are there any critical issues which might, upon closer consideration, put into question the feasibility of the strategy, or which might lead to delays in the implementation?
11 | Czech Republic | 3 | n/a | External RPV cooling (in-vessel retention, IVR) is being implemented at EDU, to be completed in 2015. Referring to the same reactor type (VVER-440/213), the rapporteur’s report for Slovakia stated 2013: Analyses of consequences of IVR failure and the preservation of containment integrity in case of a severe accident are on-going and were emphasized to be important in the discussion at the Workshop. Such analyses are not mentioned in the Czech NAcP. Are they also performed for EDU, and if so, jointly with the analyses mentioned for Slovakia? Are results already available, were any additional measures planned as a consequence?
12 | France | 1 |  | Periodic safety review / re-evaluation of natural hazards (ENSREG recommendation 2.2): ENSREG underlined the importance of periodic safety review and the necessity to re-evaluate natural hazards and provisions at least every 10 years. Have re-assessment of external hazards (seismic, flooding, extreme weather) been performed in the last PSRs? If yes, did they change the design basis hazards? If no, what are the plans for such re-assessments?
13 | France | 1 | 12 | Procedure proposed by EDF for probabilistic seismic safety studies: The methodologies of probabilistic seismic hazard assessments are generally well established. What are the key characteristics of the apparently novel probabilistic procedure developed by EDF to be ued in PSR? Are seismic hazard assessments part of the third safety reviews of the 1300 MWe plant units?
14 | France | 3 | 24, 72 | The functional perimeter of the hardened safety core, types and levels of initiating events, conditions of implementation of the hardened safety core and other important items were to be decided at a meeting of the Advisory Committee of Experts, on 13 December 2012. According to the NAcP, it was concluded after this meeting that further work regarding the functional perimeter and the design hypotheses was required; and ASN issued complementary prescriptions through a set of resolutions on 21 January 2014. This additional step was not foreseen in the NAcP of 2012. Nevertheless, the schedule for the implementation of the hardened safety core has not been changed. Is the schedule as presented at p. 72 indicative or obligatory? Are delays expected?
15 | Germany | 1 | 68 | Periodic Safety Reviews / Re-assessment of external hazards (ENSREG recommendation 2.2; No. E-2): ENSREG recommends to re-evaluate natural hazards regularly but at least every 10 years. Have external external hazards (seismic, flooding, extreme weather) been re-assessed in the last PSRs?
16 | Germany | 1 |  | Seismic design basis / minimum level of 0.1g (ENSREG recommendation 3.1.1.) The previous version of the German NAcP adressed the assessment of the seismic robustness of the NPPs KBR, KWG, KKG and KKI. For these NPPs the design basis does not meet the minimum level of 0.1g. Have these assessments been completed? If yes, what is the outcome of the analyses?
17 | Germany | 1 | 18, 75 | PSR / review of seismic hazard and design for plants which remain in operation (No. E-49; National recommendation N-14): Recommendation E-49 suggests that the next round of PSRs might be used to review the seismic hazard and design basis for all plants, which remain in operation. Such re-assessments are regarded to be particularly be important for the Rheine Graben region (NPPs KKP, GKN). Are seismic hazard / seismic safety reviews being planned or in progress? If yes applicable: what is the status of these assessments?
18 | Germany | 1 | 7 | RSK made a statement on extreme weather conditions on 06 November 2013, which is referred to several times in the NAcP. In this statement, RSK lists 10 weather conditions for which additional analyses are required (e.g. freezing rain/ice storm/snow storm; extremely low air temperature; extremely low water temperature and level for prolonged periods). These additional analyses are not mentioned explicitly in the NAcP. Are they covered by activities listed in the NAcP? If so, by which activities? If not, what is the status of these additional analyses?
19 | Germany | 2 | 22, 37, 45, 51 | For a number of actions related to AC power supply, e.g. "obtaining and providing two mobile diesel generators at the site" (GKN II action 2, KKP 2 action 2) or "Statement on the maintenance of the electricity supply on the basis of a safety analysis" (GKN I action 1, KKP 1 action 1), it is stated that the action is implemented at the plant but that further information is required (by the BW authority), and the deadline for this has been extended from 2013 to 2015. What are the issues in the implementation of these actions that are further reviewed by the BW authority and what are the reasons for extending the deadlines?
20 | Germany | 2 | 25, 31, 34, 42 | What were the conclusions of the review of the requirements for the containment venting system with consideration of SBO conditions, adverse radiological conditions and the effectiveness following external natural design hazards conducted by KKG, KKI-2 and KWG (action 9), and what optimisation measures were found necessary and implemented? What is the status of completion of the same review and optimisation for KBR (action 9), what were the reasons for extending the deadline for implementation?
21 | Germany | 2 | 23, 38, 46, 53 | GKN II No. 14, KKP2 No.13, GKN I No.11, KKP1 No.12. What were the operator's results of the additional estimates of the safety margins of auxiliary service water and ventilation under extreme weather conditions (with a recurrence frequency of 10-4/a)?
22 | Germany | 2 | 25, 31, 35, 43 | KBR No.12, KKG No.12, KKI 2 No.12, KWG No.12. What were the results of the examination of the need to be able to initiate additional accident management measures from the remote shutdown and control station?
23 | Germany | 3 | 8 | Studies and discussions of RSK on the topics of “crash of commercial airliner” and “hydrogen release in rooms outside the containment” have not yet been concluded. When will RSK issue statements on these two topics?
24 | Germany | General | 23/24 37-39 | For GKN II and KKP 2, there are seven activities which are listed as "in progress", with completion in 2014 or 2015. The completion dates for these activities were 2012/2013 in the NAcP of 2012. For the other PWRs in operation, there are at most 2 activities which have been delayed and are still in progress. According to the NAcP, all data referring to GKN II and KKP 2 correspond to the Action plan of the state of Baden-Württemberg (BW). It appears that there are considerably more delays in the state of BW. What is the reason?
25 | Germany | General |  | Note: The plant specific action plans (Table 5-2) have been significantly modified, with new actions added as compared to the 2012 version of the NAcP. While it can be deducted that the new actions are the result of RSK statements/recommendations issued after 2012, no explanation or justification is provided in the NAcP 2014. The new actions were inserted in between existing ones, all actions renumbered, making the tracing of progress and changes since 2012 very difficult.
26 | Hungary | 1 | 11, 39 | Secondary earthquake effects / Soil liquefaction (ENSREG recommendation 3.1.2, Task 4, 5): Accordingly liquefaction and ground settlement might occur due to seismic shaking at acceleration ranges slightly exceeding the design basis. What types of the safety relevant structures, systems and components are endangered by liquefaction, and which measures are envisaged to increase the robustness of these SSCs?
27 | Hungary | 3 | 21, 50 | External RPV cooling (in-vessel retention, IVR) has been implemented at Paks NPP, completed in 2014. In this context, the NAcP states: No further action is necessary. Referring to the same reactor type (VVER-440/213), the rapporteur’s report for Slovakia stated 2013: Analyses of consequences of IVR failure and the preservation of containment integrity in case of a severe accident are on-going and were emphasized to be important in the discussion at the Workshop. Such analyses are not mentioned in the Hungarian NAcP. Have they already been performed for Paks, and if so, jointly with the analyses mentioned for Slovakia? What is the basis for stating that no further action is necessary?
28 | Hungary | General | 62-69 | According to the NAcP, a small number of tasks are expected to be delayed. The public procurement procedure is mentioned as one of the reason for delays in several cases (1.9, 1.11, 1.28). Presumably, public procurement procedures are/were required for many tasks, and in most cases did not produce delays – why did they lead to delays in some?
29 | Romania | 1 | 4 | Hazard frequency: The design bases for extreme weather phenomena for Cernavoda are based on design basis events with probabilities of 10-3/year. This is not in agreement with ENSREG recommendation 3.1.1 requesting a return frequency of 10-4/year for external hazards safety cases. Have the corresponding hazard values for exceedence frequencies of 10-4 been determined? If yes, how do these values change the design basis event?
30 | Romania | 1 | 33 | Periodic safety review / re-evaluation of natural hazards (ENSREG recommendation 2.2): ENSREG underlined the importance of periodic safety review and the necessity to re-evaluate natural hazards and provisions at least every 10 years. Seismic hazards have been evaluated in 2004 giving a design basis PGA=0.2g for an exceeence probabilty of 10-3. Has a re-assessment of seismic hazards been performed in the last (or current) PSR? If yes, what are the results for the exceedence probability of 10-4?
31 | Slovak Republic | 1 |  | Periodic Safety Reviews / Re-assessment of external hazards (ENSREG recommendation 2.2): The latest seismic hazard review for the EBO site was apparently done in 1997. ENSREG suggests to re-evaluate natural hazards at least every 10 years. Has a re-assessment of seismic hazards been performed during the last PSR in 2008? If no, what are the plans for such assessments?
32 | Slovak Republic | 1 | 14 | ID 1. Periodic safety review / Re-assessment of natural risk (ENSREG recommendation 2.2): UJD SR issued the Regulation No. 33/2012 on that topic. Does this regulation require a full re-assessment of natural hazards, or only a check of the reliability of preivous assessments?
33 | Slovak Republic | 1 | 14 | ID 1. Periodic safety review / Re-assessment of natural risk (ENSREG recommendation 2.2): UJD SR issued the Regulation No. 33/2012 on that topic. Does the schedule of the next PSR for EBO 3&4 include a full re-assessment of seismic hazard, which appears desirable due to novel geological data from near-regional active faults?
34 | Slovak Republic | 1 | 15-16 | ID 4. What are the results of the overall assessment of impacts of extreme meteorological events on safety and reliability of EBO civil structures? Are there any improvement measures envisaged? What are those and what is the envisaged implementation schedule?
35 | Slovak Republic | 1 | 16 | ID 5. Hazard frequency related to seismicity (EC Communication Annex): Assessments of safety margins for EBO 3+4 during the European Stress Tests partly revealed small safety margins beyond the design basis. Consequential seismic margin assessment for the NPPs Bohunice and Mohovce used a "GIP method". Please explain this approach. What are the results of seismic margin assessment and which actions have been identified to increase safety margins?
36 | Slovak Republic | 1 | 16 | ID 5. Hazard frequency related to seismicity (EC Communication Annex): Did the task incluide or schedule a re-assessment of seismic hazard as indicated by the wording of the recommendation? If yes, what are the results/schedules for a hazard re-assessment?
37 | Slovak Republic | 2 | 34 | ID 25. What are the additional measures to be implemented for the enhancement of ventilation capacity during SBO? What is the timeline for their implementation?
38 | Slovak Republic | 3 | 53 | ID 38. What are the additional measures (in which SAM areas) envisaged following the targeted self-assessment in the area of civil accidents according to WANO methodology performed at EBO and EMO? What is the timeline envisaged for their implementation?
39 | Slovak Republic | 2, 3 | 36-63 | The following recommendation is important for a number of activities: To analyse the SAM project from the viewpoint of severe accident management at multi units (all) at the same time (...); to modify the SAM project, if needed, so that sufficient measures can be implemented. To prepare a plan of implementation of additional measures for extension of the SAM project (…). It is quoted in activities 27bis, 32, 34, 39, 41, 44, 48 and 52; and also referred to in activity 43. These activities were planned to be completed by 31/12/2014. However, according to the NAcP, only the analyses have been completed so far, and are at present evaluated by the licensee. The plan of implementation of measures is dependent on the results of these evaluations. What is the schedule for the evaluations, when is completion of the plans for implementation of measures to be expected?
40 | Slovak Republic | 3 | n/a | The rapporteur’s report for Slovakia from the 2013 NAcP Peer Review Workshop mentions the implementation of in-vessel retention which is already completed as a good practice. The report also states: Analyses of consequences of IVR failure and the preservation of containment integrity in case of a severe accident are on-going and were emphasized to be important in the discussion at the Workshop. Analyses or any other activities related to the consequences of IVR failure are not mentioned in the NAcP. What is the status of these activities? Is this work performed jointly with other countries with VVER-440/213s? Are results already available, were any additional measures planned as a consequence?
41 | Slovenia | 1 | 7 | Safety Upgrade Program (SUP / DEC analysis): The seismic hazard for Krško was determined with PGA=0.56g for a non-exceedence probability 10-4 per year (2004). The NAcP explains that a set of DEC (Design Extension Conditions) has been derived that includes an extended design condition seismic value of PGA=0.6g for earthquake. This value is extremely close to the updated design basis event (0.56g). What is the reason to select the extremely small safety margin of 0.04g for DEC analysis?
42 | Slovenia | 1 | A-6 | Periodic Safety Reviews / Re-assessment of external hazards (ENSREG recommendation 2.2; No. 102; No. 409): The latest seismic hazard review for the Krško site was apparently completed in 2004, completion of the latest assessments of meteorological hazards are not mentioned. ENSREG suggests to re-evaluate natural hazards at least every 10 years. Has a re-assessment of external hazards (seismic, extreme weather) been performed since 2004? If no, what are the plans for such assessments?
43 | Slovenia | 1 | A-36 | Confirmation of seismic hazards every 10 years / Address any new and significant information (NRC Tier 3; No 419): Recent geological and paleoseismological investigations of the near-site area (Krsko II siting) revealed significant new seismotectonic data and evidence for a capable fault (Libna fault) in the site vicinity. Did these data trigger a re-assessment of seismic hazard? If yes, what are the results the assessment? If no, what is the schedule for preparing a novel hazard assessment?
44 | Slovenia | 1 | A-15 | Peer reviews of external hazards (KJV-Topic #1: No. 204): Does SNSA intend to invite a peer review mission to reassess seismic hazard? If yes, what could be the framework of the reassessment?
45 | Slovenia | 2 | 14 | Have compensatory measures for coping with design extension conditions been required considering the delay in the implementation of SUP (new deadline (2018) approved by SNSA, previous deadline being 2016)?
46 | Slovenia | 2 | 15 | What will happen if, after the financial viability study, a decision is taken not to implement the "BB2 project"?
47 | Slovenia | 3 | 15 | Phase 3 of the Safety Upgrade Program (SUP) for Krško NPP includes the installation of hardware very important for safety (e.g. installation of an alternative ultimate heat sink, installation of additional pumps for injecting into steam generators, reactor coolant system and spent fuel pool). So far, there is no agreement with the licensee, concerning the implementation of these measures; and hence, no deadline. Does SNSA consider the measures of phase 3 of the SUP as indispensable? What is the further procedure, regarding these measures?
48 | Slovenia | General | 18/19 | Nuclear safety infrastructure needs more political support. In particular, the NAcP mentions the difficult situation regarding financing. Does this concern mainly SNSA and their technical support; or also the licensee? There are delays in the implementation of the Safety Upgrade Program (SUP) for Krško NPP. Is the situation of the nuclear safety infrastructure one of the reasons for the delays?
49 | Switzerland | 1 | 8-9 | 1.1 Periodic safety review / re-evaluation of natural hazards (ENSREG recommendation 2.2): ENSI has issued a new regulatory guidline ENSI-A03 "Periodic Safety of Nuclear Power Plants". Does this guide reuire regular updates of the assesments of natural hazards?
50 | Switzerland | 1 | 8-9 | 1.2 Early warning notification (ENSREG recommendation 3.1.4): In the Stress Tests the adequacy of the design basis for extreme weather phenomena with the regulatory requirement (exceedence probability less than 10-4/year) has not been demonstrated for all cases. The Swiss NAcP states that ENSI requeted the safety cases for extreme weather conditions to be updated by the operators, and that updated hazards for extreme weather were sumitted to ENSI in 2014. Do the new hazard assessments and safety cases account for the requirement to consider design basis events with exceedence probabilities of less than 10-4/year?
51 | Switzerland | 1 | 11 | 1.3 Hazard frequency (ENSREG recommendation 3.1.1): During the Stress Tests ENSI announced that the seismic safety of the Swiss NPPs should be reasessed in the Pegasos Refinement Project and that the results of the seismic hazard update could be expected 2012. The results were still under ENSI's review in 2014. What kinds of novel site-specific data have been acquired in framework of the Pegasos Refinement Project? What are the updated site-specific hazard levels in terms of ground motion parameters for the Swiss nuclear sites?
52 | Switzerland | 1 | 11 | 1.4 Hazard frequency (ENSREG recommendation 3.1.1): In 2014 ENSI was reviewing the seismic hazard results for the Swiss NPPs obtained by the Pegasos Refinement Project. Depending on the outcome/availability of this review: What is the time schedule for demonstrating seismic safety of the Swiss NPPs with respect to the novel hazard values?
53 | Switzerland | 1 | 11-12 | 1.5 Secondary effects of earthquakes (ENSREG recommendatoin 3.1.2): In 2013 the Mühleberg NPP started a program for reinforcing the upstream Wohlensee dam. What ground motion hazards (10-4 per year occurrence probability) are expected for the dam sites upstream of KKM according to the recent seismic hazard reasessement programs? Are these ground motion values enveloped by the reinforcement of the dam?
54 | Switzerland | 2 | 15 | 2.1 Alternate Cooling and Heat Sink. "The Mühleberg NPP submitted a proposal of alternative measures for a diverse ultimate heat sink taking into account its limited remaining operating lifetime. In its evaluation (currently in draft form) ENSI approved the proposed concept for the diverse ultimate heat sink, which has to be implemented by the Mühleberg NPP by 2015." What is the proposed concept for alternative measures for diverse UHS at Muehleberg NPP?
55 | Switzerland | 2 | 15 | 2.2 AC Power Supplies. The 2012 Swiss NAcP stated that at Beznau "a large project is going on to enhance the safety layer 4 (four emergency diesel generators, two for each plant unit, replacing hydro‐generators that are not seismically qualified)." What is the status of implementation of this project?
56 | Switzerland | 2 | 16 | 2.3 DC Power Supplies. The Swiss 2012 NAcP stated that "Particular improvements have been planned which will be realised, and some are in the phase of investigation." A followup on these is not presented in the 2014 NAcP. What improvements have been planned and which have been realised?
57 | Switzerland | 2 | 17 | 2.7 Reactor Coolant Pump Seals. The Swiss 2012 NAcP stated that a robust RCP seal water system is planned to be installed at Beznau NPP by 2014. The 2014 NacP gives an exteded deadline for this action - 2015 outage. What is the reason for the delay in implementation?
58 | Switzerland | 2 | 18/19 | 2.10 Spent Fuel Pool. The Swiss 2014 NAcP states that "Because of other major backfitting measures started before Fukushima as well as some difficulties in the procurement of the necessary nuclear-grade components, this project is delayed. ENSI accepted a final postponement until 2017 under the condition that compensatory measures be taken, which the Beznau NPP has already complied to." What are the compensatory measures taken by Beznau NPP to protect the SFP building structure in case of beyond design basis accidents, until the finalization in 2017 of the backfitting of seismically robust SFP cooling system?
59 | Switzerland | 2 | 18/19 | 2.10 Spent Fuel Pool. The Swiss 2012 NAcP stated that ENSI ordered "to backfit seismically robust SFP cooling systems in the older NPPs. Correspondingly, backfitting projects are ongoing at the Beznau and Mühleberg NPPs." An update on the status of the action is not given in the 2014 NaCP. What is the deadline and the status of the implementation of backfitting measures at Muehleberg NPP?
60 | Switzerland | 3 | 26/44 | The open point OP6-1 refers to the presence of hydrogen in unexpected places on p. 26, to deployment strategies for the containment venting system on p. 44. These are two different topics (although they are somewhat related). Could an explanation of OP6-1 be provided? According to the NAcP, the licensees have submitted studies requested by ENSI in 2014, on hydrogen migration in the containment as well as to buildings outside the containment. ENSI is currently reviewing these studies. Preliminary results of the review indicate a need for back-fitting. What is the further schedule for this activity, when can implementation of back-fitting measures be expected?
61 | Switzerland | 3 | 10/44 | The open point OP6-2 refers to the issue of restoring containment integrity during shutdown in the case of total SBO. ENSI currently reviews reports of related studies which were submitted by the operators in October 2014. What is the further schedule for this activity, when can final results and, if applicable, implementation of back-fitting measures be expected?
62 | UK | 1 | 46 | Periodic safety review / re-evaluation of natural hazards (ENSREG recommendation 2.2): ENSREG underlined the importance of periodic safety review and the necessity to re-evaluate natural hazards and provisions at least every 10 years. Seismic hazards have mostly been assessed in the 1980ies with updates in the 1990ies. Have re-assessment of seismic hazards been performed in the latest PSRs?
63 | Ukraine | General | 3 | It is stated that the schedule for a series of safety improvement measures has been extended; one of the reasons being the decision made by the operating organization to shut down the power units when their design-basis life expires in order to implement all safety improvement measures needed to justify long-term operation. This statement is not completely clear. Does it mean that originally, improvements were to be implemented stepwise during refuelling shut-downs and (as far as possible) during operation of the plants, whereas now all improvements are to be implemented during one extended phase of shut-down?
64 | Slovenia | Topic 3 | Page 5 | Reference: Table 1: Implemented short-term improvements in the Krško NPP – accelerated B.5.b requirements: ….Procurement of Tractor “Arion 630C” 103 kW, with additional equipment, e.g, air compressor, fork lift, equipment for ploughing (removing debris, etc.) - to be used as means of transportation of different equipment (e.g. portable diesel generators, pumps, barrels of oil, etc.), for transferring the fuel between tanks/barrels and equipment, for ploughing/clearing way at the site, etc. Questions: 1) Where is/will be located this Tractor ? 2) Are there any specially trained drivers? 3) How is organized the drivers availability round the clock?
65 | Slovenia | Topic 2 | Page 10 | Reference: Table 4, item 1.3 says: “Installation of alternative ultimate heat sink”. in progress, finalization after 2018; Question: What equipment is considered to be installed as alternative ultimate heat sink ?
66 | Netherlands | Topic 3 | Page 60 | Reference: 4.0 f Vendor ........“Areva NP maintains an emergency support organisation for its customers. KCB is one of the customers that has a contract in place for support during and after incidents, with the emphasis on beyond design-base incidents including core melt scenarios. In both Areva NP crisis centres (Erlangen and Offenbach) real-time KCB process information can be displayed and all necessary documentation is kept current and available on a dedicated computer.” Questions: 1) Have Areva NP crisis centres direct connection with KCB that delivers the critical parameters of the NPP in real time? 2) Have you used the services of that Areva centres so far, including for training?
67 | Spain | Topic 3 | Page 19 | Reference: Item 4.1.2 Progress in the implementation and updating of the NAcP: • „In early 2014 the nuclear utilities completed the implementation of the new Emergency Support Centre (ESC), which is capable of supplying trained personnel and equipment to any Spanish nuclear power plant in less than 24 hours.“ Questions: 1) How and where is the personnel from the ESC trained ? 2) What is the number and qualification of this personnel ? 3) What type of equipment is envisaged to be delivered to NPPs and how?
68 | Spain | Topic 3 | Page A4 | Reference: Table A-1.1, Type I14, Requirement: Study of technology alternatives for the filtered containment venting system – study completed and implementation on site is on going by 31/12/16 Question: What is the chosen alternative for the filtered containment venting system that is being implemented?
69 | Spain | Topic 2 | Page A2 | Reference: Table A-1.1, Type I4, Requirement: Implementation of new equipment (fixed or portable) to cope with prolonged SBO conditions (including to replace primary circuit inventory), completed 2014 Questions: 1) What type new equipment has been implemented “to replace primary circuit inventory”? 2) Do you mean replacement of primary circuit components or refilling the primary circuit and recovery of coolant inventory?
70 | Czech Republic | Topic 3 | Page 44/45 Page 47/48 Page 48 | Reference: Containment overpressure protection; item 3.3.2.2 Recommendations from ENSREG Country Peer Review; item 3.3.2.2.3 Filtered venting system; item 3.3.2.4 ENSREG -Follow-up fact finding site visit NPP Temelin; item 3.3.2.4.1 Selection of appropriate strategy to protect containment against overpressure (filtered venting system is one option). Question: What is the selected strategy to prevent long-term containment over pressurization as a result of accumulation of non-condensable gases and decay heat generated inside the containment in case of a severe accident and/or extended SBO conditions (for both plants)?
71 | Czech Republic | Topic 3 | Page 33 Page 58/59 | Reference: ENSREG Recommendation 3.2.9 Main and Emergency Control Rooms: Habitability of control rooms/emergency centres under DEC conditions; ENSREG Recommendation 3.3.16 Severe Accident Studies: 3.3.16.4 Radiological conditions on the site and associated provisions necessary to ensure MCR and ECR habitability as well as the feasibility of AM measures in severe accident conditions, multi-unit accidents, containment Questions: 1) What are the main outcomes of the analyses of the radiation conditions and habitability of the MCR/ECR during severe accidents, completed in 2013? 2) Are there any safety improvement actions that need to be taken as a result of these analyses (for both plants)?
72 | Czech Republic | Topic 2 | Page 69 | Reference: Action 16 for Temelin NPP: Provision of back-up coolant supply into depressurised reactor and storage pools with additional and sufficient sources of coolant. Questions: 1) What is the additional and sufficient source of coolant used for the back-up supply into depressurised reactor and storage pools? 2) Where is the new pipeline connected to the reactor pressure boundary?
73 | Germany | All topics | Pages 9-11 | Reference: Chapter 3: Studies at international level In this chapter on several places is stated that “International and national findings have been joint together”. Question: Are there any actions/measures in the NAcP influenced by or proceeding from decisions, studies or findings obtained from other countries’ activities/measures?
74 | Belgium | Topic 1 | Page 14 | Reference Item.3.1.3. Extreme weather conditions. “... At Doel, the licensee finalized its re-еvaluation of the impact of heavy rains in 2014. The regulatory body is currently assessing these studies for Doel. At Tihange, important improvements of the sewer systems have to be realized by the licensee during 2015. The related project has been presented to the regulatory body.” Questions: 1) Please provide information, if already available, on the main results of the performed re-evaluation of the heavy rains impact for Doel NPP? 2) Are there any corrective actions resulting from the performed re-evaluation? 3) Could you please explain in principle the improvement of the sewer systems at Tihange NPP?
75 | Belgium | Topic 2 | Page 17 | Reference Item. 3.2.1. Power and Water Supply „At Doel, the CSBO strategy is already being implemented. Several actions have been realized by the licensee. In this framework, the delivery of the requested mobile means has begun in 2014 and will finish in 2015. The mobile pumps have already been delivered and the mobile generators are ordered. Nevertheless, some other mobile equipment were temporarily available on the site to assume the needed safety functions since 2013.” Questions: 1) How many mobile diesel generators have to be procured? Is it envisaged to be provided possibilities for simultaneous use at all four units? 2) Please, explain the protection concept of the new diesel generators storage, including the severity of the natural hazards they will be able to withstand.
76 | Belgium | Topic 2 | Page 19 | Reference: Item. 3.2.2. Loss of primary and alternate ultimate heat sink (UHS). „Moreover, the regulatory body has requested the evaluation of two configurations for the spent fuel pools: the configuration with a fuel assembly handled in the reactor pool during a CSBO and the configuration with the loss of water inventory in the spent fuel pools. The first evaluation will be finalized in 2015 while the second one has been finalized in early 2014.” Questions: 1) What are the outcomes from the evaluation of the configuration with the loss of water inventory in the pools? 2) Are there any corrective actions resulting from the performed evaluation?
77 | Ukraine | Topic 2 | Page 12 | Reference: Item 5. SFP makeup and cooling in long-term station blackout conditions. Question: Would you please explain how do you provide make up and cooling of spent fuel pools using the SFP cooldown system for normal operation in case of loss of power supply and impossibility to open the pneumatic isolation valves?
78 | Ukraine | Topic 3 | Page 16 | Reference Item 22. Analysis of the need and possibility to qualify power unit components that may be involved in severe accident management for harsh environments. Questions: 1) What are the main results of the analysis with respect to the need and possibility to qualify components for harsh environment? 2) Are there any corrective measures proposed?
79 | Switzerland | Topic 3 | Page 24 | Reference: 3.4 Enhancement of Severe Accident Management Guidelines ENSREG recommendation 3.3.4: The enhancement of SAMGs taking into account additional scenarios, including, a significantly damaged infrastructure, including the disruption of plant level, corporate-level and national-level communication, long-duration accidents (several days) and accidents affecting multiple units and nearby industrial facilities at the same time. Question: What additional scenarios were addressed to improve SAMGs taking into account the specificity of the location of nuclear power plants?
80 | Switzerland | Topic 3 | Page 24 | Reference: 3.5 SAMG Validation ENSREG recommendation 3.3.5: The validation of the enhanced SAMGs. Questions: The text makes clear that SAMGs are kept up to date, but does not give any information on their validation. What is the process of validation of SAMG following an update? Please, explain whether it incorporates engineering judgment and use of severe accidents simulator.
81 | Switzerland | Topic 3 | Page 26 | Reference: 3.10 Presence of Hydrogen in Unexpected Places ENSREG recommendation 3.3.10: The preparation for the potential for migration of hydrogen, with adequate countermeasures, into spaces beyond where it is produced in the primary containment, as well as hydrogen production in SFPs. Questions: Please, explain whether the PARs will have the capacity for recombination of the hydrogen, generated at all phases of the severe accident (in-vessel, ex-vessel and etc.), including the hydrogen, generated by the fuel melting in SFP.
82 | Sweden | Topic 3 | Page 48 | Reference: T3.LA.8 Accident management programmes ENSREG recommendation 3.3.8. To consider the extension of existing SAMGs to all plant states (full and low-power, shutdown), including accidents initiated in SFPs. Questions: In the report is mentioned that “A review of the instructions has been carried out for all utilities. Some changes have been implemented based on the findings…..”. Please, specify whether the changes include also their extension to cover all plant states (full, low power and shutdown) and SFP accidents?
83 | Sweden | Topic 3 | Page 50 | Reference: T3.LA.19 Common system for filtered containment venting ENSREG recommendation 3.3.1: The incorporation of the WENRA reference levels related to severe accident management (SAM) into their national legal frameworks, and ensure their implementation in the installations as soon as possible. This would include: • Containment overpressure protection - Containment venting via the filters designed for severe accident conditions. Questions: How the actions in Emergency Operating Procedures and/or SAMGs are organized in case of simultaneous severe core damages of two reactors at Oskarshamn NPP, considering the common venting system(and its potential unavailability)? Is the capacity of Common venting system enough to cope with radioactive releases, generated by both units?
84 | Hungary | Topic 3 | Page 50 | Reference: Task 30 Containment overpressure protection Paks NPP prepared the concept for the implementation, which recommends the installation of an active cooling system Question: What is the final concept to prevent long-term over pressurization resulting from accumulation of non-condensable gases and decay heat generated in the containment in case of a severe accident and/or extended SBO conditions?
85 | Hungary | Topic 3 | Page 68 | Reference: On-site emergency centre Task 47 … A nuclear emergency response centre resistant to earthquakes of a peak ground acceleration higher than design basis earthquake shall be established Task 49 A Backup Command Centre that complies with protection requirements and is equivalent with the Protected Command Centre in terms of management and communication shall be established. Questions: 1) Are the ‘nuclear emergency response centre’ (Task 47) and the ‘Backup Command Centre’ (Task49) planned as a different type of facilities? If yes, please explain shortly the difference. 2) What are the ‘protection requirements’ that the Backup Command Centre will comply with? 3) Is the multi-unit approach considered in the design of the facility/facilities?
86 | Belgium | 1 | 7 (sec. 3.1.1) | It is stated that for the Tihange NPP there is no definitive conclusion on the adequacy of the design basis earthquake (DBE) yet and that nevertheless, the Safety Margin Assessment (SMA) performed during the stress test has demonstrated that the equipment is more robust than required by the DBE. If the current DBE is inadequate, is it planned to review the SMA?
87 | Belgium | 1 | 8 (sec. 3.1.1) | Regarding the compliance of the seismic qualification of the refueling water storage tank (RWST) of the Doel NPP it is stated that it is possible that the regulatory body will require checking this qualification as part of the LTO requirements. Will it be possible to accept LTO without demonstration of the seismic qualification of the RWST?
88 | Belgium | 2 | 16 (sec. 3.2) | It is stated that there are 19 emergency diesel generators (EDGs) in total for the Doel NPP. It would be appreciated if the number of EDG for every unit could be specified. How long does the stored diesel fuel last in case of a postulated demand?
89 | Belgium | 2 | 17 (sec. 3.2.1) | It is stated in the report that the construction of a new high voltage lines across the Meuse river was judged as unrealistic by ELIA. Is there any alternative plan with respect to this issue?
90 | Belgium | 2 | 17 (sec.3.2.1) | Is it ensured that ELIA keeps enough resources to realise necessary reconstruction work for NPPs power supply?
91 | Belgium | 3 | 23 (sec. 3.3.3) | The report states: “In addition, …, the study [that] shows that there is no explosion risk due to the accumulation of hydrogen in the Spent Fuel Pool buildings of the NPP`s, is still under assessment by the regulatory body.” However, the previous Action plan from 2012 states under the Additional Topics section on page 2 of 9 topic no.9 “Recommendations, Requirements from other national reviews “: “Regardless of the outcome of the assessment of the residual risk of hydrogen generation and accumulation in the spent fuel pool buildings, the installation of PARs should be considered.” Could you please comment on the question, if it is still planned to install PARs in the vicinity of the SFP?
92 | Belgium | 3 | 23 (sec. 3.3.3) | The report states: “The follow-up of R&D activities … is planned to be continuously carried out.” What are the criteria for a decision about an emergency system that injects water into the reactor pit in case of a nuclear meltdown and what is the time scale of the planned investigations depending on the R&D activities?
93 | Belgium | General |  | No information was found regarding the ENSREG-Recommendations 3.1.4, 3.1.5, 3.1.6. Please provide more information about the status of the implementation of these recommendations.
94 | Belgium | General |  | Why have the topic areas 4 - 6 of the 2nd Extraordinary Meeting of Contracting Parties to the Convention on Nuclear Safety (CNS), i.e. National Organization, Emergency Preparedness and Post-Accident Management, and International Cooperation, not been addressed in the report of Belgium?
95 | Czech Republic | 2 | 69 (sec. 6) | “Implementation of alternative measures to ensure long term DC power supply ….” (in progress 2012 – 2016). Can you provide more information on the measures that are being implemented?
96 | Czech Republic | 2 | 76 (sec. 3.2.2.3.2) | The status of Action No. 74 is shown as “finished (analysis 2013, modifications (if needed) 2015)”. Can you provide information on the results of the analysis? Has a need for modifications been identified and if so, have the modifications been implemented?
97 | Czech Republic | 3 | 6-8 | Action 49 envisages the completion of analysis, the proposal of a strategy and the schedule for implementation of measures for preservation of the long-term containment integrity and consequently measures to stabilize core melt. This action has been marked as finished which indicates that a strategy has been chosen. However, in the introduction the report states that both, in-vessel and ex-vessel cooling strategies are still being considered. It would be appreciated if this contradiction could be clarified.
98 | Czech Republic | 3 | 6-8 (sec. 1.1.3) | In the introduction of the report it is written that for ex-vessel cooling the refractory material choice and its experimental verification and design of lining remain outstanding issues. How does this open issue impact the analyses which have been carried out in the completion of action 49?
99 | Czech Republic | 3 | 6-8 (sec. 1.1.3) | In the introduction of the report it is stated that “Heat removal from the containment atmosphere by means of spraying (providing heat removal) is sufficient to maintain the safe pressure in the containment. The necessity of installing a filtered venting to ensure long-term integrity of the containment due to the release of non-condensable gases generated during ExVC has not been confirmed.” According to the figure entitled “Spraying” the spray system is available within 2 days after start of accident sequence. Even if power and medium supply of this active system is ensured to control containment pressure during long term operation, has its failure been considered (fig. Spraying, p.8 shows 5h of operation)? Is the additional contribution of steam production resulting from water-corium interaction in the “core catcher” considered in the presented estimation of long term pressure development?
100 | Czech Republic | 3 | 44 (sec. 3.3) | The report states that “the function of the containment is ensured by the construction and the structure which definitely resists design over-pressure of 150 kPa and with most probability, double over-pressure.” How has the value of double over-pressure been determined?
101 | Czech Republic | 3 | 8 (sec. 1.1.3) | For the analysis of the risk of containment overpressurization two charts are being presented in the report (spraying and venting). In the chart for “spraying” two graphs for LOCA are being shown. What is the difference between the two LOCAs? In the chart for “venting” only one graph for LOCA, however, another one for SBO is shown? What is the reason for the different charts?
102 | Czech Republic | 3 | 47, 75 (sec. 3.3.2.2.1) | “Re-criticality” For Action No. 61 the status is shown as “in progress/constantly”. Can you provide information on which additional investigations have been requested by the regulatory authority and what are the actual known results concerning the “additional investigations of the potential for re-criticality for the correspondent SAM strategies”?
103 | Czech Republic | General | 78 | In the conclusion of the Czech NAcP it is written that “this Action Plan represents complete set of measures (as of 31st December 2012) to strengthen safety of Czech nuclear power plants in response to the Fukushima nuclear power plant accident.” In view of several newly integrated actions after 2012 the date seems to be outdated. It would be appreciated if this could be clarified.
104 | France | General | 8 (sec. 1) | The chapter provides an introduction to the implementation of the recomendations resulting from the European Peer Review in 2012. It indicates that there are three phases to the implementation with phase 2 lasting from 2015-2020 and phase 3 starting from 2019. At the same time the French government is about to adopt a new law on energy “loi sur la transition énergétique” which foresees not to increase the capacity of French nuclear power above the current level. French media reports seem to imply that older plants might have to be shutdown when new plants, e.g. the EPR in Flamanville, start operation in 2017 in order to meet the requirement of the new law. Could you explain if, and if so how this was to affect the schedule for the implementation of the recommendations resulting from the European Peer Review and the planned phases 2 and 3, especially with respect to individual plants?
105 | France | 1 | 12 (sec. 1.1.1) | The report states that ASN has set the seismic hazard, defined by a response spectrum, to be considered for the SSCs of the hardened safety core as encompassing the safe shutdown earthquake (SSE) for the site, plus 50%. Which criteria (e.g. frequency, peak ground acceleration, magnitude, etc.) were considered to define the factor “plus 50%”?
106 | France | 1 | 12 (sec. 1.1.1) | Concerning the return period considered for extreme climatic conditions, the report only states that it is more variable than for earthquakes and floods. Which design requirements are established related to extreme weather conditions? It would be appreciated if the current status of the safety assessment in order to increase the robustness against extreme weather would be specified.
107 | France | 1 | 16 (sec.1.1.5) | Regarding the conformity of seismic instrumentation the report states that the licensee is requested to check the conformity of its facilities with provision of RFS I.3.b and to submit a summary of the review and corrected deviations together with a plan of action listing correction time-lines for any remaining deviations. It would be appreciated if the report would specify which corrections were carried out, if any, as well as a list of remaining deviations and the planned date for correction.
108 | France | 1 | 16 (sec. 1.1.5) | A specific recommendation from the 2012 Peer Review considers revising the basic safety rule RFS 1.3.b. ASN states that this is currently not a priority. Please specify when, if at all, this recommendation is going to be implemented.
109 | France | 2 | 26 (sec. 1.2.2) | The mentioned peer-review lists as a possible enhancement of the power supplies agreements with the grid operator on rapid restoration of off-site power. Were such agreements made between NPPs and grid operators in case of a SBO?
110 | France | 2 | 26 (sec. 1.2.2) | The report states that the licensee is requested to install additional electrical power supply capabilities. What kinds of systems are considered and what are the requirements for these systems?
111 | France | 2 | 28 (sec. 1.2.4) | In the report it is mentioned that the Nuclear Rapid Response Force (FARN) has set up an organizational structure and means for supplying consumables to sites where access conditions have been impaired. It would be appreciated if more detail on the organizational structure and on the means were given. For example, are heavy duty devices and mobile engines/pumps part of these provisions? Are there sufficient consumables for more than one plant at the same time?
112 | France | 2 | 29 (sec. 1.2.5) | It is stated that ASN has asked the licensees to include equipment and instrumentation necessary for emergency situation management. What kind of equipment and instrumentation are planned to be used?
113 | France | 2 | 29 (sec. 1.2.5) | ECS 19: The report states that ASN has asked the licensee to propose final requirements for redundancy of instrumentation for detecting reactor vessel melt-through and hydrogen in containment by end of 2013. The licensee was also requested to indicate whether or not the provisions planned are part of the hardened safety core. Could you please provide information on the outcome of the studies submitted and whether the provisions will be part of the hardened safety core?
114 | France | 2 | 36 (sec. 1.2.10) | The report states that ASN asked the licensee to present measures to prevent accidental rapid draining of the fuel storage pools. It would be appreciated if more details on the proposed measure could be given.
115 | France | 2 | 36 (sec. 1.2.10) | EDF has identified two modifications to prevent exposure of a fuel assembly during handling in the event of a break in the transfer tube. What kinds of modifications are considered?
116 | France | 3 | 39-40 (sec. 1.2.16) | The report states: “The licensee shall specify the organization and sizing of these teams, in particular: …” (p. 40). Is it planned to have different storage locations of mobile devices in order to reach different NPPs in a minimized time considering the geographical size of France?
117 | France | 3 | 42 (sec.1.2.16) | The report mentions the setup of the Nuclear Rapid Response Force (FARN). How does FARN react if more than one plant is affected by natural hazards? Are there sufficient mobile resources to handle this problem? Is there a tool to decide on a priority?
118 | France | National Organization | 60 (sec. 2.1.1) | It is stated that the Ministry of Foreign Affairs and International Development (MAEDI) is responsible for issuing relevant information via the embassies to French citizen abroad. Are those recommendations coordinated with the recommendations in the country where the accident takes place? Please comment this having especially a focus on European countries and the new approach published by HERCA.
119 | France | National Organization | 60 (sec. 2.1.1) | It is stated that both MAEDI and ANS are responsible for fulfilling the international obligations concerning early notification. Please provide further information how the responsibility and interfaces between both authorities are organized.
120 | France | National Organization | 62 (sec. 2.1.3) | It is expected that human and material resources would be challenged in case of a nuclear accident in France. It would be appreciated if France comments on this identified challenge.
121 | France | National Organization | 62 (sec. 2.1.3) | The report states that ASN adapted its mode of communication in order to cope with streams of questions from the public. ASN trained external service providers to respond to the large number of telephone queries. It would be appreciated if France could share its experiences in training external services providers under emergency conditions (especially high work load of the regulator and its TSO) in the area of nuclear safety and radiation protection. Please describe also, how the quality (here: accuracy, comprehensibility to the public) of the provided information could be ensured under emergency conditions.
122 | France | Emergency Preparedness and Response and Post-Accident Management | 64 (sec. 2.2.2) | Is the mentioned alerting and information system (cell-broadcast) already active? How it is or will it be implemented (via SMS, smartphone app or something else)? Who is responsible for sharing information and who implements the cell-broadcast?
123 | France | International Cooperation | 68 (sec. 2.3.3) | In the report it is only stated that France enhances its cooperation with the Japanese authority. It would be appreciated if France could describe its bilateral actions with European counterparts, especially from its neighboring countries.
124 | Netherlands | 1 | 24 (sec. 1.1) | ENSREG 1.4 (8): What is the temporary solution implemented in 2013 in response to Action 2 (M2)?
125 | Netherlands | 1 | 105 (sec. 8.1) | Action 33 (S3): Please elaborate in more details the main findings of the SMA performed against a defined Reference Level Earthquake of 0.15 g?
126 | Netherlands | 2 | 30 (sec. 2.1) | ‘Ample means of alternate cooling and heat sink are available… However, additional measures to strengthen the availability of the SFP have been studied and are being implemented (Acts 7 and 29).’ Please provide a short description of the additional measures?
127 | Netherlands | 2 | 30-31 (sec. 2.2) | It is stated, that the implementation of a measure to strengthen off-site power is ongoing. Please describe shortly this measure. As mobile pumps are preferred rather than steam driven pumps, it would be appreciated if the Netherlands could provide information if these mobile pumps are already available at the NPP and where those equipment will be stored. Are there any agreements about rapid restoration of off-site power between the NPP and grid operators in case of a SBO?
128 | Netherlands | 2 | 31-32 (sec. 2.3) | What kinds of implementations are made to enhance the DC power supply? What autarky time will be achieved after implementation will be completed?
129 | Netherlands | 2 | 32 (sec. 2.4) | What is the capacity of the tanks for the storage of diesel fuel? How long lasts the stored amount of diesel fuel if the diesel generators are used in case of a SBO? What are the main topics of the Extensive Damage Mitigation Guidelines (EDMG) to restore power supply in case of a SBO?
130 | Netherlands | 2 | 35 (sec. 2.10) | Please provide a short description to refill the SFP without entering the containment?
131 | Netherlands | 3 | 47 (sec. 3.5) | In the report it is stated that “Establishing independent voice and data communication under adverse conditions.” Is the purchased satellite telephone (ENSREG No. 5.1, Current status) capable of sending data or has an additional system been purchased (compare situation in Switzerland)?
132 | Netherlands | 3 | 104 | In the report the following action item is mentioned: “Develop set of clear criteria to provide a basis for deciding when to switch the turbine oil pump off to increase the battery time”. What are the criteria mentioned?
133 | Netherlands | Emergency Preparedness and Response and Post-Accident Management | 77 (sec. 5.1) | Under item 5.8 (115) an improvement of the source term is mentioned. How has this source term been improved and which improvements shall be done in future by the working group?
134 | Netherlands | International Cooperation | 114 | The Netherlands reported that a cross-inspections program with Belgium and France will start in 2015. It would be appreciated if the Netherlands could elaborate in more detail on this program. How are arrangements set up between the different regulatory bodies and license holders (granting access to staff of foreign authorities)? How will insights from such inspections be analyzed and transferred to the Dutch situation?
135 | Netherlands | National Organization | 57 (sec. 4.0.a) | In the Dutch report it is stated, that the new regulatory body, the ANVS, will operate under a mandate of the Minister of infrastructure and environment starting January 1st 2015. However, the new authority will not be formally established within 2015, because a new law has to be prepared. It would be appreciated if the Netherlands could explain in more detail the arrangements between and roles of the minister of economic affairs (who has the right to issue licenses by the Dutch nuclear energy act), the minister of infrastructure and environment, and the new authority ANVS under the mandate of the minister of infrastructure and environment in 2015.
136 | Netherlands | National Organization | 59 (sec.4.0.d) | It is stated that NRG is a license holder and also supports the licensing branch of the Dutch regulator. How does the Dutch Regulator ensure its independence in regulatory decision making with respect to licensing of nuclear activities/facilities in those cases, where its TSO is a license holder at the same time?
137 | Netherlands | National Organization | 59 (sec. 4.0.f) | EPZ has contracted AREVA NP Emergency Response Support Service in case of beyond design basis accidents. Are there possibilities to get information from AREVA’s Emergency Centre (directly or via EPZ) to the emergency organization of the regulatory body?
138 | Switzerland | 1 | 11 (sec. 1.1) | In the NAcP Rev. 0 (Page 9 section 1.1) it was said that ENSI had requested licensees to update the extreme hazard analysis on extreme weather conditions at the 10-4/y return frequency and that the ability of the plants to withstand these events had to be demonstrated. In the NAcP Rev. 1 (Page 11 section 1.1) no explicit reference to the extreme weather conditions was made. What is the current status of the actions mentioned in the NAcP Rev. 0?
139 | Switzerland | 1 | 11 (sec. 1.1) | “2012: The analyses showed that the Swiss NPPs can withstand natural hazards with a return frequency of 1E-4/y, with only moderate, non-safety relevant building damage, and have further margins beyond this.” Which natural hazards, except of earthquake and flooding, have been considered in the analyses, especially which kind of extreme weather? Was the criterion 1E-4/y fulfilled for each of them? Were there any additional safety assessments performed and/or improvements identified for the hazards other than earthquake and flooding? If yes, what are the results for the individual NPPs?
140 | Switzerland | 1 | 12 (sec. 1.2) | The ENSREG recommendation 3.1.2 deals with the possible secondary effects of seismic events, such as flood or fire. However, no reference is made in this section regarding a seismically induced fire. Has the functionality of fire fighting equipment in case of a seismic event been analysed? If yes, what were the results of the analysis? What kinds of measures are required?
141 | Switzerland | 1 | 12 (sec. 1.3) | Mühleberg NPP started a project to reinforce flooding protection of an additional water intake on the river by building a new pump station on an elevated location. It would be appreciated if the scope and timeline of the project could be briefly summarized? Will the project also affect other components like the intake screen?
142 | Switzerland | 2 | 14 (sec. 2.1) | From the Swiss report it is understood that Mühlberg NPP will no longer look for an diverse ultimate heat sink with respect to the decision to permanently shut down the NPP in 2019. Please elaborate in more detail the envisaged alternative measures for Mühleberg NPP instead of a diverse ultimate heat sink. Please comment on the request for a redundant diverse ultimate heat sink as stated in section 2.11 on page 19.
143 | Switzerland | 2 | 15 (sec. 2.2) | In terms of AC power supplies, the report mentioned a sixth layer consisting of accident management equipment. Furthermore, a seventh layer with off-site accident management equipment is addressed. Please elaborate in more detail on the differences between the sixth and seventh layer. Are there any agreements about rapid restoration of off-site power between NPPs and grid operators in case of a SBO?
144 | Switzerland | 2 | 15 (sec. 2.3) | Is the ENSI’s requirement regarding DC power supply (minimum battery capacity of 4 hours) fulfilled for all NPPs in Switzerland? Are there any intentions to increase the requirements for the minimum battery capacity?
145 | Switzerland | 2, 3 | 16, 25 (sec. 2.4, 3.6) | “2013: The procedures of the activation of the Reitnau external storage facility and the provision of Severe Accident Management (SAM) equipment and its transportation from the external storage facility to the plants have been tested. These tests have been carried out as part of an unannounced alarm exercise in one NPP and a national emergency drill.” Since Reitnau is an external storage facility “containing various accident management provisions for emergencies”, are similar unannounced exercises planned for all other NPPs in Switzerland?
146 | Switzerland | 2, 3 | 16 (sec. 2.5) | Please provide more detailed information on the improvements, which have been performed for accident instrumentation and monitoring system in the NPPs in Switzerland. What is the progress of backfitting projects for an additional flooding and seismically robust SFP cooling system? What is the outcome of the performed analyses on hydrogen management? Did you identify a need for further measures?
147 | Switzerland | 2 | 17 (sec. 2.8) | The report states that tests showed that the operability of the equipment located in rooms of the special emergency bunkered systems, including control panels, is assured for at least several days. How many days are expected in case of postulated demand?
148 | Switzerland | 2 | 20 (sec. 2.13) | The report addresses the severe accident equipment stored at Reitnau. Can Switzerland provide information on the time needed to transport equipment to the NPPs in relation to the grace time of the NPPs? Which measures are planned if a natural hazard causing a beyond design basis event also hinders the transport from Reitnau to the NPP (e. g. a heavy snow storm)?
149 | Switzerland | 3 | 26 (sec. 3.10) | The report states that only some licensees proposed to equip their containment with PARs. What is the reason for the exceptions? Have possible oxygen/hydrogen mixture situations due to air movements in severe accident situations been considered?
150 | Switzerland | National Organization | 30 (sec. 4.1.1) | In the report it is stated that ENSI as the supervisory authority is independent from the licensing authority according to the Swiss Nuclear Energy Act. According to IAEA Safety Standard GSR-Part 2 Requirement 23 authorization is a key function of the regulatory body. One prerequisite for authorizing a nuclear activity would be the review and assessment of nuclear safety. In many countries a trend can be observed to combine previously independent inspection and authorization in a single entity (see e.g. latest developments in the Netherlands). Switzerland is emphasizing ENSI's independence from the licensing authority. Can Switzerland comment its position why a clear separation of inspectorate and licensing authority is favorable?
151 | Switzerland | National Organization | 39 (sec.6.4) | Swiss Operators are obliged to form a group to analyze events within the plant (and events from abroad) and report to ENSI. It is further stated, that ENSI reviews national and international operating experience. Can Switzerland clarify the role of ENSI and the operator in more detail? Is ENSI performing event analysis independent from the utilities?
152 | Switzerland | Emergency Preparedness and Response and Post-Accident Management | 34 (sec.5.1) | The NBCN Crisis Management Board assesses the overall situation. Do other Swiss organizations additionally assess the situation? If so, which assessment is basis for e.g. a recommendation of measures?
153 | Switzerland | Emergency Preparedness and Response and Post-Accident Management | 34 (sec.5.2) | The NBCN Crisis Management Board proposes necessary measures to the government. Has the government to follow these proposes or is it free e.g. to change, add or dismiss measures? Who is responsible for giving orders about measures to implement?
154 | Switzerland | Emergency Preparedness and Response and Post-Accident Management | 34 (sec. 5.2) | Are iodine tablets pre-distributed to households only or also to other places like schools, kindergartens or companies?
155 | Switzerland | Emergency Preparedness and Response and Post-Accident Management | 34 (sec.5.2) | What is meant by reviewing the zone concept? Were changes adopted (besides the pre-distribution of iodine tablets), and if so, what was changed in the concept?
156 | Switzerland | Emergency Preparedness and Response and Post-Accident Management | 34 (sec. 5.2) | The report addresses a review of the reference scenario for emergency planning. Has this reference scenario changed, and if so, in which way?
157 | Switzerland | International Cooperation | 39 (sec. 6.4) | Inspectors of ENSI and ASN regularly perform cross inspections in Switzerland and France based on bi-lateral agreements. How are arrangements set up between the different regulatory bodies and licensees (granting access to staff of foreign authorities)? How will insight from such inspections analyzed and transferred to the Swiss situation?
158 | Germany | 3 | 8, top | The RSK studies on "hydrogen release in rooms outside the containments have not yet been concluded" - Do you have any results by now ?
159 | Germany | 3 | 17, N-6 and N-7 (20, N-21) | The German studies on hydrogen accumulation in unexpected places seem only to deal with hydrogen associated with venting operations or hydrogen formation in spent fuel pool rooms outside the containment. During the Fukushima Daiich accident the three massive explosions were caused by hydrogen generated by Zirkonium-steam reactions (where recombiners are without effect) seeping into rooms outside the containment due to malfunctioning sealing materials. Under this type of hydrogen formation, hydrogen inside the containment will not be a big problem, due to the lack of oxygen there, but malfuntioning sealing materialsaround penetrations might allow hydrogen to seep into rooms with oxygen. - This issue does not seem to be covered by German studies, do you have any results to report on this issue ?
160 | Germany | 3 | 22, GKN-6 25, KBR-9 30, KKE-19 | Studies on hydrogen propagations have been concluded for several units. - Could you elaborate on these results and the conditions assumed?
161 | Germany | 2, 3 | 24, KBR-5 | Do you have a description of the "mobile shortened residual-heat removal chain" developed ?
162 | Germany |  | 22 pp. Table 52 | It would be informative if finalisation dates for finished activities were also given
163 | Germany | 3 | 25, KBR-9 a.o. | "Review and optimisation if necessary of the requirements for the containment venting system with consideration of station blackout conditions, adverse radiological conditions and the effectiveness following natural external design impacts. - Which improvements may be needed ?
164 | Germany | 3 | 25, KBR-12 a.o. | Examination of the need to be able to initiate additional accident management measures from the remote shutdown and control station, too. - Which improvements may be needed ?
165 | Germany | 3 | 26, KBR/24 (24, KBR/3) (25, KBR/7) | Do you have any details on the concept developed ?
166 | Sweden | 2 | 45, T2.LA.9 | additional mobile generators - are they placed according to ENSREG topical peer review 2, recommendation 1, para 2, "It is important that the equipment is to be stored in locations that are safe and secure even in the event of general devastation caused by events (significantly) beyond the design basis."(ENSREG topical peer review 2, rec. 1, para 2) - the rule-of-thumb applied during the topical review was "at least or approximately 100 meters from a reactor. During the country visits the review teams noted that the existing mobile units were placed next to a reactor building, with one mobile unit per two reactors.
167 | Sweden | 3 | 26, 3.2.5 | During the Fukushima Daiich accident the three massive explosions were caused by hydrogen generated by Zirkonium-steam reactions (where recombiners are without effect) seeping into rooms outside the containment due to malfunctioning sealing materials. Under this type of hydrogen formation, hydrogen inside the containment will not be a big problem, due to the lack of oxygen there, but malfuntioning sealing materials might allow hydrogen to seep into rooms with oxygen. The Swedish report says that investigations show that seepage of hydrogen to other rooms in the containment and neighbouring buildings would not be be a problem. - Could you elaborate on this issue ?
168 | Sweden | 3 | 37, 7.1, 6th bullet | new improvement added here: Measures to minimize the risk that steam can spread from leaks or breaks in the blowdown system and that the chemical and volume control system shall affect the cooling system of the containment or the residual heat removal system. (R2) - Could similar mechanism problems apply to other PWR's ? Are any results available?
169 | Sweden | 1, 2, 3 | 42 pp., 8.2 (47,T3.LA.2) (63, 9.1.6) | The descriptions of several actions have been abbreviated, which reduces readability; replacing the previous descriptions of these actions in the next revision of the action plan is suggested
170 | Sweden | 2, 3 | 44, T2.LA.2 | Alternate cooling and alternate residual heat removal - Could you elaborate on the time schedule and expected designs after the issuance of the SSM directive of December 16, 2014 ?
171 | Sweden | 2 | 46, T2.LA.19 | F+E12or Ringhals PWRs re-criticality must be considered in the long time scenario. Measures have been identified and addressed. The overall probability for re-criticality the that endangers the containment integrity is judged to be very small for the BWRs. - Which measures have been identified, and how are they addressed?
172 | Sweden | 2, 3 | 47, T3.LA.1 and -3 | The concept for the preliminary studies and analyzes is based on the feed-and-bleed cooling concept of the fuel pools. Overall requirements for alternative function for cooling the fuel in the fuel pools have been developed by the licensees in a common project. The necessary instrumentation to monitor temperature and water level in the fuel pools will be introduced in connection with the introduction of an alternative function for cooling the fuel in the fuel storage pools, see Action T3.LA.1. - When and how will this be implemented ?
173 | Sweden | 2, 3 | 47, T3.LA.2 63, 9.1.6 (44,T2.LA.2) | "(Define the design basis for an) independent core cooling system" The licensees have in a common project developed a ”Position Paper” that defines requirements that shall be adopted. - Could you elaborate on the time schedule given in 9.1.6 and expected designs ?
174 | Sweden | 3 | 48, T3.LA.7 | "(Develop the strategies for )managing loss of containment integrity" The licensees have investigated possible strategies on loss of containment function and approaches to assess the containment damage extent. The outcome of the investigations will be incorporated in the Emergency Operating Instructions. - Do these investigations indicate damage that might lead to hydrogen seepage into rooms outside the containment ?
175 | Sweden | 3 | 48-49, T3.LA.11 | Investigation into the handling of hydrogen (oxyhydrogen) after a severe accident is handled in a joint licensees project within the Nordic Owners group (NOG). So far, the project has focused on hydrogen formation and accumulation in the reactor containment. A number of potential shortcomings in the handling of hydrogen gas after a severe accident have been identified. - Could you elaborate on these shortcomings ?
176 | Sweden | 3 | 49, T3.LA.16 | "(Reassess the use of )containment filtered venting system in the long-term" Investigations and assessments of the ability to manage a severe accident have been performed by the licensees with different suggested solutions of the case. - Could you elaborate on these findings ?
177 | Bulgaria | 2 | 12, 2-1.7. | Reactor Coolant Pump Seals: "robustnet for at least 24 hours...experimentally verified by the manufacturer". This was a high issue during the 2012 Stress Test topic 2-review. Do you have any additional information ?
178 | Bulgaria | 3 | 15, 3-1.1 19,3-1.10 | hydrogen migration to rooms outside the containment does not seem to have been considered, not even in case of hydrogen formation by Zirconium-steam-reaction, where PARs inside the containment would not be effectice, as "In severe accident containment is isolated and there is no possibility for hydrogen migration outside it." Will this assumption be valid in all situations?
179 | Bulgaria | 3 | 34, D-3-5 | Molten core retension. Are there any preliminary results ?
180 | Bulgaria | 2 | 11, 2-1.2 47, A-1-1 55, FA-1-1-1-4 33, A | as I read these points, 2 mobile DGs have been delived in 2013, but are they for 6 kV or 0,4 kV? Is one 6 kV and one 0,4 kV DG per unit envisaged in the end - or only one mobile 6 kV DG?
181 | Bulgaria | 3 | 39, first section | Typo: "As a result of the extension of scope of measure A-1-1" should be "...A-1-2" (se page 47, 3rd row)
182 | Bulgaria | 3 | 42, C-2-4 | could you give any details on the solutions developed ?
183 | Belgium | 1 | 3 | The licensee Electrabel had still not officialy requested the Long Term Operation (LTO) by the end of 2014. Question: Is there a deadline for submitting the request?
184 | Belgium | 1 | 8 | The safety margin assessment (SMA) for the Döel and Tihange units was performed on the basis of a RLE as high as 1,7 time the peak ground acceleration (PGA) of the current design basis earthquake. For Doel 1/2: RLE= 1,7*PGA < 0,1g. Question: If Electrabel ask for the Long Term Operation (LTO), is there any provision to apply an SMA with higher RLE, as part of the LTO requeriments?.
185 | Belgium | 1 | 14 | Please indicate the scope and/or standards used to modify the existing protection against lightning al Doel. Is Tihange considered K about it?
186 | Belgium | 1 & 2 & 3 | Generic | Regarding the protection against earthquakes. To comply with the topics 2 (loss of safety system, CSBO y UHS) and 3 (Severe Accident Management), Electrabel has analyzed different scenarios. Question: Please explain the criteria in order to assess margins beyond design basis earthquake for equipment needed in strategies against CSBO, Loss of primary and alternate ultimate heat sink (UHS) and Severe Accident Management.
187 | Belgium | 1 & 2 & 3 | Generic | Question: Regarding the equipment mentioned in the previous point: is there any action planned to verify the future maintenance of seismic margins obtained in assessments?.
188 | Belgium | 2 | 19 | Which are the alternative Ultimate Heat Sinks for Döel and Tihange when all the units at the site are affected by the loss of primary UHS?
189 | Belgium | 2 | 19 | Regarding the enhancements in the instrumentation of the Spent Fuel Pools (SFP): (1) Which is the program (schedule) of implementation of the improvements of the level measurements?, and (2) Are there plans to improve the temperature instrumentation (range, qualification, remote reading)?
190 | Belgium | 2 | 19 | Please comment on the provisions about SFP water level measurement (type of instruments, electric supply, qualifications,….).
191 | Belgium | 2 | 15 | High numbers (16, 17) for second level DGs are mentioned. Please briefly comment on how they are structured, i.e., the degree of redundancy existing per plant unit.
192 | Belgium | 2 | 16 | Please explain the provisions intended to ensure the make-up for the primary system in open configuration.
193 | Belgium | 2 | 16 | Please explain what is meant to make operable the emergency compressed air circuit.
194 | Belgium | 2 | 16 | Please indicate what is meant by the provision of an alternative power supply for non-conventional means or safety equipment.
195 | Belgium | 3 | 23 | Enhacements of the protection against severe accidents. What meassures are planned (or have already been implemented) to prevent the corium-concrete interaction?
196 | Belgium | 3 | 23 | What meassures are planned (or have already been implemented) in relation with the accumulation of hydrogen in the Döel and Tihange containment building?
197 | Belgium | 3 | 23 | According to the report, Filtered Containment Venting System will be implemented in Belgium NPPs around 2017. Has the Belguim Regulatory Body issued technical criteria to be met by these new systems (for instance, regarding the efficiency of the filtration or the type of containment isolation devices for this system)?
198 | France | 1 | 8 | It is mentioned that an automatic reactor trip in the event of an earthquake will be implemented. Please comment on the fundamentals for this decision, its expected adventages, and on the value possibly assigned to the trip setting.
199 | France | 1 | Page 20/73 (ECS-13) | Regarding the adopted decision to implement "an automatic seismic shutdown system": has the measure been decided to be applied to all the plants? is there any minimum level of seismic hazard to do that? (minimum value of seismic hazard or PGA)
200 | France | 1 & 2 & 3 | Generic | With regard to the equipment needed to manage loss of ultimate heat sink (LUHS), station blackout (SBO), and severe accident situations. Questions: Are all included in the "hardened safety core"?. Has been verified the seismic behavior of all of them for earthquakes beyond the initial design basis of the facilities (hardened safety core level earthquake)?.
201 | France | 1 & 2 & 3 | Generic | Question: Regarding the equipment mentioned in the previous point: is there any action planned to verify the future maintenance of seismic margins obtained in assessments?.
202 | France | 2 | 26 | Please indicate provisions to adding layers of emergency power.mainly in relation to external power supplies.
203 | France | 2 | 27 | Please explain how the autonomy of the batteries has been increased from 1 hour to 2 hours.
204 | France | 2 | 27 | Are the batteries needed for control purposes in case of an SBO event, up to the time that DG extra supplies are made available?
205 | France | 2 | 37 | Please give some details on the tasks performed related to guarantee separations and independence of the safety systems.
206 | France | 2 | 39 | Are material resources available for the FARN activation, "redundant" from the resources (mobile&portable equipment) available at the sites, or are thought with a different scope?
207 | France | 3 | 41 | In the ASN letter to EDF, the following is stated: "ASN asks you to integrate into the accident operations procedures and the severe accident management documents, including the severe accident management guidelines in particular, the new provisions for handling the extreme situations studied en the stress tests and affecting several reactor on the same site, for all operating states, as well as the fuel storage buildings". What kind of changes have French NPPs implemented as a response to this requirement?
208 | France | 3 | 42 | Inspection of equipment: Which are the main characteristics of the maintenance programme developed by the French NPPs to verify the operability of the mobile devices? What is the test frecuency? Have the plants set "inoperability times" to take action in case of inoperability of thse equipments?
209 | France | 3 | 44 | What kind of instrumentation will be implemented to detect reactor vessel melt-through?
210 | France | 3 | 45 | What kind of modifications are being implemented to prevent high-pressure melt ejection in high-pressure secuences?
211 | France | 3 | 45 | "EDF concluded that a geotechnical containment at an economically acceptable cost is not feasible" Which other measures are currently being analysed to prevent basemat melt-through?
212 | France | 3 | 34 | Regarding ECS-29, "Reinforcing of the U5 venting filtration system", what will be the specefic design provisions for the limitation of hydrogen combustion risks?
213 | France | 3 | 34 | Regarding ECS-29, "Reinforcing of the U5 venting filtration system": 1) what are the validation and calculations performed to demonstrate the ability to manual-local open/close the venting filtration system isolation valves under high radiation fields? 2) Is it included in the Venting Filtration System reinforcing project the implementation of an additional passive way of venting (i.e. instalation of a paralel line including rupture disks plus open valves)?
214 | Germany | 1 | Table 7-1 (Annex, page 68; No. E-5) | Regarding the global scope of recommendation N-13, has this already been covered in all involved plants? The report is not very clear on this regard. Please, do you mind to explain any more about it? Apart from some seismic aspects, are there any other activities on going relating to N-13 and natural hazards?
215 | Germany | 1 & 2 & 3 | Table 5-2 (page 46; No. 12) | The report mentions "Performance of an adapted robustness analysis" like an activity "in progress" and also "finalisation 2014". Could be explained better this situation? Has this any relation with the specific consideration of extreme external events (natural or human-induced)?
216 | Germany | 1 & 2 & 3 | Table 5-2 (page 53; No. 13) | Same as before, the report mentions "Performance of an adapted robustness analysis" like an activity "in progress" and also "finalisation 2014". Could be explained better this situation? Has this any relation with the specific consideration of extreme external events (natural or human-induced)?
217 | Germany | 1 & 2 & 3 | Generic | A systematic review in the event of a beyond design earthquake (objective: guarantee of vital functions) has been carried out as part of a robustness analysis of the plants. Question: Please explain the criteria in order to assess margins beyond design basis earthquake (minimum values HCLPF for equipment needed in strategies against SBO and Severe Accident Management)
218 | Germany | 1 & 2 & 3 | Generic | Question: Regarding the equipment mentioned in the previous point: is there any action planned to verify the future maintenance of seismic margins obtained in the assessments?
219 | Germany | 2 | 22 and generic | GKN II/PWR: Battery capacities by plant design are higher than 10h. Is this the minimum capacity required for German NPPs? Is there any analysis to increase the time until battery depletion?
220 | Germany | 2 | 22 | GKN II/PWR: 1) What exactly are "multiple-cell coolers"? 2) How is river Neckar the diverse heat sink available (pumping water from the river or from wells)?
221 | Germany | 2 | 25 and generic | KBR. "Creation of a diverse source of cooling water (water intake from a source other than the river". 1) Can you provide additional information about the nature of this additional water sources? 2) Additionally, in general, what engineering solution have German NPPs adopted when the UHS is a river?
222 | Germany | 2 | 16 | To reach the 10 hours duration for batteries, is load shedding considered, or 10 hour sized batteries are implemented?
223 | Germany | 2 | 16 | Please comment about improvements in communication systems in order to coordinate actions from different places during the emergency.
224 | Germany | 2 & 3 | Generic | "Mobile shortened residual-heat removal chain" What does it refer to?
225 | Germany | 3 | 24 | GKN II/PWR: "The operability in an emergency of the permanently installations for fuel pool cooling has been demonstrated". Please, provide clarification of this point, it is not clear if the sentence means that no additional cooling means (neither fixed nor mobile) have been implemented.
226 | Germany | 3 | 33 | KKG/PWR: "Development and preparation of Severe Accident Management Guidelines (SAMG), as well as introduction and instruction at the plant. Development, preparation, plant-specific adaptation, introduction and instruction completed" 1) Which are de generic Basis that have been used for the SAMGs development? 2) What has been the validation processes performed by the specific NPP for the plant specific adaptation?
227 | Germany | 3 | 47 | GKN I/PWR: "GKN I have developed manual actions for low-power and shutdown operation that can also be used as recommended actions within the framework of SAM" Which are these manual actions mentioned above for low-power and shutdown operation?
228 | Germany | 3 | 17 | Please summarize provisions, or performed upgradings, to initiate actions from the remote shutdown stations.
229 | Germany | 2 | 16 | Please indicate provisions, or credit, taken for the use of hydraulic power units, external to the plants, in case of station blackout.
230 | Germany | 2 | 16 | Please comment about the extention of provisios for using portable instrumentation. Is this the first option, or using plant instrumentation supported by batteries is preferred?
231 | Germany | 2 | 16 | During the first 10 hours of the accident, is the ac power supplied by one (or more) portable DG located at the site? Please indicate the time goal for such availability, and the guarantees for extending the performed exercises for a real case (availability of personnel at the site).
232 | Germany | 3 | Tabla 7.2 | Paragraph C-2, please explain: How are going to be guaranteed and justified competent and sufficient human resources to face emergencies?
233 | Germany | 3 | Table 7.2 | Paragraph C-13: How often are going to be performed such long term exercises?
234 | Germany | 3 | Table 7.2 | Paragraph C-22, please give more information on which medical and human aspects of the response have to be analyzed to support emergency workers.
235 | Romania | 1 | 15 | Please indicate provisions, or applicable regulations, in relation with lightning protection, and connections to earth.
236 | Romania | 1 & 2 & 3 | Generic | Regarding the protection against earthquakes, the assessments performed for Cernavoda NPP demonstrated that the safety functions for the success paths for seismic events are fulfilled with a margin of minimum 0.4g. Regarding topics 2 and 3, the license has analyzed different scenarios (SBO, LOUHS,.. and selected severe accident scenarios).Question: Have been analyzed using the same criteria (margin minimum 0.4g) the necessary equipment to meet the different scenarios ?
237 | Romania | 1 & 2 & 3 | Generic | Question: Regarding the equipment mentioned in the previous point: is there any action planned to verify the future maintenance of seismic margins obtained in assessments?
238 | Romania | 2 | 17 | 1) Are the activities in the Secondary Control Area (SCA) aimed to cool the reactor from the secondary side? Please comment. 2) Are MSSVs opened manually, in case of SBO accident, from a new facility? What equipments are controlled from such facility?
239 | Romania | 2 | 17 | 1) Such SCA facility, just only require one 100 kW mobile DG, for electrical supply for instruments)? 2) Are auto/manual control stations required?
240 | Romania | 2 | 17 | 1) What is the reliability assigned to the dousing tank? 2) Has it been tested? 3) Is its use the first option of the plant, because it seems to be faster than using mobile DGs?
241 | Romania | 2 | 17 | Please indicate which is the use assigned to that mobile diesel engine driven pump.
242 | Romania | 2 | 17 | 1) Is it a time goal to complete the connection of the mobile DGs? 2) Are exercises periodically performed, with appoved procedures? 3) Please comment about personnel availability at the site for emergency response.
243 | Romania | 3 | 18 | What is the validation performed to the specific NPP SAMG?
244 | Romania | 3 | 20-21-22 | In the table, action 26 provides information about the qualification of instrumentation for SA conditions. 1) Can you detail what design modifications have been (or are going to be) implemented in cables and/or instruments to upgrade to the severe accident qualification? 2) Are there existing instruments that have been upgraded in terms of qualification, to demonstrate their robustness agains severe accident envinroments?
245 | Romania | 3 | 20 | Regarding the containment isolation: are the materials (seals, valves, etc) qualified to avoid containment failure due to sustained Severe Accident high temperature/pressure/radiation levels?
246 | Romania | 3 | 20 | What meassures are planned (or have already been implemented), if any, in relation with the accumulation of hydrogen in buildings outside the containment?
247 | Romania | 3 | 20 | According to the report, Filtered Containment Venting System has been implemented in recent years. Has the Romanian Regulatory Body issued technical criteria to be met by these new systems: for instance, regarding the efficiency of the filtration or the type of containment isolation devices for this system (RUPTURE DISK,...)? 2) If not, which technical criteria have been considered by the supplier in the design and implementation of the system?
248 | Romania | 3 | 25 and 31 | SAMG for shutdown modes: 1) have PSA level 1 and 2 for Shutdown and Low Power been considered in the development of SAMG? 2) If yes, did PSA been considerd for generic SAMG and/or for Cernavoda specific Shutdown SAMG?
249 | Romania | 5 | Action 40 | Please give more information about the alternative off-site emergency control center of Constanta city (60 km away from Cernavoda NPP). 1) Which information from NPP will be available in emergencies on this center? 2) How will be implemented and which kind of communications will be between the center, the NPP, and the Competent Authorities management center? 3) How are going to be guaranteed and justified competent and sufficient human resources to face emergencies in this center?
250 | Switzerland | 1 | Page 11 (Secc. 1.1 - 2014) | The text indicates "ENSI is reviewing the submitted documents." Is there a deadline planned to finish the ENSI review? (for seismic hazard and other natural hazards, if any. See later question about page 14)
251 | Switzerland | 1 | Page 14 (Secc. 1.7 - 2014) | Regarding "Flooding margin assessments", is there a deadline planned to finish the ENSI review?
252 | Switzerland | 1 & 2 & 3 | Generic | Regarding the protection against earthquakes. To comply with the topics 2 (loss of safety system) and 3 (severe accident management), the licenses have analyzed different scenarios. Question: Please explain the criteria in order to assess margins beyond design basis earthquake for equipment needed in strategies against SBO and Severe Accident Management.
253 | Switzerland | 1 & 2 & 3 | Generic | Regarding the equipment mentioned in the previous point: is there any action planned to verify the future maintenance of seismic margins obtained in assessments?
254 | Switzerland | 2 | 14 | Please indicate the basic aspects for the Mülheberg UHS proposal (to be implemented by 2015).
255 | Switzerland | 2 | 14 | Please indicate what is included in the thrid layer of defence, and the degreee of avalilability for inmediate (or delayed) use for plant supply.
256 | Switzerland | 2 | 15 | Please indicate how the 4 hours requirement, for battery capacity, is being reached. Some before such time, mobile DGs would be available to supply the battery chargers?
257 | Switzerland | 2 | 16 | 1) Please comment if the activities that have been done in order to try the use of instrumentation based in passive principles. 2) Please indicate if there are instruments that have been changed in the Swiss NPPs, on this bases or due to other reasons (also related to the Stress Tests results).
258 | Switzerland | 2 | 19 | 1) Please explain how Periodic Safety Reviews(PSRs) are used to assure that physical separation and independence of safety systems? 2) Please indicate the regulations that are considered, and eventually some example.
259 | Switzerland | 2 | 19 | Please indicate, if applicable, the activities performed to assure the availability of instrument air, and some example about the credit assigned to such air supply.
260 | Switzerland | 2 | 20 | Please comment on the extent and controls for the periodic drills performed with the on-site stored equipment.
261 | Switzerland | 2 | 20 | For the NPPs having turbodriven pumps, the time to connect mobile DGs (in SBO accident) seems to be critical: 1) What is the time goal for such situation, if applicable, and 2) has it been guaranteed on the basis of the periodic drills?
262 | Switzerland | 2 | 20 | 1) The safety systems to be operated in the a full SBO accident (with no damage in the primary coolant loop), are fed from medium voltage buses, or from low voltage buses, or both? 2) Is it the same for all the Swiss NPPs? 3) Please comment on how this relates to the strategy for using the mobile DGs.
263 | Switzerland | 2 | 15 | Mühlberg NPP has submitted a proposal of alternative measures for a diverse ultimate heat sink. Which is the proposed concept for this diverse UHS, currently in evaluation by ENSI?
264 | Switzerland | 2 | 17 | Shutdown improvements. ENSREG recommendation 3.2.6: "The enhacement of safety in shutdown states and mid-loop operation. Examples of improvements include, reducing or prohibiting mid-loop operation, adding dedicated hardware, procedures and drills, the use of other available water sources (e.g. fron hydro-accumulators), requiring the availability of SGs during shutdown operations and the availability of feedwater in all modes". Which of the above mentioned improvements are included in Swiss NPPs procedures?
265 | Switzerland | 2 | 19 | Beznau NPP: Which compensatory measures have been taken until 2017 when the plant should install a venting duct to remove heat and pressure generated by boiling SFP water?
266 | Switzerland | 3 | 29 | The report states: "The SAMGs of the Swiss NPPs cover all plant states and include the SFPs". 1) Which are the actions included in these SAMGs specifically oriented to mitigate the consecuences of a severe accident during refueling outages? And 2) if the severe accident takes place in the SFP?
267 | Switzerland | 3 | Paragraph 3.13 | Please give more information about the protections implemented in every on-site emergency centers?
268 | Switzerland | 4 | Generic | In relation to National Organization in respect of Nuclear Safety please give more information about: 1) How stakeholders participate to the debate during the meetings promoted by ENSI. 2) How are being taken into account the stakeholder recommendation in emergency preparedness & response issues?
269 | Belgium | 2.1 & 2.2 | p7 §3 Status of the Stress Tests Actions | The content of the revised NAcP is much more comprehensive in so far as it allows to better evaluate the proposed changes and evolution at Tihange and Doel sites since the Fukushima Daichi accident. However the datasheet related to the actions planned (description and schedule) is no more included in this new version and it is explained in §3 that “For the purpose of readability, this report does not list the status of all actions. Only the major actions are highlighted.” For example concerning power and water supply, the schedule of the various actions is given globally and consequently it is difficult to appreciate the progress.
270 | Belgium | 2.2 | p11 | At Tihange site which has to be protected against the Meuse level, the non-conventional means will be deployed during the flooding alert period. These non-conventional means are located at least 1 m above the level corresponding to the design flood and consist, among other things, of additional diesel generators in bunkered buildings, fixed pipes (with a few exceptions of flexible elements), pumps for make-up of water from water tables to the primary circuit, the steam generators and the spent fuel pools. So it consists of fixed means which are supposed to be operational in case of design flood. Could Belgium clarify if additional mobile equipment like mobile EDGs are nevertheless considered to cope with severe accident conditions?
271 | Bulgaria | 1.1 | p7 | In 2013, France asked the following question related to NAcP §1.1 p7: “ENSREG compilation (3.1.1) recommends a return frequency of 10-4 per annum for hazards. Bulgarian NAcP considers that characterizations of earthquake, maximum level of the river, wind and tornado are consistent with this recommendation. Other weather conditions are not mentioned. Moreover, country report shows that extreme temperature over the design temperature has already occurred. Could other weather conditions (e.g. air and water temperature, drought, snow, hail…) be developed with regards to this recommendation?” The §1.1 of the updated NAcP did not change; does it mean that the other weather conditions above mentioned are already covered by the design?
272 | Bulgaria | 1.1 | p35 | In 2013, France asked questions related to NAcP §III.1 p31. We note that some answers to questions posted by France are brought in the updated NAcP. Notably p35 concerning the detail of measure A-1-1, the construction of bunker buildings for MDG sheltering, as well as the provisions for access routes of these MDGs are considered. However it is not clear whether the other measures concerning provisions for connection and for charging the batteries of the safety systems by the MDGs, give an answer to the questions asked in 2013 (extreme weather conditions, diversity, independency). Could Bulgaria clarify this point?
273 | Czech Republic | 1.1 | General | A French comment in 2013 was: “Could Czech Republic clarify how the table of Part I is fulfilled and to what extent there is a narrow link between the recommendations and the associated actions?” It is a commendable aspect to note that all the tables of PART I, II and III are now linked to the table of PART IV which makes easier the understanding of the report and allows to assess how the recommendations are dealt with. Moreover, this important point has been identified in the updated NAcP (page 6, §1.1.3 Revision 2 of NAcP) as follows: “Based on the findings set out in Part 3 of reference [10] Revision 1 of the NAcP has been developed, in which links between parts I - III of the NAcP summarizing the results of stress tests and Part IV of the NAcP containing the relevant action were clearly shown.”
274 | Czech Republic | 2.2 & 2.3 | p70 | Loss of UHS for Dukovany NPP: The recommendation page 15 of the Czech Republic Peer Review Country Stress Test is effectively identified as recommendation number 3.2.11.2.1, page 35 of the updated NAcP about safety qualification of the 4 wet cooling towers; it is linked to action 33, page 70 of the NAcP: “Implementation of the ventilator towers for ensuring independent ultimate heat sink”. A good practice is that the schedule for hardware modification has been shortened since the Peer Review Report: 2014-2016 instead of 2015-2017. In addition this shortened deadline is maintained from the initial to the updated NAcP. Could Czech Republic confirm this action will be effectively solved in 2016?
275 | Czech Republic | 2.3 | p77 | In the revised NAcP there are 2 new actions number 78 and 84 which are respectively: “For EDU, procurement of additional fire truck to cope with multiunit accidents.” And “For EDU and ETE, procurement of fire brigade truck equipped with necessary devices to cope with selected SA.”: For EDU could Czech Republic clarify whether there is really a difference between these 2 actions? Why in the first case it is considered as a design issue and in the second case as a part of severe accident management?
276 | Czech Republic | 2.3 | p77 | In the revised NAcP there is a new action number 79 which is: “For EDU and ETE, preparation and validation of procedures for the use of the safety DG of the other unit in case of an SBO.” Could Czech Republic clarify the status of this action and in which conditions it can be applied? Indeed it seems it cannot be considered in case of site SBO due to external hazards
277 | Finland | 1.1 & 2.3 | p7 | In the ENSREG peer review country report for Finland, reviewers recommend to consider additional assessment of critical SSC with respect of PGA = 0,1 g. One French comment in 2013 was that in section 8 it was not found any action planned to address this issue. The question seems to be still valid in so far as the list of actions in section 8 addressing topic 1 remains unchanged in the updated NAcP. However it is said in section 1.1 page 7 that “STUK has required Fortum to evaluate the needs and possibilities for improving the supports of the seismically most sensitive main components [...]. In accordance with the new regulatory YVL Guides, STUK has required that the licensees review and update the site specific seismic hazard”. Could Finland clarify whether these complementary information constitute new actions in response to the above ENSREG recommendation and in this case why they are not reported in section 7?
278 | Finland | 2.2 | p26 | From §3.5 the internal and external communication network in case of severe accident has been identified as a system to strengthen. Could Finland clarify whether there is an action dealing with this issue recorded in section 7 tables 2 and 3?
279 | Germany | 2.2 | p13 | In the updated NAcP p13: “Table 5-1 contains the national recommendations from the GRS Information Notice and from all RSK Recommendation as well as RSK Statements relating to Fukushima”. Could Germany clarify, in Table 5-2 and for each NPP, how this GRS information notice is taken into account insofar as there are only 11 RSK recommendations in Table 5.1 (N1 to N11) which address this notice?
280 | Germany | 2.2 | p76 | Table 5-2 it is noted: “Only 4 of the NPPs have performed a seismic PSA. The next round of PSRs might be used to review the seismic hazard and design for all plants, which remain in operation”: It corresponds to N14 RSK recommendation. Since 2013 this recommendation has been applied for KKE/PWR; however, from Table 5-2, there is no reference to seismic PSA for 3 units still in operation, GKN/II, KKP2/PWR and KRB B+C/PWR. The consideration of a seismic PSA for these 3 plants should be clarified taking account the work already achieved as suggested by Table 2-3 of the German National Report.
281 | Germany | 2.2 | p24 | In the Peer Review German Report, it is noted: “The regulator intends to extend the requirement regarding seismic monitoring systems to all plants. No schedule for implementation was provided”. From Table 5.2 of the updated NAcP only KBR/PWR has clearly taken provisions for installation of seismic instrumentation. Why this requirement has not been extended to all plants?
282 | Hungary | 2.2 | p63 | Part V p63 Progress in the Action Plan: “2 independent diesel generators protected against external hazards will be provided. They will have accident as well as maintenance functions. Deadline 2018 can be met.” Could Hungary clarify if these two EDGs will be used only for severe accident management or also for core melt prevention and possible SFP accident prevention?
283 | Hungary | 2.2 | p63 | Part V p63 Progress in the Action Plan: concerning the 2 above mentioned EDGs, it is a commendable aspect that deadline 2018 can be met : if this deadline is so far, does it mean that the corresponding equipment protected against external hazard requires the implementation of heavy infrastructures ? Pending this deadline is it considered the installation of provisional emergency power supplies?
284 | Hungary | 2.2 | Task 27 p46 | “Possible cross-links shall be studied and the concluding modifications shall be carried out for providing safety electrical power supply from any operable emergency diesel generator in any unit to the safety consumers of any other unit.” As said in the peer review report, “the possibilities of interconnection of existing equipment are beneficial. However it might also lead to loss of separation. Such improvements or modifications should be prepared carefully. Before the implementation, separation issues should be investigated.” Could Hungary clarify whether this preliminary work has been performed?
285 | Lithuania | 2.2 & 2.3 | p12 | It is a commendable aspect that all the technical measures on design issues have already been completed except action 13. This action is related to the sub-module of the plant computer information system which will provide information about the water temperature and level measurements in spent fuel storage pools as well as radiation level in the spent fuel storage pools halls from both units during and after beyond design-basis accident. From the comment in the table it appears that some works are completed (hardware options for DBAs and data transmissions both to the computer information system of organization of emergency preparedness and to the accident management centre of VATESI) and other works related to installation of the new water level measuring equipment for BDBAs conditions are still in progress. Could Lithuania specified why this remaining work postpones the deadline from 2013 to 2015?
286 | Lithuania | 2.3 | p8-9 | Concerning natural hazards (actions 4 and 5 related to the study of the spent fuel cask tip over in case of earthquake during transportation) the deadlines are revised from 2013 to 2017 taking into account updated schedule of the Ignalina NPP Interim Spent Fuel Storage Facility (ISFSF designed to withstand an intensity of 7 on the MSK 64 scale with a PGA of 0.1g) construction project. Could Lithuania clarify why the new project of ISFSF is delayed for 4 years in so far as the seismic assumptions for its construction have not change since 2013 ?
287 | Netherlands | 2.3 | p94 | Emergency Response Centre (ERC) - study and consider options to better protect ERC like alternative location ERC, new building, strengthening current building etc. It is explained that on-going discussions about the earthquake risk, the exact location of the new building and the building type caused project delays from mid-2014 to 2017. In so far as this delay concerns only studies, could Netherlands clarify the new delay for the implementation and realization of the associated works?
288 | Netherlands | 2.2 | p97 Action 9 | Reduction of the time necessary to connect the mobile diesel generator to Emergency Grid to 2 hours. A tractor and trained personnel is constantly available on site to transport the diesel generator from its parking position to the connection point. However, as explained in the National Report, if a truck is considered to be light equipment, in the postulated scenario of ENSREG it will be available 24 hours after LOOP started; if this truck is considered to be heavy equipment, during the first 24 hours no credits can be given to the mobile EDG. How this issue has been dealt with to ensure this mean can be quickly implemented in case of SBO? Does it mean that the truck considered in the National Report was not parked on the site while the new tractor is constantly available on the site?
289 | Netherlands | 2.2 & 2.5 | p31 | Concerning the reassessment of alternative power sources (alternative to emergency grids) including reassessment of the possibility of having extra fixed external connections for mobile diesel generator. The study is completed, additional connection points to mobile power will be implemented. Could Netherlands specify whether implementation of alternative power sources has been decided?
290 | Netherlands | 2.2 | p35 | The actions 6, 7 and 29 relative to the SFP cooling are considered there as design issues while they are considered as part of SAMG in Table 8.1. Could Netherlands clarify this point?
291 | Romania | 2.5 | Table 1 Action 29 p24 | It is indicated that review of Level 1 & 2 PSA has been finalized in 2013 as planned. Moreover, from the CNS report page 4 and 5 (§1.2.1.a.1 Review of the design basis earthquake), in 2004 a probabilistic seismic hazard analysis (PSHA) was carried out for the Cernavoda NPP to support a seismic Probabilistic Safety Assessment (PSA). Could Romania clarify whether the review above mentioned take into account the conclusions of this seismic PSA? Is that all lessons that have been learned from this seismic PSA and is there a revised version in progress following the Fukushima accident?
292 | Romania | 2.2 | Table 1 Action 10 p16 | In the Peer Review Romanian Report, §213, it is noted: “There is only little information about margins to cliff edges, weak points and no evidences that further improvements in the seismic upgrading have been considered. Further work is proposed in this area and it is recommended that the CNCAN obtains good quality programmes from the licensees and ensures that the work is appropriately followed up.” The action 10 of the NAcP is expected to meet this recommendation. However, the target date to implement this action (“Depending on the development of a common methodology, at EU-level, for assessing margins to cliff-edge effects due to external events”) may be distant and push too far its implementation. Could Romania clarify this point? In the updated NAcP, there is no progress in so far as the action is always planned but without target and time frame. How to take this action which seems to be blocked ?
293 | Slovak Republic | 1.1 | p14 | It is a commendable aspect that in the main table p14 covering all the topics, the status on the fulfilment of recommendation has been completed in a detailed manner.
294 | Slovak Republic | 1.1 & 2.2 | p18 | Action 7 p 18 – One French comment in 2013 was the following: ‘Secondary effects of earthquake seem to be taken into account only for potential interaction between SSC in Bohunice NPP (Initial NAcP table pages 7 and 8). Action 7 should be clarified (fire, explosion, flooding…).” It is quoted p18 about Action 7 that for all NPPs, “Updated scenarios were incorporated into Operating Instructions for Emergency Situations.” However could Slovakia clarify if other effects than potential interaction between SSC are considered?
295 | Slovak Republic | 1.1 & 2.2 | p15 Action 4 | Regarding the resistance of selected SSC at extreme external events, France asked these 2 questions: in 2013 could you confirm that: 1) Relevant combinations of hazards would be considered? 2) A probability notably less than once per 10,000 years would be considered for a set of SSCs? In the revised NAcP it is specified that: New metrological studies for the site were developed for Bohunice (EBO) and Mochovce (EMO) NPP. In 2013 a draft time schedule of implementation of measures for 2014 – 2018 to enhance the resistance of selected EBO and EMO civil structures was prepared over, and an overall assessment of impacts of extreme meteorological events on safety and reliability of EBO civil structures, was prepared. Measures resulting from assessment of EMO1,2 civil structures are being incorporated into the on-going seismic reinforcement documentation. Under these assumptions, could Slovakia clarify how does it answer to the 2 above questions. For EBO, are there sufficient margins for combination of relevant hazards and for the consideration a probability notably less than once per 10,000 years?
296 | Slovenia | 2.3 | p23 | It is written in the conclusion of the updated NAcP: “In 2013 the Krško NPP applied for the extension of deadline for the implementation of the SUP due to several different reasons. The SNSA approved the extension of the deadline until the end of 2018. Yet even today the future of one part of the SUP (Safety Upgrade Program) is still uncertain due to the owners’ doubts about financial sustainability of the project”. For instance, for action 1.2 of the SUP “New pump for supplying SGs; in a bunkered building with a dedicated water supply”, the initial target was 2015 but now in the updated version the finalization is foreseen after 2018. Even if there is an important shift in the delay how to explain why this delay is not limited?
297 | Slovenia | 2.2 | p13 | §5.1.1: The revision of the 2004 Seismic PSA: “Taking into account the results of investigations carried up to now it was concluded that the assumptions considered in 2004 seismic hazard analysis for the Krško site are defendable even against these new seismological assessments. Thus no immediate measures are planned to implement the recent findings into an existing seismic hazard assessment for the Krško NPP. Further revision of seismic hazard assessment as well as seismic probabilistic safety assessment will be considered when all ongoing investigations are complete.” As the Krško NPP is located in a seismically active region (as reminded in the Slovenian National Report), these investigations are important. So is it possible to give a deadline for the completeness of these ongoing geological and seismological investigations?
298 | Spain | 2.2 | p19 | The meaning of the following comment should be clarified: “In summary it may be stated that no significant aspects are appreciated that might have an impact on the basic objectives of the Plan”. Does it means that there is no additional important mean to implement and that the provisions, modifications and procedures coming from the plants analysis are consistent with the initial planning for safety and robustness improvement of the NPPs?
299 | Spain | 2.2 | p19 | Mention may be made of the following relevant aspects that have now been completed: Implementation at all the nuclear sites of mobile equipment (pumps, electrical generators, etc.) allowing for quick connection to the fixed systems of the plants. What should be understood by "quick connection" in case of SBO? Less than 10 hours?
300 | Spain | 2.5 | p19 | Also already completed: Verification and, where appropriate, reinforcement of the seismic resistance capacity of equipment of importance for accident management to a “seismic margin” of 0.3 g (PGA). What type of structural elements and components were reviewed? What is already completed: the identification of the equipment to reinforce or the next step which is the reinforcement by itself?
301 | Spain | 2.3 | Table A-1-1 pA3 | “Analysis of the suitability of the human resources currently assigned to the ORE (emergency response organisation). Implementation of improvements deriving from the analysis.” This requirement doesn’t refer to multiunit events as it was the case in the initial NAcP. Shall we consider that this reference is implicit or is there a change in the requirement?
302 | Sweden | 1.1 | p30 | Some of the actions of §5, especially those to be performed by the licensees, are already included in the measures developed in § 2 and § 3. The existence of two sets of measures/actions at national and local levels could be an issue for ensuring consistency between them. For example, on one side page 34 §5.3.2 the issue on the accessibility and functionality of the ordinary on-site emergency control center and the alternative emergency control center and on another side page 27 §3.2.8 the issue on the accessibility of the emergency control center, is there a difference between the 2 set of issues in so far as they are handled within the same framework of action in response to the requirements of the new emergency regulations, SSMFS 2014: 2?
303 | Sweden | 2.2 | p17 | In the NAcP, the action T1.LA.5 does not clearly stipulate all cases studies for the combination of high sea water level and other external phenomena. Could Sweden specify combinations analysed between high sea water level and other external phenomena?
304 | Sweden | 2.2 | p43 | From the new table 1 page 43 it is maintained that this work will be completed in 2015 but there is no additional information concerning the combination of high sea water level and other external phenomena. Could Sweden clarify this point?
305 | Switzerland | 1.1 & 2.2 | p45 | It is a commendable aspect to note that the updated NAcP includes in Part IV (“implementation of activities”) tables 8.1 (Cross-reference table: ENSREG recommendations and ENSI post-Fukushima actions) and 8.2 (Cross-reference table: recommendations resulting from CNS 2nd Extraordinary Meeting and ENSI post-Fukushima actions) with links to check points and open points. The deadlines associated to these points is probably still missing. Could Switzerland clarify this point?
306 | Switzerland | 2.2 | p15 | The peer review country report mentions that a feasibility study for the need of installation of an automatic scram system is required by the regulator. In the updated NAcP it is stated: “In 2014, ENSI is analysing the advantages and disadvantages of an automatic shutdown of the plants triggered by the seismic instrumentation. Depending on the results of the analysis, upgrades could be initiated.” Could Switzerland clarify what are the deadlines for knowing the results of the analysis and also whether 2017 remains the deadline for the possible upgrades implementation?
307 | Switzerland | 2.2 | p21 | From the updated NAcP : “In order to limit the consequences of an internal flooding that could affect more than one safety system, the Mühleberg NPP has taken measures both on the preventive side, by reducing the amount of water that could be released after pipe breaks, and on the coping side ,with plans of backfitting an additional line for RPV injection as accident management measure”. Could Switzerland clarify what is the deadline for the implementation of this additional line?
308 | UK | 2.2 | General | In the UK peer review report, the reviewers made ​​a number of recommendations and conclusions. To address these comments, UK refer to the Stress Tests Findings (STFs already mentioned in the national final report in December 2011). Could UK precise for each recommendation mentioned in the country report peer review, the changes made ​​to the findings (question already asked as part of the peer review process of NAcP in 2013)? Could UK clarify whether the STFs have changed or been completed to account for the UK Peer Review?
309 | UK | 2.2 | p41 | p41 updated NAcP and p15 UK Peer Review Report: One reviewer’s conclusion is that in some cases, there is no satisfactory evidence of capability of plant beyond design basis (e.g tsunami, lightning). Cliff edge effects beyond design basis have not been established in a consistent manner for external hazards, ONR has raised findings on these issues. Could UK clarify whether STF 5 which considers hazard margins for wave events and extreme weather meet this recommendation?
310 | Ukraine | 2.2 | p16 Item 22 | It is mentioned that the analysis of the need and possibility to qualify power unit components that may be involved in severe accident management for harsh environments is ongoing; more precisely, at the beginning of 2015, the operating organization completed analysis of the need and possibility to increase harsh environment qualification of power unit components (for pilot units: RNPP-1, SUNPP-1 and ZNPP-1) that may/must be involved in severe accident management. The analysis results are under SNRIU review. Could SNRIU clarify what is the status of the new PORVs (Pilot Operated Relief Valves) concerning their qualification in case of severe accident? Indeed it was already specified in the initial NAcP (page 12) that they have been replaced at all NPP units by safety valves qualified for the feed & bleed mode and that the operability of equipment for depressurization of the reactor coolant system will be verified during qualification of equipment involved in severe accident management.
311 | Ukraine | 2.3 | action 3/p6 & 11 action 16/p7 & 15 | Country report recommends to take into account “the risk induced simultaneously by reactor and SFP in case of a severe accident should be assessed (for example in L2 PSA)”. Moreover, the initial NAcP did not provide a detailed answer to the country report recommendation. In the updated NAcP Item 3, page 11, it is mentioned: “Consideration of a full range of initiating events for all reactor and SFP states in PSA. This measure is intended to perform probabilistic safety assessments of levels 1 and 2 for a full range of initiating events (including natural hazards) for all regulated states of the power unit, covering both the reactor core and spent fuel pool.” But again, it is not clearly identified that simultaneous accidents would be considered. Could Ukraine detail the actions with regards to simultaneous accidents in reactor and SFP (with several units affected)?
312 | Belgium | General | General | Are findings (flaws in the RPVs) at Doel-3 and Tihange-2 influencing the schedule and completion of items of the NAcP of Belgium? It doesn't seem to be rational to carry out significant modifications before it is clarified whether the plants can be restarted or not.
313 | Belgium | General | eg. 8-9 | What is the current situation with Doel 1-2 with respect to final shut down or LTO? If LTO is to be approved, will the completion of all NAcP actions be condition of LTO licensing?
314 | Belgium | 1 | 8 | "At Tihange 1, the licensee classified the Electrical Auxiliary Building (BAE) as having a medium probability to resist a RLE. Although a medium probability is acceptable in the context of the stress tests, the licensee committed to evaluating the feasibility of raising the BAE to a high probability of resistance." what does it mean in technically precise terms "medium probability to resist"?
315 | Bulgaria | 2 | 41,43,55, 33 | Some of the "new measures" defined in Attachment 4 in relation to A-1-1 could have been understood as substantial components of the original measure: e.g. FA-1-1-2 and FA-1-1-4, since without appropriate storage for the DGs and without the option to reload batteries the original task A-1-1 does not seem to be complete. What is the justification of closing A-1-1 without these items? See also bullet 1 on page 33: – The Kozloduy NPP considers delivering of the two additional mobile generators. As long as these mobile generators will be considered for beyond design basis events, they should be adequately protected for such events. – included in measure A-1-1;
316 | Bulgaria | 3 | 32.49 | The measures D-2-6 and D-2-7 are referred in the list under Part III.1. (p. 32), which list is introuduced so that "which have been addressed in topics 1 through 3 and are included in Attachment 1 of the plan:". However, these measures are not shown in the table of Attacment 1, only in Attachment 3, where for D-2-6 hints for re-scheduling are given. Please, explain the causes for re-scheduling and also the actual meaning of the category "Additional Activities".
317 | Bulgaria | 1 | 7 | The confidence level for the annual frequencies of exceedance is not indicated. Are these annaula frequencies mean or meadian estimates?
318 | Bulgaria | 1 | 7 | "The extreme winds for the region of the site are evaluated at 1E-4 frequency of occurrence and at 1E-6 – for tornado." What is the Enhanced F-scale of the 10E-6/a tornado? Are some new information available? The information regarding tornado hazard given in BG_Report_EN.pdf refere to a large area.
319 | Bulgaria | 1 | 7 | "The report presents and analyses the results from possible earthquake secondary effects such as floods or fires, considered in the Kozloduy NPP Seismic Probabilistic Safety Assessment (PSA). The most conservative scenario is analyzed for a catastrophic wave caused by a sudden and complete damage of the Hydro-power Facilities Zhelezni Vrata 1 & 2, resulting from a beyond design basis earthquake in combination with maximum water level of the Danube" This combination of events seems to be rather conservative. It seems, that the combination earthquake and fire caused by earthquake could be more probable?
320 | Czech Republic | 3 | 8 | Will an IVR scheme with external vessel cooling be also implemented for the Temelin plant?
321 | Czech Republic | 3 | 9 | Heat removal from the containment will be solved with spraying instead of venting. What kind of spray system is foreseen for the management of severe accident? What would be the electrical source and what would be the heat sink?
322 | Czech Republic | 2 | 68 | What would be the water source for back-up coolant supply into the depressurized reactor and storage pools? How this additional water source would be properly borated?
323 | Czech Republic | 3 (3.3) | 6 of 78, 7 of 78, 8 of 78, 72 of 78 (Action 48) | IVR (in vessel retention) of core melt for VVER 440 units: The time frame on page 8 (10 + years) is not in line with the completion target (2015) on page 72. Were there international exchanges on analitycal and experimental results of this issue wih other countries operating VVER 440 units?
324 | Czech Republic | n. a. | 68 of 78 | Please clarify the difference between the "implemented" and "finished" status of a given action (e.g. actions 8 and 9)
325 | Finland | 3 | 16 | Regarding the spent fuel pools, the approach is to "practically eliminate" the events involving fuel damage in the pools. What are the criteria that allow or support such elimination? Does the practical elimination also mean that even SAMG (containing possible operator actions that would be carried out at least to avoid unnecessary worsening of the situation) is not required and not developed for those supposedly rare and eliminated events?
326 | Finland | 3 | 27 | The radioactive material is assumed to be maintained inside the containment and there is a claim that it is not necessary to treat large amounts of contaminated water outside the containment. Is the leaktightness of the containment with all the auxiliary systems ensured for the long term (for months) after a severe accident? Are there any creteria for opening of the containment for long (stabilisation, clean-up etc.) term actions.
327 | Finland | 1 | 7(51) | The confidence level for the annual frequencies of exceedance is not indicated. Was the 10E-4/a a mean estimate? Is the 10E-5/a a meadian one?
328 | Finland | 1 | 7(51) | Are the requirements for analysis of the sieimic safety for DEC C conditions identified by the Finnish Regulations?
329 | Finland | 1 | 9(51) | "In accordance with the new regulatory YVL Guides, STUK has required that the licensees review and update the site specific seismic hazard in connection with the periodic safety reviews." Are you aware of that the new hazard evaluation can result in a controversal result, hence the 10E-5/a median PGA might be smaller than the former 10E-4/a mean PGA?
330 | Finland | 1 |  | There is no mentioning of the man-made hazards.
331 | Finland | 2 | 12 | The alternative heat removal system was or not implemented in 2014?
332 | Finland | n. a. | 48 (51) | It is not clear to which Action/Activity the remark with asterisk (*) is related below table 2. (May be the relevant part within the table wass deleted or modified.)
333 | Finland | 3 | 48 (51) | Action/Activity 213 in table 3 marked as "In progress", although its schedule is set as 2013. As the updated version of the National Action Plan is dated December 2014, it needs clarification.
334 | France | 3 | 51 | The licensee is committed to supplement its severe accident management procedures to cover spent fuel pool accident in the fuel building. What kind of spent fuel pool accidents are foreseen? Will the existing set of SAMGs be extended to the events involving the following: extensive fuel damage, melt-down in the pool, hydrogen concentration and pressure build up in the building, high radiation environment in the fuel building, etc.?
335 | France | n.a | 8 | Taking into account the numerous NPP sites how did the ASN supervise the implementation of modifications taken place in Phase 1? How the ASN keeps track of status of the actions in progress?
336 | France | n.a | 9 | Are the Phase 3 modifications preconditions of long term (beyond 40 years) operation of the reactors?
337 | France | n.a | 51 | ECS – 35.III: Severe accident management training One of the actions are: "EDF sub-contractors are not involved in emergency situations." Is that a mistake or if no, what does this sentence mean?
338 | France | n.a | 70 | What is the planned date in France to completely incorporate the post-Fukushima WENRA RLs into the French regulatroy system?
339 | Slovak Republic | 3 | 11 | There is an ongoing activity to analyse the feasibility of filtered venting of the containment. Are there any alternative solutions analysed in case the filtered venting would be found as unfeasible mean for containment long term heat removal?
340 | Slovak Republic | 1 | 15 | What kind of civil structures are affected and what kind of measures have to be implemented to enhance the resistance againts extreme weather events?
341 | Slovak Republic | 2 | 25 | Do the tests carried out for mobile feed water sources included testing of the entire systems with injection lines up-to the SGs or were restricted to the mobile pumps?
342 | Slovak Republic | 2 | 32 | What are the most important operator actions included in the procedure used in case of RCP desealing?
343 | Slovak Republic | 2 | 33 | What kind of experiments were carried out to prove resistance of the RCP seals without cooling for 72 hours?
344 | Slovak Republic | 3 | 36 | Have the accumulation of the hydrogen in the reactor hall been studied in case of severe accidents occurring separately or simultaneously in spent fuel pool(s) and open reactor pressure vessel?
345 | Slovak Republic | 1 | 14-15 | What kind of technical solutions do you use for the containment long-term heat removal? Do you use passiv system? If active, then how do you supply the system with electricity? The system will be constructed untill the end of 2015 or only the feasibility study will be ready?
346 | Slovak Republic | 1 | 15-16 | What is the frequency of events that you understand under "extreme meteorological events"? Could you define the loads which the civil structures should withstand?
347 | Slovak Republic | 3 | 63 | Item 49: What type of equipment is selected for remote control?
348 | Slovak Republic | 3 | 63 | Item 49: How the funcionality of the centre will be provided during the seismic reinforcement implementation? What is the deadline for the project?
349 | Spain | 3 | 20 | It is mentioned that the BWR plants are already fitted with "hard vent". Some explanation would be useful to clarify the relation of that venting system to the severe accident filtered venting.
350 | Spain | 1 | 20 | Could you clarify what kind of uncertainties are of concern in relation to the dam rupture scenarios?
351 | UK | 1 | 8,41,47,59 | It is not completely clear how it is possible that the studies are not completed yet or not reviewed so far, but the related resilience modifications are already completed. Is it not possible that after the full completion of the studies and their review some further modification could become necessary?
352 | UK | 3 | 50 | The task 3.2.5 was scheduled for the end of 2014. Has it been successfully completed at all plants? (IR-22 - Provision on-site of emergency control, instrumentation and communication STF-15 - Facilities for remote indication of plant status)
353 | Belgium | general | Ch2/p6 | In paragraph b the number of 350 actions is mentioned. In paragraph c an additional number of actions is mentioned, but without a number. Can you expand a bit about the number of additional actions and their nature?
354 | Belgium | topic 1 | Ch3/p7 | In paragraph 3.1.1 you mention the fact that D1 and D2 were not assessed because of imminent shutdown. When will the Action Plan with the measures for Doel 1 and Doel 2 become available to the ENSREG members and the public?
355 | Belgium | topic 1 | Ch3/p7 | Could you provide the results of the final Electrabel report about the Tihange seismic hazard evaluation?
356 | Belgium | topic 1 | CH3/p8 | The RLE is based foll reactors except D1/2 on 1.7 times the PGA of the DBE. Internationally practised multiplication factors lie between 1.3 and 1.7. What did Belgium decide to use the upper bound value? For Tihange a non-confirmed higher PGA was found than the earlier value. Was this value used in the SMA or the existing value? Is Belgium using Seismic PSA as a tool or are there plans to do so?
357 | Belgium | topic 2 | Ch3/pl7 | In paragraph 3.2.1, third bullet ELIA rejected an Electrabel proposal. It is unclear to us what the proposal was, what happened after that, and what the role of FANC was. Can you expand on that?
358 | Belgium | topic 2 | Ch3/19 | In paragraph 3.2.2, first bullet. Can you please explain why the proposed conclusion/action was not satisfactory and what happened after that? Will this lead to further delays and how much?
359 | Belgium | topic 3 | Ch3/p22 | In paragraph 3.3.2, first bullet. What was the role of the regulator in the dertermination of the specification of the COS? What are the bases and values of the "defined" specification? What is the impact of the non-consolidated DBE of Tihange?
360 | Bulgaria | general | Introduction/p4-5 | Why are the additional measures in the NAcP limited to the study outcomes, and not also determined by further Fukushima-lessons-learned?
361 | Bulgaria | topic 3 | PART IV/A/p34 | What is the expected year of implementation of the in-vessel retention strategy?
362 | Bulgaria | general | PART IV/B/p35 | As a reason for delay, four points are mentioned. The third reason "transformation of comprehensive measures into several activities with implementation terms" as such, does seem an unusual reason for delay. Can you explain why splitting the original measure into a number of different measures does lead to delay?
363 | Bulgaria | topic 3 | PART IV/p37 | Dl-2: what are the extreme hazard design criteria that are applied? Were updated Wenra RLs applied or the 1:10000 risk value? Why does the ERC not seem to have a design against earthquakes like the bunkers for MDGs?
364 | Bulgaria | topic 3 | PART IV/p37 | D2-4: the reason for the delay of each of the FDs remains unclear/not mentioned
365 | Bulgaria | topic 3 | PART IV/p41 | MDG Bunkers: for earthquake a 50% on top the DBE is taken. What about the other severe conditions? Offsite ERC: how far will it be located from the NPP and why? Part will be above and part under ground. Can you please explain for what purposes this configuration has been chosen?
366 | Bulgaria | topic 3 | PART IV/p43 | A3-1: Are provisions foreseen/available to clear the access roads (bulldozer etc.) and what will happen if in the end no access road is available?
367 | Czech Republic | topic 3 | Ch 1 / p.7 | You describe that the proposed Ex Vessel Cooling strategy is effective in maintaining containment integrity but that "Refractory material choice and its experimental verification and its experimental verification and design of lining remain outstanding issues". Is it already clear when these issues may be resolved?
368 | Czech Republic | topic 3 | Ch 1 / p.8 | It is stated that the necessity of installing a hardened filtered venting has not been proven for the Ex-Vessel-Cooling (ExVC) scenario. Are there any other scenario's possible, for example due to a failure of the ExVC system, where a filtered venting system would be beneficial? You also describe that containment spraying is sufficient for removing heat after corium flooding, thus suggesting a filtered venting system has no additional benefit. Will this also be the case in scenarios with long periods of station blackout? And will your conclusions also be applicable to other reactor types in Europe?
369 | Czech Republic | general | Ch 1/ p.8 | The ambitious schedule is described as a challenge as well as a good practice. Could you elaborate on which parts are especially challenging and which parts will be less difficult to achieve?
370 | Czech Republic | topic 1 | Ch3.1.6, page 18 | You have developed plant walk-downs for flooding and procedures for extreme weather. Will Czech Republic also implement a specific methodology for seismic plant walk-downs ?
371 | Czech Republic | topic 2 | CH3.2, page 23 | From the NAcP document it is not completely clear how Czech Republic is dealing with loss of ultimate heatsink. Will there be modifications at both sites to implement alternative ultimate heatsinks?
372 | Czech Republic | topic 3 | Ch3.3.13, page 56 | From the Nacp it is not completely clear how the ENSREG recommendation to implement a provision of an on-site emergency centre protected against severe natural hazards and radioactieve releases, will be fulfilled. Can you explain if new ECCs will be build at both sites?
373 | Czech Republic | topic 1 | Ch3.2.14, page 38 | Do NPPs in Czech Republic have bunkered back-up systems for all safety functions?
374 | Czech Republic | topic 1 | Ch3.3.15, page 58 | Can you explain to what level PSA is used in NPPs in Czech Republic? Is PSA level 2 implemented for all plant states?
375 | Finland | topic 1 | PartI/par1.1/p7-9 | The seimic levels in Finland are very low, even below 0,1g. Why has it been decided to require seismic PSA in stead of Seismic Margin Assessment? What are the advantages/disadvantages of both? Can STUK specify which requirements are set to update the site specific seismic hazard?
376 | Finland | topic 1 | PartI/par1.1/p9 | Seismic improvements will take place when components are replaced due to ageing. What is the rationale behind this?
377 | Finland | topic 1 | PartI/1.2/p10 | Decision to improve seawater flood protection in 2015. What will be the expected implementation of the improvements?
378 | Finland | topic 1 | PartI/1.2/p10 | STUK will consider the capacity of the drainage system. When will this be ready?
379 | Finland | topic 1 | PartI/1.6/p11 | What is your plan to develop more rigorous guidance for walkdowns?
380 | Finland | topic 2 | PartI/2.1/p13 | The ACIS: will it be a bunkered system? Please specify the design requirements against extreme events.
381 | Finland | topic 2 | PartI/2.1/p13 | Paragraph starting with "the licensee has assessed possibilities….normal systems are lost". Please explain in some more detail what options might be available for OL3
382 | Finland | topic 2 | PartI/2.3/p15 | Why will the depletion times of the batteries be substantially lengthened through the ongoing automation renewal project. Please give some more details.
383 | Finland | topic 2 | PartI/2.3/p15 | Last alinea: is there no battery charging by dieselgenerators foreseen in OL3?
384 | Finland | topic 2 | PartI/2.4/p16 | Independent air-cooled cooling units..is under implementation. In 2.1 it was written that it was implemented in 2014. What is right?
385 | Finland | topic 2 | PartI/2.5/p17 | It seems that the implementation of mobile pumps was delayed at least one year and the decision is still pending because of combination with another project. Please give a somewhat more detialed reasoning for the delay.
386 | Finland | topic 3 | PartI/3.1/p19 | Is there no ex-vessel retention at Loviisa, when in-vessel retention fales? Is in-vessel retention at OL1/2 not possible?
387 | Finland | topic 3 | PartI/3.2/p23 | What is TDCF and LLERF for OL1,OL2, L1 and L2. For those values that are still to high: what strategy is followed to bring them down according the principle of continuous improvement? What are the main contributors to the higher values that could be improved?
388 | Finland | topic 3 | PartI/3.4/p25 and PartII/5.4/p38 | For emergency exercises explain more on the frequency and content of the long-duration events that are exercised, including the way how stressful conditions are trained. Also specify what is the duration and frequency of the long-duration excercises
389 | Finland | topic 3 | PartI/3.5/p25 | The Reserve Emergency Centers: what minimum distances from the NPP are required for the remote location? What are the design requirements? Are they also protected against extreme external events?
390 | Finland | topic 3 | PartI/3.5/p26 | Large volumes contaminated water: the design strategy is understood, but for reasons of contingency it might be considered to have a plan how to deal with the failure of the strategy. Please comment.
391 | Finland | topic 3 | PartI/3.5/p27 | What are the (beyond) design requirements of the SAM control room at Loviisa? How is electricity secured and communications.
392 | Finland | topic 3 | PartI/3.5/p28 | It is written that "at the moment" there are no emergency control rooms at OL1/2. What does this mean for the future?
393 | Finland | topic 4, nat org. | PartII/4.2/p32 | IRRS recommendations: the inspection effectiveness should be improved. In what way will they be improved? How does defence in depth have a role in this? The qualification of inspectors formalized: what are the plans to do this and how much time will it take to realize?
394 | Finland | topic 5, EPR & PAM | PartII/5.1/p36 | The launch of the National Nuclear Power Plant Emergency Peparedness Forum, combined with the permanent coordination groups could be considered as a good practice.
395 | France | topic 3 | Page 6 | As understood, France has evaluated the use of existing systems for filtered containment venting designed for DBA, and decided not to use them in case of severe accidents. Will France, in the light of this conclusion, implement filtered containment venting systems designed for severe accidents or adapt the existing systems? Could you elaborate on the filtered venting in DB and Beyond DB conditions?
396 | France | topic 1 | Ch1, page 8 | France is reinforcing the earthquake and flood resistance of emergency management premises. Are the design requirements in line with the ENSREG recommendation of a return frequency of at least 10-4/yr? In other words: would it be acceptable to have a lower resistance for emergency managent premises than for bunkered safety systems and the reactor building?
397 | France | topic 1 | Ch1, page 9 | Hardened safety core: will these systems be independent from the existing safety systems? What is the rationale behind the design requirements for the buildings and systems of the hardened safety core against extreme events (SSE+50% and return period for extreme weather conditions)? Will these systems and buildings only be implemented after 2020?
398 | France | topic 1 | Ch1.1.1, page 11 | When will France have completed probabilistic seismic hazard analyses for each site and have implemented upgrading of the design basis?
399 | France | topic 1 | Ch1.1.2, page 14 | The analyses for the seismic design of the fire-fighting systems were completed by the end of 2012. Nevertheless the implementation of associated modifications has been rescheduled/delayed (and aligned with the PSRs)? Could you expand on that?
400 | France | topic 2 | Ch1.2.8, page 32 | The ensreg peer review recommendation about main and emergency control rooms espect measures for MCR, ECR and ECC. The measures in France only seem to deal with MCR and ECC. Do the plants in France have implemented ECR' or are they planned in the concept of hardened safety core?
401 | France | topic 2 | Ch1.2.10, page 36 | Since Advisory Group of Experts is planned only after more than 2 years (even 4 years for certain topics) after proposal of possible measures, the practical implementation of measures might be delayed for more than two years. Does ASN think this is a acceptable practice?
402 | France | topic 3 | Ch1.3.4, page 48 | Can you elaborate on this section and the scheduling of the implementation of SAMGs for SFP, shutdown states and multi-unit events. It seems that implementation is dependent on other measures and will take a long time?
403 | Germany | topic 3 | p.22 | GKN II/DWR, Nr.6. "additional studies into H2 propagation have been carried out" - what were the conclusions; did they result in additional measures?
404 | Germany | general | p.24, top | GKN II/PWR, Nr.14. What is the current status of the robustness analysis, or will you report about that at the upcoming review meeting?
405 | Germany | topic 3 | p.28-30 | KKE/PWR, Nr.5. An emergency measure is introduced (for initiating accumulator injection in midloop operation). However it is stated: "The review of the activity/measure by the supervisory authority has not yet been concluded". Will you report about that at the upcoming review meeting? Same question for KKE/PWR Nr.14 and nr.17 (p.29) and Nr.21, p.30.
406 | Germany | topic 5, EPR & PAM | p.64 | M-4, status says planned conclusion in 2014. What was the outcome of the review of the German regulations and guidelines for off-site emergency response?
407 | Hungary | general | Introduction/p9 | Could you provide the new deadlines that will be determined beginning of 2015?
408 | Hungary | topic 1 | PartV/p62 | For the tasks 3 and 4 please provide the new planning dates for completion.
409 | Hungary | topic 1 | PartV/p63 | For task 11 part will be completed beginning 2015. What about the rest? When will it be ready?
410 | Hungary | topic 3 | PartV/p68 | For task 46 the claim is that it is completed, but you also mention that problems need to solved. Can you elaborate on that?
411 | Hungary | topic 3 | PartV/p68 | Tasks 47, 48 and 49 seem to be more closely related than was apparent from the original planning. Task 48 is determined by 47 and 47 is determined by 49. Can you provide clarity on the delay of 48 and what might be the delay of 47? Will that shift into 2019/2020?
412 | Hungary | topic 4, nat org | PartV/p68 | It is not readily apparent from task 50 what the relation with the text in the last column is. Could you provide more information about the actions to improve the position of the regulatory body?
413 | Romania | topic 5 | topic 3, SAMG (on site) section 3.1, p. 8 and topic 5 (EP&R off-site), p. 10 | On pag 8 it is stated: "The licensee's organisation for accident management and emergency response has been found adequate.". Can you comment on the adequacy of the national organisation (off-site)? Is that adequate too?
414 | Romania | topic 3 | p.17 | Action 13. Fire fighting truck and flexible conduits are mentioned as a means to provide coolant dring emergency conditions. From what source(s) will these means draw water?
415 | Slovak Republic | topic 4, nat org | general information, page 6 | An amendment to the Atomic Act relates to new provisions to finance nuclear regulatory activities. Could you elaborate on these provisions? Are the licensees involved? Which provisions are in force? Do these provisions cover all costs or only part of them?
416 | Slovak Republic | topic 3 | Status of implementation, ID 22, page 31 | "The technical specification and procurement of the mobile measuring unit in progress.". What is the time frame for completing this measure?
417 | Slovak Republic | topic 3 | Status of implementation, ID 25, pag 34 | Can you elaborate on the "additional measures resulting from the analyses" of the environmental condition in MCR and ERC etc. Which additional measures re being considered? What is de planning for implementation of these measures?
418 | Slovak Republic | topic 3 | p.37 | ID 27bis, page 37, SFP and simultanuous accidents at multiple units, its says: 'A plan of implementation of additional measures is under preparation'. Can you expand on this in somewhat more detail?
419 | Slovak Republic | topic 3 | p.38 | ID.28. In emergency situations, where do the mobile feed water make-up pumps (to SGs) draw their water from?
420 | Slovak Republic | topic 3 | Status of implementation, ID 40 | What is the deadline for finishing the project to update the SAMG's with regard to potential damage to infrastructure etc.?
421 | Slovak Republic | topic 2 | p.42 | ID 29, new shelters for mobile DGs are mentioned. What are the design requirements of these buildings, can they survive severe external hazards (including earthquakes) with low return frequencies?
422 | Slovak Republic | topic 3 | Status of implementation, ID 46, 47, p.59 | What is the expected deadline for finishing these projects?
423 | Slovak Republic | topic 3 | Status of implementation, ID 54 | Can you elaborate on the "replacement of seals at the reactor pressure vessel cavity lids and doors" which is in progress. Why did you decide to replace these and what were the new design requirements?
424 | Slovak Republic | topic 3 | general | Could you elaborate on the existing in-vessel corium retention capabilities at the Slovakian plants?
425 | Slovak Republic | topic 3 | p.61 | ID 49. At 'status' it is mentioned that remote control of some equipment has been considered. What kind of equipment has been selected for remote control?
426 | Slovak Republic | topic 6, int cooperation | p.65 | ID 57. Are there cross border cooperations regarding emergency management?
427 | Slovenia | topic 3 | P IV / CH 1 / p 4 | On page 4 in the NAcP you state that by June 2011 the accelerated B.5.b requirements where implemented 'to a large extend'. It is not entirely clear if and when the remaining improvements were implemented, could you elaborate on the nature and cause of the delay on these improvements?
428 | Slovenia | topic 2, topic 3 | P IV /p.14 | Several delays are mentioned on page 14 and others regarding the implementation of SUP as well as the associated risks involved for the continuation of the operation of the Krsko plant. How was the prioritization and planning of the measures decided on? And can further delays jeapordize the continued operation of the NPP?
429 | Slovenia | topic 4 | Ch4, page 13 | Could you elaborate on how action 11 is executed, especially concerning safety culture (required actions, evaluation and detection)?
430 | Slovenia | topic 2 | P IV / Ch 5 / p 16 | It is mentioned in Action #2 on top of page 16 that the SNSA will examing the need to draw new requirements concerning LOOP, SBO and loss of UHS. Has this been finalized yet? What was the result from that investigation? Was it necessary to add additional requirements concerning these topics?
431 | Slovenia | topic 6, int cooperation | P IV / Ch 5 / p 17 | On multiple occasions in your report you explain the alignment of Croatia and Slovenia concerning the National Radiation Emergency Plans. This kind of international alignment is often a very difficult proces. At a previous Review Meeting this was recognized as a challenge. Could you elaborate some on the difficulties you experienced in this proces and the steps both parties needed to take before a close alignment became a reality?
432 | Slovenia | topic 3 | P IV / Ch 5 / p 18 | According to the NAcP the SNSA is still considering whether to require additional analysis concerning certain issues. Can you estimate when the SNSA will make a decission about these studies and if deemed necessary when discussed studies can be finished, is that before 2018? Will this evaluation be finished timely enough to allow its conclusions to be implemented in Phase III?
433 | Slovenia | topic 4, nat org | P IV / Ch 5 / p 19 | In action #7 you mention for example prioritizing your international involvement as a way to mitigate the difficulties you have as a small regulatory body. Are there any other ways you use to mitigate these difficulties and which could be beneficial to other countries having small or understaffed regulatory bodies?
434 | Slovenia | topic 2 | P IV / Ch 5 / p 20 | Concerning the use of an PSA, does the Krsko plant uses a so called living PSA to continuously analyse the effect of small plant modifications or maintenance jobs? What level PSA applies to Krsko?
435 | Spain | topic 3 | Ch4/p19 | What are the design values which are specified for the ESC's in Spain? How were these values determined?
436 | Spain | topic 1 | Ch4/p19 | Can Spain list the most important modifications and/or investments that are necessary because of the 'seimic margin value'(RLE) of 0.3 g? Why is this value the same for all plants?
437 | Spain | topic 3 | Ch4/20 | In 4.1.4. Analysis of H2 in annexed buildings: what actions have been proposed?
438 | Spain | topic 1 | Ch4/p20 | In 4.1.3. no explanation is given for the delay of ITC issuing. Can you please provide this information.
439 | Spain | topic 3 | Ch4/p21 | Regarding section 4.1.4, could you explain what difficulties were encountered with the scarcity of international experience?
440 | Spain | topic 3 | Ch4/p21 | With reference to 4.1.5: Can you describe how capacity for handling of large volumes of contaminated water has been realised? Why is international experience mentioned as challenge?
441 | Spain | topic 6 | Ch4/p21 | With reference to 4.1.5: The reference standard as developed by CSN might be a candidate for sharing with other RBs. Could CSN explain in more detail about the contents of this document?
442 | Sweden | topic 1 | Ch1.2, page 16 | Why is the seismic reassessment limited to specific buildings and piping of the NPP? Is a probabilistic seismic assessment requested from licensees?
443 | Sweden | topic 1 | Ch1.2, page 17 | Is a return frequency of less than 10-4/yr used in the hazard assesment for external hazards (siesmic, flooding and extreme weather)?
444 | Sweden | topic 2 | Ch2 | A lot of investigations in the Action Plan under the topic Design Issues were within the scope of the European Stresstest. Why are these investigations still part of the Action Plan?
445 | Sweden | topic 4, nat org | Ch4.2 | The description of the Havsörn exercise in the NAcP suggests that it still has to take place. On the other hand it should have taken place in December 2013. Probably this part of the NAcP has not been updated?
446 | Sweden | topic 6 | Ch6.3, page 36 | Can you make clear if the IRRS actionplan and specifically (IAEA standard and OEF) are implemented in Sweden? For OEF: is guidance established and implemented (8.3.2: T6.RA.3)?
447 | Sweden | topic 5 | Ch8 | Why are actions/measures identified in part 5.3.1. and 7 not incorporated in the summary tables of chapter 8 and progress reported ?
448 | Sweden | topic 1 | CH8.2, page 43 | The mentioned EPRI method is meant for seismic assesmments. Is also a walk-down methodology defined for flooding and extreme weather?
449 | Sweden | topic 4, nat org | CH8.4, page 58 | For certain well-defined actions like T4.NA.2 and T4.NA.3 no schedule is set. They are labeled ongoing instead, but it seems that these kind of actions should have a time schedule and deadline and will not go on forever.
450 | Switzerland | topic 1 | Ch 1.1., pag 11 | When is the PEGASOS project expected to be finished?
451 | Switzerland | topic 1 | Ch 1.5, pag 13 | When are the results expected of the analysis of advantages and disadvantages of an automatic shutdown of the plants triggered by the seismic instrumentation?
452 | Switzerland | topic 2 | Ch 2.1, pag 15 | The original project for an alternative diverse heat sink at Muhleberg NPP has been abandoned, when the decision was taken to permanently shut down the plant in 2019. However, a new proposal has been implemented. Can you elaborate on the differences in design and safety between the two projects?
453 | Switzerland | topic 3 | Ch 3.10, pag 26 | Can you comment why PAR's are not yet in place in Swiss NPP?
454 | Switzerland | topic 4, nat org | Ch 4.3, pg 33 | Can you elaborate on the ENSI self-reflection study on its own oversigth culture and its effects on licensee nuclear safety and safety culture?
455 | Ukraine | general | Introduction / p.3 | Your NAcP states: "It should be emphasized that the schedule for a series of safety improvement measures at operating NPPs that require substantial funding has been extended, taking into account the situation on the territory of Ukraine over the last year and the decision made by the operating organization to shut down the power units when their design-basis life expires in order to implement all safety improvement measures needed to justify long-term operation. " How were the various elements weighted in the decision to postpone some measures?
456 | Ukraine | topic 2 | Introduction / p.3 | Regarding the situation in Ukraine. Has there been an analysis performed on the influence of this situation in Ukraine on certain scenarios evaluated in the Stresstest? It is imaginable that for example the chance on large scale blackouts has increased significantly. If this would be true, it could be a reason to give higher priority to some of the proposed improvements. Was a reasoning like this evaluated and a reason for a readjustment?
457 | Ukraine | topic 1 | annex, page 27 | A methodology for seismic walkdowns is implemented. Will Ukriane also implement procedures for walkdowns for flooding and extreme weather?
458 | Ukraine | topic 2 | annex, page 27 | From the NAcP it is not completely clear how Ukraine is dealing with loss of ultimate heatsink. Will there be modifications at both sites to implement alternative ultimate heatsinks?
459 | Ukraine | topic 2 | annex, page 28 | Issues 24 and 27 deal with back-up safety systems. It seems that Ukraine uses mobile systems to fulfill back-up safety functions. For these kind of systems, installed bunkered systems are introduced in different European NPPs. Can you elaborate on the design requirements for back-up safety systems? Are the mobile systems being protected against extreme external events?
460 | Ukraine | topic 5 | annex, page 35 | Issues 114 and 115: Rodos is a decision support system. Source estimation will be input to Rodos? Are actual plant data during an accident of all NPPs available in the Emergency Centre of Ukraine? And what method is used to make a proper estimation of the source term during an accident?
461 | Ukraine | topic 6 | annex, page 38 | Ukraine always had access to the relevant engineering information of their NPPs provided by the Kurchatov Insitute. Does Ukraine have access to this information in the present political situation? Are there any alternative sources available?
462 | UK | topic 1 | par 20 and 22, p.6 | The regulatory requiremnent is retun frequency of 10-4 per annum. What happened with the investigation by the UK Meteorological Office (MO) of weather hazards at a 10-5 per annum return frequency? Where can we find a specfication of these weather hazards?
463 | UK | topic 2 | par 36, p.9 | It is stated that the review conducted by licensees and National Grid produced a number of recommendations and these are being progressed via “normal business”. Can you give more details about the possible enhancements for coordination and restoration which have been identified regarding grid reliability?
464 | UK | topic 2 | p.10 | Paragraph 40: do the plans for consumables also include lubricants?
465 | UK | topic 3 | Par 46, p.11 and par 74, p.17 | "A feasibility study for the installation of Filtered Containment Venting (FCV) has been completed and a decision on installation at Sizewell B will be made in the early part of 2015." Has the decision been taken? Will FCV be installed at Sizewell B?
466 | UK | topic 2 | p.12 | Spent Fuel Pool (SFP), Paragraph 49 states that the focus for power independent monitoring is on post-emergency equipment rather than on continuing monitoring with installed equipment. This suggests monitoring equipment will need to be brought to the SFP after an emergency has occured, which may be under difficult conditions. Did you also consider securing power supply to the installed equipment?
467 | UK | topic 2 | p.14 | Mobile devices, paragraph 60: it is stated that AGRs rely on pods stored at strategic locations within the UK and this would be acceptable because a response at a longer timescale (than with Sizewell B, PWR) is deemed acceptable by ONR (see also paragraph 48). Has damage to infrastructures (roads, bridges et cetera) blocking transports of the pods been considered in this reasoning?
468 | UK | topic 3 | par 84, pag 19 | Can you give more details on why Sizewell B does not have SAGs and SBERGs?
469 | UK | topic 3 | par 95, pag 21 | "The approach will be to leave water where it accumulates if secure". Can you give more information about the criteria to establish whether accumulation of comtaminated water is 'secure'?
470 | Switzerland | topic 2 | page 10 | On page 10 it is written that: "The restoration of the containment integrity in case of a total Station Black-Out (SBO) during shutdown (see OP6-2) has also been identified as an open point by ENSI at the end of the EU stress tests. In fact, fairly large containment openings are present for a specified period during shutdowns in connection with the annual refuelling and maintenance outages in order to transport material and equipment or to allow access by individuals. If an accident involving a prolonged loss of the power supply (SBO) occurs during this period, it must be expected that the restoration of containment integrity will have to be carried out under more difficult conditions. At the end of the first EU Stress Tests Follow-Up workshop in April 2013, ENSI was also suggested to put additional emphasis on this issue. Specifications for the analyses to be performed by the operators were issued at the end of 2013. The operators submitted the related studies in October 2014. These reports are currently under review." We would like to know whether ENSI performs a technical review of the licensees' emergency operating procedures for SBO occurring during shutdown states and what are the main aspects covered by this review.
471 | Switzerland | topic 3 | page 24 | On page 24 it is written that: "The severe Accident Management Guidelines (SAMGs) of the Swiss NPPs are generally symptom-based and thus not only focused on specific scenarios. In Switzerland, the adequacy of SAMGs is continuously reviewed within the frame of PSRs and emergency exercises." Does ENSI perform a technical review of the SAMGs? What are the aspects covered by this review?
472 | Switzerland | topic 3 | page 24 | On page 24 it is written that: "In Switzerland, the adequacy of SAMGs is continuously reviewed in PSRs and emergency exercises." What are the expectations of ENSI with regard to the analytical validation of SAMGs? (i.e. with specific computer codes)
473 | Switzerland | topic 3 | page 25 | Regarding the SAM training, how does ENSI review the training received by operators, shift supervisors and the technical support group on SAMGs? How often is training on SAMGs provided? Are SAM-related topics a part of the authorization process for plant staff with roles in accident management?
474 | Germany | topic 3 | page 14 | On page 14 it is written that "The operators of the German nuclear power plants additionally developed a generic concept for dealing with severe accidents (SAMG – severe accident management guidelines) in the form of a "Manual for mitigating emergency measures" (HMN) as a supplement to the existing emergency manuals (NHB) and presented it to the RSK. This concept is now being introduced in all plants in power operation and is subject to continuous improvement." Could you please provide more information on what is the extent and depth of the regulatory review of the emergency operating procedures and SAMGs developed by the licensees? (i.e. what topics are covered, what technical aspects are reviewed, how human factors are taken into account, etc.)
475 | Belgium | 1 | 7 | For the Tihange NPP, the assessment resulted in the finding of a greater peak ground acceleration (“PGA”) than was presumed when designing the facilities. Could you please explain what were the main reasons behind the resulting greater PGA?
476 | Belgium | 1 | 9 | In summary, the main progress made in 2014 for the protection against earthquakes consists of the revaluation of the PSHA study in detail and the completion of the SSC upgrade. Could you present some detailed information about the PSHA study (e.g. seismic source characterisation/model, ground motion prediciton equation used in calculations, hazard calculations, site response and control point ground motion)? Also what kind of the SSC upgrades are planned to upgrade seismic resistance/ robustness of the facilities?
477 | Belgium | 1 | 12 | At Tihange, the internal hazards potentially induced by the flooding were examined, as requested by the regulatory body. The possibility of internal fires and internal explosions was considered. The licensee proposed protective actions, which were judged acceptable by the regulatory body and were then completed. Could you give some information about the protective actions implemented/planned for preventing/mitigating internal fires or internal explosions due to flooding?
478 | Belgium | 1 | 24 | Concerning earthquakes, the licensee proposed to develop procedures in order to detect possible leaks in the WAB after earthquakes and to isolate them. This action has been officially closed by Electrabel and the Regulatory Body. Could you present some more details about these procedures, how do operators use them to detect and isolate possible leaks in the WAB after earthquakes?
479 | Bulgaria | 1 | 7 | The current assessment of natural hazards are included in the periodic safety analysis for all nuclear facilities on the site. Could you shortly present the results of periodic safety analysis for natural hazards?
480 | Bulgaria | 1 | 8 | Procedures are developed for preventive actions of the staff in case of notification of as follows: extreme weather conditions, emergency low level of the Danube, …. It seems that earthquake is not included. Do you have special procedure for it? If not, why?
481 | Czech Republic | 1 | 67 | Regarding action No. 3: What kind of reinforcement will be used and will it satisfy up to date IAEA/WENRA requirements regarding seismic, flooding and other natural sever challenges?
482 | Czech Republic | 1 | 69 | Regarding action No. 12: According to the subscription provided, how is assessment done in the meantime when mentioned guidance are not yet released/available ? What references/guidance have been used when assessment of the natural hazards was done in the past?
483 | Czech Republic | 2 | 70 | Regarding action No. 33: What is the capability of the ventilator towers, how will they be energized, how long can they operate in the case of extended SBO?
484 | Finland | 2 | 17 | It is written that "the licensee of the Loviisa NPP has studied the possibilities to utilize mobile power supply and mobile pumps to support safety functions." The preliminary investment decision was planned in 2012. The investment decision hasn’t been made yet. When are you planning to buy mobile power supply and mobile pumps to support safety functions?
485 | Finland | 2 | 12 | Both licensees have investigated their cooling water reserves at site taking into account the situations where all plants in same site are in emergency including spent fuel pools. What were the results of these investigations?
486 | Finland | 2 | 14 | The licensees together with the diesel engine manufacturers have carried out investigations of replacing conventional diesel with widely available biodiesel. Based on these investigations biodiesel is allowed to use in exceptional circumstances. Could you explain these exceptional circumstances? What does that mean?
487 | Finland | 3 | 27, 28 | The Loviisa units' MCRs can be used as emergency rooms for other unit, while for Olkiluoto 1 & 2 there are no ECR available. Are there some plans to install some ECRs or other capabilities that would enable controlling of the units in case of loss of MCRs?
488 | France | 1 | 14 | EDF has submitted the required studies (ECS-12) and proposed a program of modifications aiming to ensure the seismic resistance… Could you please explain, what kind of modifications are intended to be implemented for this issue?
489 | France | 1 | 39 | Will the storage facility for mobile devices be seismicly qualified? If yes, what will be the design basis?
490 | France | 1 | 16 | Regarding ECS - 7, Measures to cope with site isolation in the event of flooding, can you please describe in more details (or give a reference) how have you determined when you had to shutdown the reactors in the case of bad meteorological or hydrological conditions? Have you also assumed loss of offsite power in the case of site isolation?
491 | France | 3 | 34 | What is the motivation for not using the U5 filter in a severe accident situation? In which situation would it be used?
492 | France | 3 | 49 | Does the French regulation require the SAMG’s to be approved by the ASN?
493 | Germany | 1 | 26 | KBR/ PWR, action No. 17: Could you give some more details about the seismic instrumentation that has been installed? Technology, standards, number of measurements, …
494 | Germany | 3 | 30 | KKE/ PWR, action No. 19: Can you please explain in more details how was the effectiveness of installed H2 recombiners for hydrogen reduction demonstrated? Was the effectiveness of the installated H2 recombiners proved by testing?
495 | Germany | 3 | 39 | KRB B+C/ BWR, action No. 4: What is the total capacity of the installed recombiners in one unit? For which postulated accident was their capacity chosen?
496 | Hungary | 2 | 16 | What is the capacity of safety diesel generators fuel storage capacity (for how many days of operation)? Do diesel generators have common reservoairs or are they separate?
497 | Lithuania | 1 and 2 | 7 | In the table 1 "Summary of measures of the Plan of Strengthening Nuclear Safety in Lithuania" it is mentioned that topics 1 "natural hazards" and 2 "general" are in progress due to waiting for the updated Wenra RL. Which changes of the new Wenra RL will be taken into consideration in topics 1 and 2?
498 | Netherlands | 1 | 95 | Regarding action No. 2: Which values of seismic load parameters were taken into account as design basis?
499 | Netherlands | 3 | 98 | Regarding action No. 12: Is the new seismically resistant fire annunciation system operable in case of design basis event? Does this system exchange data via an ordinary data cable or wirelessly? What kind of seismic technical solutions were applied for the system?
500 | Romania | 1 | 16 | Table 1, action 10: The peer review concluded that there is only little information about margins to cliff edges due to external events and weak points. Further work is proposed in this area and it is recommended that CNCAN obtains good quality programmes from licensees and ensures that the work is appropriately followed up. When will this issue be resolved?
501 | Slovak Rebublic | 1 | 19 | You mentioned in your report the predictive regulation No. HP/3006 for measures against extreme climatic conditions which were prepared and implemented. This recommendation is completed for all operating units. Could you please give some examples of implemented measures for EBO3&4 and for EMO1&2?
502 | Slovak Rebublic | 1 | 17 | The seismic reinforcement of structures for EMO1&2 units will be made, related to the seismicity - minimum peak ground acceleration 0.1g recommendation. Could you present some detailed information about planned reinforcement for these units?
503 | Spain | 2 | A2 | Regarding the requirement I3: Which NPPs have possibility for recovery of off-site electrical supply from nearby stations (hydroelectric or other)? Do they have the possibility for black start? Which stations were modified to provide black start possibilities?
504 | Spain | 3 | A4 | Regarding the requirement No. I14: What were the results of the study of technology alternatives for filtered containment system? What kind of filtered containment venting system will be (or have already been) installed on Spanish NPPs?
505 | Sweden | 1 | 17, 43 | It is reported that analyses of incrementally increased flood levels were performed. At what level, in comparison with the design basis flood, has been reached the cliff edge effect? What improvements are planned to be introduced at some plants?
506 | Sweden | 2 | 21, 44 | The integrity of the primary system for prolonged extreme situations has been evaluated for PWRs. What were the findings on primary system creep rupture in case of core melt (e.g. steam generator's U tubes, hot leg etc.), which part of the primary system pressure boundary was found to be the weak point (other than the reactor coolant pump seal)? Please, provide more information on planned modification/replacement of primary pump seals. What is the benefit of new seals for extended SBO scenario and are there any possible disadvantages of this design for some other severe accident scenarios?
507 | Sweden | 3 | 21, 49 | The action was completed in 2014 according to schedule (category) and it is mentioned that there are different suggested solutions for the use of the containment filtered venting system during prolonged severe accident conditions (more than 24 hours). Please, provide more information on results of these reassesments and possible improvements (any design modifications or required human actions for such conditions).
508 | Switzerland | general comment | 45 | Chapter Part IV: It is not evident when the actions will be implemented. Could you give some specific information on the current status and the schedule for action implemention?
509 | Switzerland | 1 | 11 | From the report it is not evident, what would be possible secondary effects of the seismic event (e.g. fires, etc). Have such analyses been done and what were the results/conclusions?
510 | Switzerland | 1 | 20 | Is the external storage facility at Reitnau seismicly qualified and if yes, what are the design basis?
511 | Switzerland | 3 | 24 | Is the revision of the SAM planned with respect to already implemented changes in Swiss NPPs? How are the SAMGs validated?
512 | Switzerland | 3 | 26 | Some licensee proposed to equip their containment with PARs. Are there any plan to equip also the SFP building with PARs? Are there any other countermeasures planned for mitigation of hydrogen ( e.i. upgrade or modified the existing venting systems,..)?
513 | Switzerland | 3 | 29 | How are in practice implemented issues related with "additional studies including accident timing, core melt, reactor pressure vessel failure, basement melt-through, SFP uncovery"? Please give some examples.
514 | Switzerland | 1 | 12 | The flood protection of safety related buildings was enhanced with mobile flood barriers. This may be an action that requires extensive work when performed in an emergency. Please, provide information on how much personnel is needed for implementation of such barriers, how much time is required to install barriers, up to what flood level is the plant protected (height of the barriers). Have the operators included installation of these barriers also in the emergency plans and training/exercises?
515 | Switzerland | 1 | 13 | In the process of assessing the external flooding safety margin, have you also determined the cliff edge? Please, provide comparison between design basis flood flow/level and the cliff edge flow/level and the return period (or frequency) of such cliff edge event.
516 | Switzerland | 2 | 14 | Information is presented for the Mühleberg NPP process of developing a project for an additional, diverse ultimate heat sink. One concept was approved by ENSI in 2012, then the operator abandoned it. In 2014 the operator submitted an alternative solution for the diverse ultimate heat sink and this was approved by the ENSI. No details are presented. Please, provide a brief description of the first and the second concept of the diverse ultimate heat sink and give an estimate of their capacities.
517 | Ukraine | 2 | 13 | Regarding improved reliability of emergency power supply, could you please explain what does this improvement include and what is with this improvement for plants RNPP, ZNPP and KhNPP?
518 | Ukraine | 3 | 14 | Regarding provision of instrumentation during and after accidents, could you please give some details on the qualification of the instrumentation? What are the requirements for qualification?
519 | UK | 1 | 47 | Table 3: Several actions under STF-7 & IR-10– Review of flooding studies, Completion of flooding studies and Completion of the Safety Case comparison are stated to be on-going actions. What is the status of this actions? What kind of flooding studies are still on-going?
520 | UK | 3 | 50 | Could you give details on status of actions IR-22 - Provision on-site of emergency control, instrumentation and communication and STF-15 - Facilities for remote indication of plant status (it's not clear)? What kind of enhancements were implemented?
521 | Bulgaria | 1-Natural hazards | 9 | It is mentioned: "The equipment important to safety and included in the emergency scenarios is analysed for seismic stability. The margin of Units 5 and 6 according to the analyses conducted is 0.13 g." Do you plan to ensure seismic stability of equipment important to safety at 0.2 g (considering that the Design Bases Earthquake (DBE) (also SL2, Safe-shutdown Earthquake) - PGA 0.20 g).
522 | Bulgaria | 3-Severe Accident management | 38, 39, 56 | It is mentioned that the measure: "Modifications of SAMGs and electricity supply recovery procedures from MDG to ensurerestarting of the ventilation systems for recirculation and air filtration in the MCR" Have the same measures and modifications been considered to the ECR?
523 | Bulgaria | Area D - Severe Accident management | 37 | Measure D-2-4:Develop technical means to provide direct injection of water to the reactor core, SGs, spent fuel pooland the containment by mobile fire protection equipment in extreme conditions Could you please provide the updated information of the current status of these measures implementation and main technical parameters for the mobile equipment?
524 | Bulgaria | Area D - Severe Accident management | 38 | Measure D-2-6: Extension ofthe scope of SAMGs-for the spent fuel poolsand for specific reactor shutdown states, not covered by the current SAMGs. Could you please clarify how the staff training on SAMG is ensured? Are there any simulators for SAMGs training?
525 | Hungary | 1-Natural hazards | 62 | It is mentioned: "The concept for management of small diameter (d < 100 mm) pipelines is ready. The completion of the task may undergo delay because the appropriate technical solution for large diameter pipelines should be found" What is the reason of the different concept for small (d < 100 mm) and larger diameter? What problems have you faced in the second case?
526 | Hungary | 2-Design issues | 65 | It is mentioned: "2 independent diesel generators protected against external hazards will be provided. They will have accident as well as maintenance functions." What are the main characteristics of the DGs (power, cooling, seismic resistance etc.)? Where they will be located? Will there be a special shelter(s) for DG? If these DG are "installed" (not mobile), than what about MDGs?
527 | Hungary | 3-Severe Accident management | 57 | It is mentioned: "Seismic qualification of the on-site shelters not yet qualified shall be performed and non-earthquake resistant equipment in the shelters shall be improved. A nuclear emergency response centre resistant to earthquakes of a peak ground acceleration higher than design basis earthquake shall be established." Which method (s) is to be used for seismic qualification? What is the basis for selection of requirements on seismic resistance of the emergency response centre (higher than design basis earthquake)?
528 | Hungary | 3-Severe Accident management | 66 | Could you please explain the concept of slow over-pressurisation of the containment (which rooms are covered, actuation criteria, filtering method, ...)? Have the strategy of in-vessel melt retention been taken into account?
529 | Czech Republic | 1 – Natural hazards | p. 76 | According to chapter 6, Action 70 "Seismic PSA including analysis of secondary effects with a proposals for remedial measures" was finished in 2015. Please provide information on contribution of seismic impact to the CDF for Dukovany and Temelin NPP. Which safety improvements have been identified?
530 | Czech Republic | 2 - Design issues | p. 68-69, line 16 | It is mentioned that the measures "Provision of back-up coolant supply into depressurised reactor and storage pools with additional and sufficient sources of coolant" were completed. Could the details of the back-up coolant supply be provided? Whether the additional borated water sources are installed? What means are used to ensure injection to RCS and SFP (mobile pumps or design means with electrical supply from mobile DG), etc. How long the back-up coolant supply could be maintained from available water sources?
531 | Czech Republic | 2 - Design issues | p. 68-69, lines 13-16 | It is mentioned that a set of mobile equipment for SBO conditions was implemented. Please provide some details on the storage places of the mobile equipment. How the equipment is protected from external hazards and common cause failures? What is the estimated time for its transportation and connection to consumers?
532 | Czech Republic | 2 - Design issues | p. 76, item 75 | It is stated that the batteries capacity real load tests were finished. What are the results of these tests? Were the additional measures to extend batteries depletion time found necessary?
533 | Czech Republic | 3 - Severe Accident Management | p. 8 | It is mentioned: "Heat removal from the containment atmosphere by means of spraying (providing heat removal) is sufficient to maintain the safe pressure in the containment". How containment protection against overpressurization is ensured in case of SBO? Has the passive containment filtered venting system been under consideration for Temelin NPP?
534 | Czech Republic | 3 - Severe Accident Management | p. 70, line 27 | It is mentioned: "Implementation of important measurements into post-accident monitoring system – the addition of RA situation measurement and SFP condition into PAMS". How will the operation of PAMS and its components (especially, sensors and communication channels) in the condition of severe accident be ensured? Are there special (more strict) qualifiation requirements for these sensors? How will power supply be provided for PAMS and its sensors in case of full loss of power?
535 | Czech Republic | 3 - Severe Accident Management | p. 73, item 50 | Completion of measures for maintaining long-term contatinment integrity during severe accidents is scheduled for 2022. Are there any short-term measures (other than hydrogen control) planned for implementation at Temelin NPP under this topic?
536 | Czech Republic | 3 - Severe Accident Management | p. 73, line 51 | It is mentioned that the measure "Verification of the correctness of assumptions about the functioning of the equipment during beyond design-basis conditions and external risks, including possible measures to ensure functionality according to SAMG" was completed. What approach has been used to assess and prove the performance of equipment in conditions of severe accidents? How the PORV functionality was justified for primary depressurization during severe accidents?
537 | Czech Republic | 3 - Severe Accident Management | p. 74, line 58 | It is mentioned that the measure "Analysis of habitability MCR/ECR during severe accidents, including the impact on MCR/ECR unaffected unit" was completed. Have any enhancements of the MCR/ECR habitability during severe accidents been identified and implemented resulting from the performed analysis? For how long the control rooms could remain habitable upon the blackout? Is there oxygen regeneration provided?
538 | Finland | 2 - Design issues | p 17, para 2.5 p. 47, line 110 | According to para 2.5, the implementation of mobile devices (diesel generators and pumps) was planned to be completed in 2013. However, the licensee will make the decision regarding the mobile devices jointly with the decision on comprehensive solution for flooding protection. This measure is scheduled for 2018. Please provide explanation for combining the implementation of mobile devices with the solution for flooding protection.
539 | Finland | 2 - Design issues | p. 16, para 2.4 | According to para 2.4, the plant modifications concerning water injection to the spent fuel pools will require further analysis before starting the detailed design work. The conceptual plan has been submitted to STUK in 2014. Please provide some details on the decisions that are under consideration. Will pure or borated water be supplied to SFP? Are the mobile devices going to be used?
540 | Finland | 3 - Severe Accident Management | p. 16 | It is mentioned: "To improve monitoring of the water temperature and level in the spent fuel pools inside the reactor building, there is a plan to equip all spent fuel pools with a temperature and level measurement system that enables measuring water level from the normal level down to the top of the fuel assemblies. The measuring system will be visible outside the containment and independent from the power supply". What kind of measurement system is to be used? How the independence of this system from the power supply is ensured?
541 | Finland | 3 - Severe Accident Management | p. 23, para 3.2 | According to para 3.3, both at Loviisa and Olkiluoto operating NPPs, the frequency of large releases is higher than the limits set in STUK’s regulatory guide YVL A.7. Is there any estimation of decrease in the frequency of large releases after implementation of SAM measures? Is it sufficient to comply with the limits set by STUK or additional measures should be taken?
542 | Finland | 3 - Severe Accident Management | p.25(51) | In para.3.5, a new requirement of the Governmental Decree on Emergency Response Arrangements at NPPs concerning construction of the reserve emergency centres outside the power plant area is mentioned. Has a decision been taken on location of the reserve emergency centres? What is the progress in construction of the reserve emergency centres so far?
543 | Finland | 3 - Severe Accident Management | p.26(51) | Para.3.5 mentions a requirement that maintenance personnel need to be trained and regularly participate in exercises. Does this requirement apply to the maintenance personnel of NPPs or to the outside maintenance personnel as well? What kind of competences and skills are to be trained? What is the recent practical experience in participation of the maintenance personnel in the exercises?
544 | Finland | 5- Emergency Preparedness and Response and Post-Accident Management (Off-Site) | p.36(51) | Para.5.1 mentions that the National Nuclear Power Plant Emergency Preparedness Forum is to be launched in order to coordinate local cooperation between the regional rescue services, regional police departments, NPP licensees, STUK. What is a status of this Forum? Is it a consultative body to the Government or is it a decision-making body?
545 | Slovak Republic | 1 – Natural hazards | p.17 | According to the information presented in ID6, Seismic PSA has already been completed for Mochovce-1,2. Please provide information on the contribution of seismic impact to the CDF.
546 | Slovak Republic | 1 – Natural hazards | p.19 | According to the information presented in ID10, Bohunice and Mochovce seismic monitoring stations were built and "in case of stronger seismic events, the analysis results are prepared within two days from their recording". Could you clarify the criteria to define the "stronger seismic events"? Will the plant walkdowns be provided in case of this stronger seismic events.
547 | Slovak Republic | 2 - Design issues | p. 21, 46 | It is mentioned that new procedures for operators of diverse mobile devices were developed and implemented. Training programmes for the diverse mobile devices were prepared, implemented and tested at EBO and EMO through exercises. Do the training programs include the additional actions necessary to clear the blockages (for example, in case of an earthquake) on the way of the water supplied from mobile sources to SG?
548 | Slovak Republic | 2 - Design issues | p. 25, line 18 | It is mentioned that “Projects for shelters for placing the 0.4 kV mobile DG and cabling between the 0.4 kV mobile DG and selected consumers - procurement in progress” Which requirements for withstanding to external hazards were applied to the shelters? Are these shelters located within or outside the site?
549 | Slovak Republic | 2 - Design issues | p. 29, line 19 | It is mentioned that “Mobile DG 0.4 kV with connecting cabling were purchased in 2012 for all units.” What are the main consumers and power loads of the mobile DG 0.4 kV? Are there any plans to have mobile DG 6kV to feed one safety train? Correspondent measure was specifed for evaluation in the previous revision of NAcP (p.25)
550 | Slovak Republic | 2 - Design issues | p. 36, item 27, Spent Fuel Pool | Page 26 of the previous revision of National Action Plan (dated 2012) identifed SFP inventory maintenance and cooling measures which are not reflected clearly in new revision of NAcP. How SFP cooling will be ensured during SBO and/or loss of UHS?
551 | Slovak Republic | 2 - Design issues | p. 21, item 12 | It is mentioned on page 21 that the study of an impact of extreme external temperatures in selected NPP rooms after loss of cooling was performed. What are the main conclusions of this study? Were any needs/measures identified to improve equipment cooling robustness?
552 | Slovak Republic | 2 - Design issues | p. 51, item 35 | It is stated that if "the unit is not cooled below 238°C during SBO, no fuel damaging occurs due to loss of sub-criticality". Stuck of secondary circuit steam dump (or relief) valves or excessive SG feed from mobile pump during SBO could potentially lead to a decrease of coolant temperature below the specified value. How potential recriticality issue at SBO is addressed? Is it foreseen to provide power supply from mobile DG to boron injection pumps?
553 | Slovak Republic | 2 - Design issues | p. 26, item 18 | Last paragraph on page 26 mentions preparation of design documentation for autonomous cooling of emergency DG. Are any principal design decisions already available for this system, e.g., type of system (passive or active), independence from existing cooling system, number of emergency power supply trains to be modified, etc.?
554 | Slovak Republic | 3 - Severe Accident Management | p.34 | The paragraph (ID) 25 states that the SAM project includes also the habitability of the main control room and the control of selected equipment from the ERC. For how long the control rooms could remain habitable upon the blackout? Is there oxygen regeneration provided?
555 | Lithuania | 1 - Natural hazards | p.9 | Please provide information on which methodology was used (SMA, SPSA) for seismic margin estimation of Ignalina NPP accident management centre (according to ID 6 of Table 1, the results of the calculations confirmed the robustness and availability of the AMC in case of an earthquake with peak ground acceleration of 0,13g).
556 | Lithuania | 1 - Natural hazards | p. 9, item 6 | Could you please explain, whether it means that seismic analysis is performed directly for the AMC building? Does the analysis include assessmnts of seismic resistance of equipment and communications of AMC or only of the building?
557 | Lithuania | 2 - Design issues | p. 12, line12 | It is mentioned that “…relevant severe accident management guidelines of Ignalina NPP have been updated and approved by VATESI”. What is the scope of the SAMG for Ignalina NPP? Which main modifications have been introduced in SAMG upon assessment of the equipment performance in conditions of beyond design-basis accident? What technical provisions are in place to manage severe accidents in the spent fuel pools? Is it enough just to update SAMG to solve the issue, or appropriate replacement of equipment is required?
558 | Germany | 1 – Natural hazards | p.76 | According to information of ID E-49, only four NPPs have performed a seismic PSA. Please provide information on planned terms of performing SPSA for all plants that remain in operation.
559 | Germany | 3 - Severe Accident Management | p. 25, line 9 | It is mentioned: “Review and optimisation, if necessary, of the requirements for the containment venting system with consideration of station blackout conditions, adverse radiological conditions and effectiveness following natural external design impacts”. Have the requirements for containment venting system been updated based on the obtained review results? Which radiological safety criteria were applied for CFVS?
560 | Germany | 3 - Severe Accident Management | p. 32, line 20 | It is mentioned: “Review of the robustness of the plant regarding load crash events. For this purpose, an assessment of the existing precautionary measures and the robustness of the plant in connection with postulated load crash events was carried out." What load was assumed for analysis of NPP robustness? Which methods are used? Are there any outcomes from the analysis?
561 | Czech Republic |  | eg. 73 - integrity of the containment, eg.13,15, - PGA | 1. In the whole stress test procedure is not evaluated the crash of the big aeroplane on the nuclear power plant - I think this is against the sense of the stress test procedure. 2. The earthquake in the Action plans are evaluated for the PGA 0,1 g - which is value for the designed project. Official statement of czech authorities is that Temelin and Dukovany NPPs are evaluated for "overprojected" earthquake - which obviously is not thruth. 3. Implementation of measures for maintaining long-term containment integrity according to selected severe accident management strategies should be in Temelin NPP finished till 2022!? I think this shoud have been done in the very beginning of the NPP Temelin operation, not after more than 20 years operation!
562 | Slovenia |  | A1 -A49 | The Carinthian government has to mark the following comments to the follow up action plan: Tests for the validation and verification of modernization measures must be taken. A new - the state of the science and technology adequate assessment of seismic hazard for the location Krško, which identifies the seismic potential of active faults in the vicinity of nuclear power plants and assesses these paläoseismic based methods, is highly recommended. With the result of the analysis the probabilistic hazard analysis (PSHA) should be updated. With regard to the interpretation earthquake is recommended that the Slovenian Authority takes up the proposal of ENSREG and may require an update of a design basis for future modifications to the powerplant Krško. Assessing the quality and reliability of the analysis of seismic activity, indicating the value of the SSE with PGA = 0.56g. The analyzes have to be completed and mainstreaming climate change and therefore those expected in the future extreme weather situations of extreme rainfall in the analysis of possibility of flooding the location Krško and thus to monitor the relevant measures against flooding. The only reference to historical data is not enough. It is recommended to complete the analysis and to include in addition to the occurred historical weather situations for future extreme weather conditions with low water and simultaneously high air temperatures, since their appearance will be more frequent due to climate change. The Krško stress test considers only the event of external flooding by the river Sava. However,there is no consideration of internal flooding, which could be the consequence of a large triggered fraction of pipes in the building etc. turbine. This deficiency should be corrected in an update to the stress test. A sufficiently transparent approach requires the notification and disclosure of relevant documentation, analysis and experiments which led the operator to provide the actions referred for a serious accident in the NPP Krško. Among other things, this relates to the flooding of the reactor cavity to control a possible meltdown after failure of the reactor pressure vessel. Based on these documents, the analysis should be carried out, which assessed the effectiveness of the flooding of the reactor pit on the control of meltdown in the NPP Krško. The operator NEK and the approval authority SNSA is recommended to recalculate with their available analytical core melt accidents at the three blocks of Fukushima. Thus, the computer programs may be checked. The assumptions and calculation methods for the assessment of steam explosions in the RDP and containment outside the RDP were presented and analyzed. Simulation calculations to underpin the concept of in-Vessel or in containment retention of corium in the event of serious accidents are to be performed. The consequences of a delayed containment failure in a serious accident with core melt are not addressed in the Slovenian stress test report. This deficiency should be corrected in an update of the stress test report. It is proposed to carry out repeated tests for the seismically qualified emergency diesel on the changes made. The discharge of the battery blocks of the NPP Krško should again be reviewed and, if necessary, the batteries should be replaced by those with a longer discharge time. Additional measures for procedures in the event of a serious accident at the storage pool for spent nuclear elements have to be completed. A strategy (plan and technological option) should be brought up, as in the case of emergency spent nuclear fuel could be rapidly removed from the storage pool and the building. It is recommended after the Fukushima accident to provide adequate new nuclear liability rules. Internal events and the extent of possible human errors and gross violations that can lead to serious accidents should be discussed and analyzed in the context of an update Krško stress tests. The Krš
563 | Germany |  | 1 | Within the national reports and actionplans there is no plant specific information available which risks of the related plant had been analyzed, what systems are/were affected by that risks and what system- and component-specific modifications of the plant are or were needed to cope with the predefined safety criteria to eliminate the analyzed risk or to tolerate it. Corresponding to an answer of the German Top-Regulator at the "VDTÜV Fachforum 2014" the German Top-Regulator BMUB has no plant specific information of the modifications on the system- and component-level planned or done by the operators. Above that the BMUB could not answer the question whether the state-regulators has got this kind of information. I ask the European Nuclear Regulators whether they are precisely informed on the analyzed safety deltas on system- and component level following the stresstest, whether the safety criteria that are/were used to define the deltas are explicitly defined and approved and correspond to the state of the art - and if not, why? I ask the European Nuclear Regulators whether they are willing to make a list available of the identified shortcomings/risks, the affected systems and components, the used safety criteria to define the risks, the component- and system-specific measures taken, and the degree up to which the shortcomings have been eliminated by their measures - and if not, why? These questions should be answered by all countries. The only reason to specify a country as addressee lies in the given poor format of this kind of participation. The same applies for the page number of the national action plan that must be chosen arbitrarily to submit these questions. Wolfgang Renneberg, Institute for Safety- and Risk Sciences, BOKU, Vienna
564 | Spain |  | page 20 of http://www.csn.es/images/stories/actualidad_datos/revision_1_plan_de_accion_nacional_espana_171214.pdf | The CNS requires re-analysing the seismic hazard at each NPP site in Spain. As suggested by the ENSREG peer review team the analysis needs to consider geological and paleoseismological data characterizing relevant active faults of the Iberian Peninsula. The CSN required the licensees to submit the new assessments by 2016 (S1). According to the updated NAcP, the issuing of a new ITC (foreseen in 2013) by the CSN is postponed to the first quarter of 2015. A new schedule for the seismic hazard assessment has not been announced yet. Question 1: Which time schedule has been set to finalize the new seismic hazard assessment and complete the CSN review?
565 | Spain |  | page 20 | The Spanish licensees have analyzed possible secondary effects of earthquakes during the stress tests (31/12/2012). Significant improvements have been identified and scheduled for implementation by 31/12/2014 (A1 and A2). One of the EC staff working document´s recommendations is not mentioned in the Spanish NAcP: “Within the framework of the on-going analyses on the effects of pipe rupture (non-seismic and seismic), it is suggested to consider in particular verifying that there are no common cause failure issues.“ According to the updated NAcP, the implementation of improvements (regarding internal flooding due to the circumferential rupturing of non Seismic Class piping, and water containers rupturing with major fluid releases) is completed. Question 2: Which severity of an earthquake was assumed to assess the expected secondary earthquake effects? The EC staff working document recommended evaluating common cause failures – has this been undertaken?
566 | Spain |  | page 20 | The site is located on the left bank of the Arrocampo brook reservoir; the Valdecañas dam is situated upstream (storage capacity 1146 hm3). The dam break analysis was re-assessed to check against the dam emergency plans and to resolve the identified inconsistencies. The analysis was completed by 31/12/2012 (A3). According to the updated NAcP, this activity is listed as completed despite the fact that “certain specific cases pending.” It is mentioned that the revision and acceptance by the CSN of the analyses of dam rupture scenarios have undergone something of a delay due to the existing uncertainties, these having emerged during the review being performed by the CSN. Question 3: Please name the mentioned “existing uncertainties.” When is the completion of the review due? Are some interim results available?
567 | Spain |  | page 20 | The necessary improvement of external flood protection of buildings containing safety related systems, structures and components (SSCs) was implemented in 2012(I2). According to the updated NAcP, this measure is completed. Question 4: Does the external flooding protection include protection against a possible dam break scenario?
568 | Spain |  | page 20 | Studies of the site accessibility in the event of extreme natural events (including possible proposals for improvement) were to be performed by (31/12/12, A6) According to the updated NAcP, the analyses have been completed and resulted in incorporating improvements at several plants. Question 5: Has CSN completed reviewing this measure? If new results of the natural hazards assessment were found, would they be followed up with new studies?
569 | Spain |  | pages 20-23 of http://www.csn.es/images/stories/actualidad_datos/revision_1_plan_de_accion_nacional_espana_171214.pdf | Efforts to Remedy the Weaknesses the Spanish Stress Tests Described (Status 12/2014) The CNS requires re-analysing the seismic hazard at each NPP site in Spain. As suggested by the ENSREG peer review team the analysis needs to consider geological and paleoseismological data characterizing relevant active faults of the Iberian Peninsula. The CSN required the licensees to submit the new assessments by 2016 (S1). According to the updated NAcP, the issuing of a new ITC (foreseen in 2013) by the CSN is postponed to the first quarter of 2015. A new schedule for the seismic hazard assessment has not been announced yet. Question 1: Which time schedule has been set to finalize the new seismic hazard assessment and complete the CSN review? The Spanish licensees have analyzed possible secondary effects of earthquakes during the stress tests (31/12/2012). Significant improvements have been identified and scheduled for implementation by 31/12/2014 (A1 and A2). One of the EC staff working document´s recommendations is not mentioned in the Spanish NAcP: “Within the framework of the on-going analyses on the effects of pipe rupture (non-seismic and seismic), it is suggested to consider in particular verifying that there are no common cause failure issues.“ According to the updated NAcP, the implementation of improvements (regarding internal flooding due to the circumferential rupturing of non Seismic Class piping, and water containers rupturing with major fluid releases) is completed. Question 2: Which severity of an earthquake was assumed to assess the expected secondary earthquake effects? The EC staff working document recommended evaluating common cause failures – has this been undertaken? The site is located on the left bank of the Arrocampo brook reservoir; the Valdecañas dam is situated upstream (storage capacity 1146 hm3). The dam break analysis was re-assessed to check against the dam emergency plans and to resolve the identified inconsistencies. The analysis was completed by 31/12/2012 (A3). According to the updated NAcP, this activity is listed as completed despite the fact that “certain specific cases pending.” It is mentioned that the revision and acceptance by the CSN of the analyses of dam rupture scenarios have undergone something of a delay due to the existing uncertainties, these having emerged during the review being performed by the CSN. Question 3: Please name the mentioned “existing uncertainties.” When is the completion of the review due? Are some interim results available? The necessary improvement of external flood protection of buildings containing safety related systems, structures and components (SSCs) was implemented in 2012(I2). According to the updated NAcP, this measure is completed. Question 4: Does the external flooding protection include protection against a possible dam break scenario? Studies of the site accessibility in the event of extreme natural events (including possible proposals for improvement) were to be performed by (31/12/12, A6) According to the updated NAcP, the analyses have been completed and resulted in incorporating improvements at several plants. Question 5: Has CSN completed reviewing this measure? If new results of the natural hazards assessment were found, would they be followed up with new studies? Adopting a consistent approach for the return periods associated to heavy rain and extreme temperature scenarios at individual sites is planned in line with the ENSREG Peer Review team (S2) suggestion. In this context, the new WENRA Reference Levels for external events should have been implemented in the Spanish regulation in 2014. According to the updated NAcP, the implementation of the WENRA RL is pending. Question 6: What time schedule is envisaged for the assessment of heavy rain scenarios (i.e. implementation of WENRA Reference Level into the Spanish regulation, review of the operator´s studies, and implementation of
570 | Slovak Republic |  | 18, 29, 39, 45, 48 | Resistance against earthquakes: A value of the peak ground acceleration (PGA) of 0.1 g was used during plant construction. During a reassessment in 2003, the value was increased to 0.143 g. ÚJD SR decision No. 100/2011 ordered the implement seismic resistance to a new value of 0.15 g by December 31, 2018. The ENSREG peer review team recommended considering prioritization of the seismic upgrading measures. The NAcP includes this recommendation: The seismic reinforcement of structures with the highest priority is planned to be finished by 31/12/2015. (ID 6) According to the updated NAcP, priorities of the tasks defined. The Priority 1 (highest) includes buildings where equipment important for long-term residual heat removal after a seismic event is situated: Fire station, access point for external power supply, pipeline of emergency SG feed, emergency response center, etc. Other systems, structure and components (SSCs) will be seismically reinforced up to 2018. Question 1: Is the reinforcement project being implemented according to the time schedule?
571 | Slovak Republic |  | 24473 | However, no analysis of the resilience of this equipment under beyond design earthquake conditions is available yet. Therefore cliff edge effects cannot be excluded. The NAcP requires analyzing seismic margins of selected SSCs by 31/12/2013. (ID 5) According to the NAcP, the measure is completed: Seismic margins of civil structures evaluated. Question 2: Which results have the seismic margins analyzes delivered? Which back-fitting measures are necessary and which time schedule is set for their implementation?
572 | Slovak Republic |  | 24473 | Question 3: How does UJD SR assess the reliability of the current seismic hazard assessment? Are there any open questions regarding seismic hazard assessment and fault investigations?
573 | Slovak Republic |  | 21, 30, 40, 46, 49 | The protection against the design basic flood (DBF) of Mochovce 1/2 is adequate mainly due to the relatively high difference in altitude between the site and the closest rivers. However, an assessment of the safety margins against extreme flooding events was required; places where water accumulates were to be identified. Immediate implementation of temporary solutions and the proposal of a final solution were scheduled to be finished by 31/12/2013 (ID 12). According to the updated NAcP, the measure is completed. New metrological studies for the site were developed. Immediate measures (flood protection bags) were implemented. In December 2013 a draft time schedule of implementation of measures for 2014 - 2018 to enhance the resistance of selected civil structures was prepared, and an overall assessment of impacts of extreme meteorological events on safety and reliability of civil structures, including margins to withstand these events was prepared. Question 4: Which measures to enhance the safety margin against flooding events has the operator proposed and which additional measure has UJD SR required?
574 | Slovak Republic |  | 5, 23, 24 | Concerning extreme weather events, precise quantitative specification of the cliff-edge effects was not available. Evaluation is required of the resistance of selected SSCs against extreme weather events (floods caused by heavy rain, high and low external temperatures, direct wind and other relevant events) on the basis of updated new studies on meteorological conditions, and to consider events with intensity corresponding to the probability of occurrence once per 10,000 years or less. The plan for implementing these measures was to be prepared by 31/12/2013 (ID 4). According to updated NAcP, the measure has been completed. As mentioned above new metrological studies for the site were developed and in December 2013 a draft time schedule of implementation of measures for 2014 - 2018 to enhance the resistance of selected civil structures was prepared. Question 5: Which measures are envisaged? Why is the deadline for the implementation not early as 2018? Which measures has the operator proposed and which additional measure has UJD SR required?
575 | Slovak Republic |  | 28, 29, 32, 35, 38, 41, 44 | The emergency power sources are to be diversified by deploying mobile diesel generators (DG) that can also charge the accumulator batteries; to be finished by 31/12/2013 (ID 20). According to the updated NAcP, the measure is completed. Mobile DG (0.4 kV) with connecting cabling were purchased in 2012. In 2013, mobile rectifiers to charge accumulators from this DG were supplied. Question 6: Is the operability of the mobile DGs assured also under severe accident conditions?
576 | Slovak Republic |  | 25 | Alternative cooling and heat sink: To analyze and if needed to ensure means for cooling water make up from in-site and off-site water sources in the case of lack of cooling water, incl. preparation of respective procedures by 31/12/2013. (ID 18) According to the updated NAcP, necessary equipment has been analyzed and purchased for example: portable pumps, portable switchboards. Training programmes for the diverse mobile devices for cooling water make up from in-site and off-site water sources were prepared and tested during emergency exercises. Question 7: How does UJD SR assess the reliability of the measure concerning alternate cooling and heat sink? Does the operator consider installing an independent diversified alternate ultimate heat sink (UHS)? Does the nuclear authority consider requiring the installation of an independent alternate UHS?
577 | Slovak Republic |  | 37, 48, 50, 52, 53, 54, 55, 57, 58, 60, 63 | The SAM project being currently implemented is based on originally defined scope with assumptions for occurrence of a severe accident on only one of two units. The analysis and the modification of the SAM project from the viewpoint of severe accident management at both units are necessary. The plan of implementation of additional measures shall be prepared by 31/12/2014 (ID 39; ID 44) According to the updated NAcP, the measure is completed. NAcP states that the analysis of severe accident management at all units on the site (including reactors at full power, reactors in shutdown and spent fuel pool) has been prepared (Report No. CVV 12/2014-01 “Management of Severe Accidents on All Units on Site”). The licensee performed a self-assessment on the implementation of severe accident management. A plan of implementation of additional measures is under preparation. The analyses has been completed and at present evaluated by the licensee. The plan of implementation of measures is dependent on the evaluation of the analyses results. Question 8: When are the analyses expected to be completed? Why is the measure announced to be “completed”, despite the fact it is not completed. Why are the measures delayed? Which time schedule for implementation of measures is envisaged?
578 | Slovak Republic |  | 14 | The NAcP requires analyzing the need for filtered containment venting and other potential technical measures for long-term heat removal from the containment by 31/12/2015 (ID 2). According to the updated NAcP, the project is in the phase of elaboration with the contractor VUJE. Finishing of the project expected by the defined deadline. Question 9: Is there a tendency in favor or against the implementation of a filtered venting system?
579 | Slovak Republic |  | 24473 | Instrumentation and monitoring: To analyze the availability of important parameters, and if needed, to ensure mobile measuring units which can use stabile sensors also without standard power supply by 31/12/2015. According to the updated NAcP, the technical specification and procurement of the mobile measuring unit in progress. (e. g. equipment for measuring of temperature and pressure in the primary circuit and water level in the SG). Question 10: What are the technical specification of these mobile units regarding earthquake resistance and duration of long-lasting events?
580 | Slovak Republic |  | 14, 34 | The conditions of the environment of rooms with safety relevant equipment during long-term station blackout (SBO), loss of ultimate heat sink (UHS) and severe accidents were to be analyzed. The plan of the required measures was to be prepared by 31/12/2013 (ID 25). According to the updated NAcP, the measure is completed. The impact of extreme external climate conditions in selected rooms was analyzed. A plan on the implementation of some additional measures resulting from the analyses was prepared. Question 11: What is the time schedule for the necessary back-fitting measures?
581 | Slovak Republic |  | 64 | The leak-tightness of all penetrations through the containment under severe accident conditions (in particular leak-tightness of seals) have to be verified. Another task was to analyze the SAM project from the viewpoint of resistance of seals and penetrations of the containment under severe accident conditions by 31/12/2015 (ID 54). According to the updated NAcP, the project is completed. A study was prepared by UJV Řež to test the sealing under SA conditions. Replacement of seals at the reactor pressure vessel cavity lids and doors is in progress. Question 12: When will the replacement of seals at the reactor pressure vessel cavity lids and doors be finished?
582 | France |  | all | France (in particular Cattenom, Fessenheim and Gravelines 1. ASN requested EDF to conduct a more in-depth seismic margin assessment (SMA), which was performed during the stress tests in a simplified way. The review of the equipment likely to suffer cliff-edge effects, and the initiating of the necessary corrective measures is to be done until mid-2014. (FLE-3) According to the updated NAcP, first elements of this assessment were submitted by EDF in mid-2014. Question 1: Which safety important Structures, Systems and Components (SSCs) show small safety margin? Which correction measures are proposed by EDF and which additional correction measure are required by ASN? 2. A study evaluating the resistance to an earthquake of fire-fighting systems (fire detection and fixed extinguishing systems) and a program of necessary modification was to be done by 30/12/2012 (ECS-12). According to the updated NAcP, this measure is completed. EDF has submitted the required studies and proposed a program of modifications aiming to ensure the seismic resistance of its facilities at these increased levels. These modifications will be carried out during the periodic safety reviews of the reactors concerned. Question 2: Which modifications are proposed by EDF and which additional modifications are required by ASN? 3. Earthquake induced flooding represents a hazard for Fessenheim: The seismic robustness of the Grand Canal d’Alsace embankments and other structures designed to protect the NPP against flooding and the possible consequences of a failure of these structures were to be analysed by 31/12/2013. (ECS – 11) According to the updated NAcP, EDF submitted the synthesis of its studies at the end of 2013. The studies necessitated additional analyses. ASN has tasked IRSN, its technical support organisation, to evaluate the robustness of the embankments and other protective structures against earthquakes including more specifically surveys of the in situ structures. The conclusions should be available at the end of the first quarter of 2015. Question 3: What are the results of the analyses by IRSN? How does IRSN asses the robustness of the embankments and other protective structures against earthquakes? In the opinion of ASN, is the seismic robustness sufficient? What could be the result of a possible earthquake induced flooding event for Fessenheim? 4. ASN asked EDF to propose a hardened safety core (“noyau dur” (ND)) of robust material and organisational measures designed in response to the extreme situations studied in the stress tests, by 30/06/2012. The hardened safety core includes systems that are independent and diversified with respect to the existing systems in order to limit common mode risks. The systems, structures and components (SSCs) shall be protected against on-site and external hazards. (ECS – 1). According to the updated NAcP, a specific meeting of the Advisory Committee of Experts for nuclear reactors (GPR) was scheduled for 13 December 2012 to decide on the objectives associated with the hardened safety core. The GPR concluded on the need to supplement the functional perimeter of the hardened safety core and to detail the design hypotheses, particularly with regard to earthquakes. On this basis ASN has issued complementary prescriptions through a set of resolutions dated 21 January 2014. On 30 June 2014, EDF submitted the list of new and existing equipment items intended to form part of the hardened safety core, the general hypotheses for the design, construction, verification, qualification and testing of these new or existing equipment items, the seismic levels for each site in response to ASN's demand of 21 January 2014. These files will be examined by the GRP in the first half of 2015. Question 4 : The time schedule for the definition of the ND was postponed. Does ASN expect further delays? What is the main reason for the delays in the opinion of the ASN? What will be the earliest and what the latest
583 | Slovak Republic |  | 59 | To analyze the SAM project from the viewpoint of potential migration of hydrogen to other places by 31/12/2015 (ID) According to the updated NAcP, the project is in the phase of elaboration with the contractor UJV Řež. Preparation of the initial study which will be followed by other investigations in progress. Partial project outputs can be expected at the beginning of 2015. Question 13: Will there be the need for the installation of additional PARs or other measures?
584 | Slovak Republic |  | 9, 10, 25, 26, 27, 39, 42, 45, 47, | One of the most important modifications concerning the prevention of major radioactive releases during accidents is the external cooling of the reactor pressure vessel (RPV). This so-called in-vessel retention (IVR) concept aims to ensure the integrity of the RPV during a severe accident. Until now proof that this concept fulfils all the intended functions was delivered only with limited experimental analyses. Therefore the peer review team recommended considering a failure of the reactor pressure vessel (RPV), despite the fact this is claimed to be very unlikely. However, the evaluation of the consequences of RPV failure is not included in the NAcP. Question 14: Why did UJD not follow the recommendation of the peer review team to consider a RPV failure?
585 | Belgium |  | all | Belgium 1. In April 2011 following the Fukushima accident, Electrabel commissioned a probabilistic seismic hazard analysis (PSHA) using a state-of-the-art methodology. This PSHA resulted in a considerable increase of intensity of the design basis earthquake (DBE): For the Tihange site the value of the peak ground acceleration (PGA) increased from 0.17 g to 0.23 g (increase of 35%), for the Doel site from 0.056 g to 0.081 g (45%). A more elaborate PSHA study, e.g. with due consideration of results arising from the EC-project SHARE (seismic hazard harmonization in Europe) was required. NAcP: Detailed studies for both sites have to be conducted by the Royal Observation of Belgium (ROB); target date was 31/12/2014. (No. 1 and No. 429). The updated NAcP does not mention these studies. Question 1: What are the results of these detailed studies? Which PGA values have been calculated? 2. Adequacy of the design basis earthquake (DBE): The updated NAcP states, Doel 1 and 2 were not assessed for this aspect, because of their imminent shutdown. Question 2: Will FANC require to evaluate the adequacy of the DBE for the Doel 1 and 2, because the imminent shutdown is cancelled? What will be the time schedule for this evaluation? 3. Adequacy of the design basis earthquake (DBE) Tihange NPP: According to the updated NAcP, the reevaluation of the seismic hazard is currently still in progress. Electrabel plans to have the final report ready by early 2015. Question 3: What are the results so far? Which time schedule will be set for necessary backfitting measures? 4. The seismic margin review1 in the frame work of the stress tests have highlighted that 28 Structure, Systems and Components (SSC) of Doel and Tihange have a low probability of resisting an earthquake exceeding the “Review Level Earthquake” (RLE). 22 systems, structures and components (SSC) were identified at Tihange 1, 3 at Tihange 2, 1 at Doel 1/2, 1 at Doel 3 and 1 at Doel 4. The necessary backfitting was to be finished by 2013. According to the updated NAcP, the backfitting is not finished. Question 4: Which measures have to be performed in 2015? Does the new seismic hazard evaluation indicate to define a new Review Level Earthquake (RLE) (Tihange RLE = 0.3g, Doel: RLE = 0.17g)? Which would be the consequence? 5. Concerning the necessary reinforcement of the electrical auxiliary building (BAE) at Tihange 1 a feasibility study was to be performed by 2012. According to the updated NAcP, this feasibility study showed that the actions necessary for reinforcement are technically difficult or impossible. Nevertheless, there remain some specific and feasible improvements that could be considered. The improvement of the BAE has been incorporated in the action plan for the Long Term Operation (LTO) of this reactor. Question 5: What are the specific reason that the reinforcement of electrical auxiliary building (BAE) at Tihange 1 was assessed to be technically difficult or impossible? Was the construction of new electrical auxiliary building (BAE) at Tihange 1 considered? What is the consequence of incorporating the improvement in the action plan for the LTO? 6. The reinforcement of the refuelling water storage tank at Doel 1/2 was to be done by 15/12/2014. According to the updated NAcP, when the Belgian government decided in 2013 to permanently shut down these two nuclear reactors in 2015, the Regulatory Body deemed it unreasonable to still demand the implementation of this action. At the end of 2014, debates on the permanent shut-down of Doel 1/2 were re-opened again, so it is possible that the regulatory body will demand implementation of this action after all, as part of the Long Term Operation requirements. Question 6: Does FANC demand the reinforcement of the refueling water storage tank at Doel 1/2? What is the status of reinforcement of the refuelling water storage tank at Doel 1/2? What is the consequence of demanding the implementation
586 | Switzerland |  | various | Switzerland (Draft) 1. An earthquake exceeding the design basis can possibly occur at the Muehleberg site. The seismic hazard assessment of the PEGASOS project (2004) indicates that the current design maximum PGA of 0.15g for safety significant buildings and systems could be exceeded at a frequency of approx. 6 x 10-4 per year, which is not extremely rare. The resistance against earthquake is not in compliance with the ENSREG recommendation. In order to reduce the uncertainty of the PEGASOS results, the PEGASOS Refinement Project (PRP) was initiated. The re-assessment should define the updated site-specific seismic hazard levels (H3). The PRP project was expected to be completed in 2013 (PP1). According to the updated NAcP, the results of the PEGASOS Refinement Project (PRP) were submitted to ENSI for final review. It is stated that depending on the outcome of the review a renewed seismic safety assessment by the operators may be required. According to our information, the review and publication of the results of the PRP, announced for 2014 at the latest, have been delayed once again. Question 1: What are the outcomes of the PRP? When are the results going to be published? What are the reasons for the new delay? Which site-specific values (PGA) for the seismic hazard (H3) have been evaluated? Will a new seismic safety assessment be requested by ENSI? If yes, in which time schedule the reassessment and the subsequent backfitting measure are to be performed? 2. The PEGASOS Refinement Project (PRP) should define the updated site-specific seismic hazard levels (H3). During the EU Stress Tests the outdated hazard levels H1 and H2 were used to evaluate seismic margins of the SSCs. Nevertheless, the evaluation revealed only small safety margins (e.g. for one safety train for core cooling and spent fuel pool cooling). Question 2: Will ENSI ask for a new seismic margin assessment using the updated site-specific seismic hazard level (H3) for all plants? 3. The potential failure of the Wohlensee dam located 1 km upstream is a serious seismic hazard for the Muehleberg NPP. The dam is very old and might break in case of a severe earthquake. After the dam break, clogging of the NPP cooling water intakes has to be expected, potentially causing the reactor cooling to fail. (PP1) Question 3: According to the updated NAcP, reinforcement project of the Wohlen Lake dam was finished in 2014. However, the results of the PRP, whose review is still ongoing, could show the need for a new assessment, will ENSI ask for a new assessment and/or for new reinforcement project? If not, why not and if yes, in which time frame? 4. Regarding seismic robustness of the containment and primary circuit, ENSI will complete the reviews for all the NPPs by issuing evaluation reports in the course of 2013. Possible further actions will be decided upon in 2013(OP 2-2). Question 4: According to the updated NAcP, ENSI will require a more detailed examination of the seismic robustness of the isolation of the containment and the primary circuit. What is the status of this action? Will the same scope of measures for all NPPs (including Muehleberg NPP) be required by ENSI? 5. In 2013, ENSI has set up a working group to investigate the necessity to implement automatic scrams triggered by seismic instrumentation. Once the information including international practice is collected and structured, ENSI will issue an evaluation report. Based on these results a backfitting demand could be sent to the licensees, if considered necessary. (OP 2-1). According to the updated NAcP, ENSI is analysing the advantages and disadvantages of an automatic shutdown of the plants triggered by the seismic instrumentation. Depending on the results of the analysis, upgrades could be initiated. Question 5: When will the decision be made? When could the implementation be finished? 6. ENSI will follow up on the impacts of a total debris blockage of hydraulic engineering installat
587 | Sweden |  | Entire report | The updated Swedish Action Plan by SSM is highly problematic since it obviously is not taken seriously by SSM, but rather a quick fix to get it over and done. In short this is a very disappointing report that does not really do anything to increase the credibility of the whole stress test exercise. The best would be when this action plan is rewritten taking into account what really happened in the two years since the 2012 version and including transparent references. Concerning several of the more important issues identified during the stress tests like cooling problems in severe accident situations, hydrogen, venting, it should be considered to withdraw the operation license of reactors until the necessary measures are actually implemented. One serious issue of the updated action plan is that it largely is a cut and paste exercise. The report consists of 70 pages. Out of these 70 pages 45 are copies of the previous report, with only a few minor wording changes. Within these 45 pages there are embarrassing mistakes where SSM are writing about future actions, to be conducted during 2013! If a serious effort would have been put into this report we would instead have got to know more about the results from these actions. It is clear that the function of this report has not been taken seriously by SSM. It is basically non-information and the vast majority of it is a cut and paste of the 2012 action plan. Some examples: SSM is in part 4.2 writing about the exercise Havsörn 2013. In several paragraphs it is described what the purpose of the exercise is etc. This is a clear example of that the Swedish Updated National Action Plan is not taken seriously by SSM. It would instead have been interesting if SSM were to summarize some of the learnings of the exercise that reveals several serious issues in the Swedish emergency preparedness, for example: The knowledge is poor about the system of alarms for nuclear hazards. Another issue is that there is a fundamental problem when it comes to knowledge in what different actors’ responsibilities are which leads to a lack of a comprehensive picture. These, and many other learnings could be found in the evaluating report, which is available here: http://www.lansstyrelsen.se/uppsala/Sv/publikationer/2014/Pages/utvarderingsrapport-ovning-havsorn-2013.aspx Another example of the lack of serious work by SSM in the updated Action Plan is in Part 4.3. It is a complete copy and paste from previous report and for example SSM is not writing anything about the Government decision of January 24, 2014 to commission SSM and other agencies to produce a National Plan for Emergency Preparedness (which eventually was delivered in February 2015). In part 6.3 SSM is writing that an action plan for managing recommendations and suggestions from the IRRS mission to Sweden is being prepared and that the recommendations “is planned to be implemented by December 2013.” Instead of copy and paste, it would have been interesting to know if the action plan is finished and the recommendations are fully implemented. In Part III, 7.1 SSM is writing that “almost all modernization activities of Oskarshamn 2 is planned to be completed in 2013.” Instead of copy and paste the previous original Action Plan, it would have been interested for ENSREG and the public to know that many of the modernization activites of Oskarshamn 2 is NOT AT ALL finished, and that SSM in December 2014 again did grant OKG respite to finish the activities. When it comes to the roughly 25 pages where there are a review of the action plan the information is very poor. There are extremely limited information about what has been done and what remains. Also there are no references at all to further documentation. There are no details in the tables in part 8.3 and 8.4 – the level of abstraction comes down to “trust us, we are doing our best”. On the contrary, this non-information undermines the trust of SSM and the operators. From issues
588 | Sweden |  | Entire report | The updated Swedish Action Plan by SSM is highly problematic since it obviously is not taken seriously by SSM, but rather a quick fix to get it over and done. In short this is a very disappointing report that does not really do anything to increase the credibility of the whole stress test exercise. The best would be when this action plan is rewritten taking into account what really happened in the two years since the 2012 version and including transparent references. Concerning several of the more important issues identified during the stress tests like cooling problems in severe accident situations, hydrogen, venting, it should be considered to withdraw the operation license of reactors until the necessary measures are actually implemented. One serious issue of the updated action plan is that it largely is a cut and paste exercise. The report consists of 70 pages. Out of these 70 pages 45 are copies of the previous report, with only a few minor wording changes. Within these 45 pages there are embarrassing mistakes where SSM are writing about future actions, to be conducted during 2013! If a serious effort would have been put into this report we would instead have got to know more about the results from these actions. It is clear that the function of this report has not been taken seriously by SSM. It is basically non-information and the vast majority of it is a cut and paste of the 2012 action plan. Some examples: SSM is in part 4.2 writing about the exercise Havsörn 2013. In several paragraphs it is described what the purpose of the exercise is etc. This is a clear example of that the Swedish Updated National Action Plan is not taken seriously by SSM. It would instead have been interesting if SSM were to summarize some of the learnings of the exercise that reveals several serious issues in the Swedish emergency preparedness, for example: The knowledge is poor about the system of alarms for nuclear hazards. Another issue is that there is a fundamental problem when it comes to knowledge in what different actors’ responsibilities are which leads to a lack of a comprehensive picture. These, and many other learnings could be found in the evaluating report, which is available here: http://www.lansstyrelsen.se/uppsala/Sv/publikationer/2014/Pages/utvarderingsrapport-ovning-havsorn-2013.aspx Another example of the lack of serious work by SSM in the updated Action Plan is in Part 4.3. It is a complete copy and paste from previous report and for example SSM is not writing anything about the Government decision of January 24, 2014 to commission SSM and other agencies to produce a National Plan for Emergency Preparedness (which eventually was delivered in February 2015). In part 6.3 SSM is writing that an action plan for managing recommendations and suggestions from the IRRS mission to Sweden is being prepared and that the recommendations “is planned to be implemented by December 2013.” Instead of copy and paste, it would have been interesting to know if the action plan is finished and the recommendations are fully implemented. In Part III, 7.1 SSM is writing that “almost all modernization activities of Oskarshamn 2 is planned to be completed in 2013.” Instead of copy and paste the previous original Action Plan, it would have been interested for ENSREG and the public to know that many of the modernization activites of Oskarshamn 2 is NOT AT ALL finished, and that SSM in December 2014 again did grant OKG respite to finish the activities. When it comes to the roughly 25 pages where there are a review of the action plan the information is very poor. There are extremely limited information about what has been done and what remains. Also there are no references at all to further documentation. There are no details in the tables in part 8.3 and 8.4 – the level of abstraction comes down to “trust us, we are doing our best”. On the contrary, this non-information undermines the trust of SSM and the operators. From issues
589 | Germany |  | 1 | To implement the actions following the stresstest procedures to approve the measures of the opertors must be in place. Which procedures had and have been forseen and executed? Could you make available of a list of the executed or ongoing procedures of approvement (plantspecific) ? In Germany every change in the plant that can have positive or negative impacts on the safety of the plants have to licensed. The function of this regulation is beside other purposes to open participation procedures. Are there licensing procedures in place? As far as there are no licensing procedures in place, do the corresponding measures taken have no relevant impact for the safety of the plant? Wolfgang Renneberg, Institute for Safety- and Risk Sciences, BOKU, Vienna
590 | Belgium |  |  | The full list of actions (see «Datasheet Implementation of activities») updated with the current status of every action (in progress/completed, and in case of delay, a new deadline or comments clarifying the situation) should be provided
591 | Belgium |  | 9 | It is mentioned that «actions performed at the corporate level (…) have been added to the graph». Were these actions already included in the original action plan or are they new? In the latter case, what is the nature of these actions?
592 | Belgium |  | 10 | The report mentions, that the second level for flood protection (local volumetric protections) has been abandoned because of the complexity of the interactions with the other levels of protection. Could you provide more details on these interactions and the specific concerns justifying this decision?
593 | Belgium |  | 3, 7, 9 and 23 | Discussions were ongoing at the time of the NAcP report preparation and still continue regarding Doel 1&2 shutdown or life extension. Could you please clarify the impact of these discussions on possible safety improvements for Doel 1&2 especially regarding earthquake analyses, water supply to Steam Generators, installation of Filtered Venting Systems?
594 | Bulgaria |  |  | The national report does not refer to the new WENRA reference levels. The WENRA reference levels were updated taking into account the lessons learnt from the Fukushima Dai-ichi nuclear accident and the recommendation of the follow-up EU stress test exercise. How the new reference level and in specific "Issue T: Natural hazards" will be implemented and follow up by the Bulgarian regulations?
595 | Czech Republic |  | 6 to 8 | Studies are ongoing regarding applicability of IVR or ExVC especially to the VVER 1000 units in Czech Republic. Under which timeframe are these studies expected to be finalized? What are the deadlines for subsequent potential plant modifications according to the results of the studies?
596 | Finland |  | 45 (4,5) | For the National Action Plan, two action points, which are related to the interaction of the "nuclear sector" with the "non-nuclear sector", are the only "national" action points which have not been implemented. It should be clarified whether this is related to the fact that it is outside the direct competence of STUK, whereas the responsibility to implement the measures is national
597 | Finland |  | 27 | Large volumes of contaminated water: As in the previous report, no preparation for solutions for post-accident contamination and treatment of potentially large volumes of contaminated water have been initiated. From other parts of the report, the shallowness of the seas around Finland is used as an argument not to take high tsunami waves into account (p.9). Furthermore, for both Loviisa and Olkiluoto, there is a difficulty to find/ define an alternative heat sink which does not rely on the sea water. This is an indication that other water sources are not abundant and that they may have to be protected from contamination. It should be better explained why it is accepted that no preparation for possible solutions has been initiated until now.
598 | France |  | 11 | Article 1.1.1. Hazard frequency: previous report stated that ASN will adopt a position on the methodology produced by EDF (for the development of an experimental probabilistic seismic safety study for the Saint-Alban NPP). In the actual report it is stated that the issue was discussed in the meetings of the Advisory Committees of Experts, which concluded that the works should be continued with the aim of developing a method that can be used in the next periodic safety reviews. Is there any deadline specified for the implementation of the developed methodology and implementation at the France nuclear fleet?
599 | France |  | 19 | Hardened safety core, section 1.2, LOSS OF THE SAFETY SYSTEMS: ASN mentioned several times in the report that the requirements of the hardened safety core of systems, structures and components (SSC) will be specified. So far final requirements will not be available before mid-2015 after the GRP meeting.Is there a deadline foreseen or planned for the implementation of hardened safety core requirements for SCC
600 | France |  | 18 | Specific inspections and verifications of facilities: Introducing of ASN guidelines, dealing with the deviations relative to earthquake resistance, protection against flooding and other hazards, is delayed. Does the delay of the guidelines affect the inspections?
601 | France |  |  | Studies regarding: - hardened safety core: actions ECS-1- seismic risk, actions ECS-12,- flood risk: actions ECS-11,- water and electrical supply: actions ECS-15, ECS-17,- severe accident and emergency accident: actions ECS-29, ECS-21, ECS-23, ECS 14.1, ECS 14.2, ECS 19 were provided in time by the licensee. The analysis and decision making by ASN is on-going or planned for the first half of 2015. Does the extensive evaluation and decision making process have an effect on the overall implementation schedule of the actions?
602 | France |  |  | ECS - 29: Reinforcement of the U5 venting-filtration system ("sand-bed filter"). The licensee performs studies on a solution enabling the U5 filter (container venting-filtration system) not to be used in a severe accident situation, instead controlling the pressure in the reactor containment through an ultimate spraying system. What are the reasons for a possible change in the philosophy of pressure reduction in the containment?
603 | Germany |  |  | There are some uncertainties regarding the consideration of the German recommendations (numbered N-1 to N-24) for all individual plants. It is probable that some recommendations are not applicable to all plants (like for example N-7 on spent fuel pool being stored outside the containment), but it is not so clear for other recommendations. More specifically, N-14, N-16 and N-17 are not mentioned for GKN-II and KKP 2; many recommendations are not mentioned for KRB B+C (N-3, N-4, N-11, N-12, N-14, N-16, N-17, N-20 and N-21). For these three plants, it should be explained if the recommendations are applicable and if yes, how they are considered
604 | Germany |  |  | Previous question is also valid for the shutdown plants, although there are of course several non-applicable recommendations for those plants. For example, it is not clear why recommendation N-24 about extreme weather is mentioned for some shutdown plants (GKN-1, KKI-1, KKP-1, KKU and KWB A+B), but not for the others (KKB-1 and KKK)
605 | Hungary |  | 65 | Task 28 concerning PSA assessment. Would it be possible to get some information about the results of the PSA assessment?
606 | Hungary |  | 66 | Task 30 regarding the system to prevent long term containment pressurization. Could you please provide additional information regarding the solution chosen and associated analyses performed?
607 | Lithuania |  |  | no questions
608 | Netherlands |  | 109 | Concerning procedures for handling large amounts of radioactive water, it is stated that “An existing 17.000 m3 water tank connected to underground piping can be used to store a large amount of radioactively contaminated water”. It is not clear if a 17.000 m3 water tank is enough to handle large amounts of radioactively contaminated water resulting from a severe accident. Additionally the robustness of the tank and the underground piping in case of a severe seismic event is not elaborated in the report.
609 | Romania |  |  | The updated NAcP does not explicitly highlight or specify any nationally identified good practices. Are there some findings that Romania would recommend to other countries?
610 | Slovak Republic |  | ID18 | ID 18 (on alternative cooling and heat sink), part 3: The action 'to finish required modifications of existing equipment for connection of diverse mobile feedwater and power sources resistant to external events' is marked as completed, but the additional measure to provide shelters for placing some mobile equipment and cabling is in progress. It would remain to be confirmed that this mobile equipment is already operational before the installation of its shelters
611 | Slovak Republic |  | ID25 | ID 25 on ventilation: the 1st part of this action is not listed anymore. Its status should be clarified
612 | Slovak Republic |  | ID55 | ID 55 on large area fire control: parts 2 to 4 of this action are not listed separately anymore. Their status should be clarified
613 | Slovenia |  | 10, 14-15 | The Action 1.1 (see Table 4) for «Safety upgrade of AC power supply» has a new deadline in 2018. However, it is not mentioned in the paragraph 5.2.1 (pp. 14-15). Could you indicate in which phase (1, 2 or 3) of the new schedule for the Safety Upgrade Program will Action 1.1 be included?
614 | Slovenia |  | Table 1 | The same question applies to Action 1.7 in Table 1 («Installation of a fixed spray system around the SFP with provisions for quick connection from different sources of water»)
615 | Slovenia |  | 10 | Table 4 indicates for all actions in the Safety Upgrade Program (except 1.5), that status is «in progress». However, from the clarifications given in paragraph 5.2.1, it is not clear if some progress has been achieved. Could you indicate which of these actions have been started, if any, and what specific progress has been achieved so far?
616 | Spain |  | table Attachment 1/p.20 | The table in Attachment 1 does not include new action points, as also stated on p.20: "No relevant additional measures have been included." In the action list, many analysis have been listed, some of those with the sub-task "implementation of identified improvements". However, 11 analyses do not contain such a statement, which is the same in the previous action plan. It should be clarified whether this means that for the analysis under: A1, A2, A3, A4, A5, A8, A9, I16, I17, I19, I20 no additional activities were necessary.
617 | Spain |  | 21 | Two activities A9 and I17 are reported as "A number of difficulties have been encountered due to scarcity of international experience". It should be clarified which activities Spain has carried out to meet this challenge and whether activities at European level can contribute to the solution of such difficulties.
618 | Spain |  | 22 | The special situation of the Garona Plant should be elaborated further (change of closure date previously 2013 and now 2019). It should be especially clarified how stress tests evaluation in 2012 for Garona NPP could have been affected by the fact that the plant was supposed to shut down in 2013 and now should remain in operation until 2019.
619 | Sweden |  |  | Clarification would be needed for the action, where the year of completion and the related comment seem to be contradictory: For the status of action T3.LA.11, Analyse the management of hydrogen in long-term it is reported "Investigation into the handling of hydrogen (oxyhydrogen) after a severe accident is handled in a joint licensees project within the Nordic Owners group (NOG). So far, the project has focused on hydrogen formation and accumulation in the reactor containment. A number of potential shortcomings in the handling of hydrogen gas after a severe accident have been identified." The reported year for completing the action is 2014, but the comment gives the impression that the project has not been completed yet. What is the status of this action?
620 | Sweden |  |  | Clarification would be needed for the action, where the year of completion and the related comment seem to be contradictory: For the status of action T1.RA.1, Research project regarding the influence of paleoseismological data it is reported "A literature search has been initiated". The reported year for completing the action is 2013, but the comment gives the impression that the project has not been completed yet. What is the status of this action?
621 | Sweden |  |  | As a minor comment: It would be helpful to have the full action titles in the summary tables. Most of the action titles of actions to be performed by the licensees have been shortened in the updated report, and do not describe sufficiently the action
622 | Sweden |  | 20 | Even if the report presents valuable information regarding the progress of actions, the understanding of the situation in Sweden could be significantly improved by addressing the following comments: The NAcP states , that "The outcome of the evaluations and reassessments shall result in which technical and/or administrative measures that needs to be implemented and when in time they will be fully implemented". However, for cases where analyses have been completed and further measures are identified, no time schedules are provided for the implementation of the measures. Have the licensees provided SSM with any detailed time schedule for implementing the measures? It would be advisable to indicate the time schedules in the summary tables
623 | Sweden |  |  | Now that most of the evaluations and reassessments have been completed, it would be advisable to provide more plant-specific information in the implementation plans of technical and/or administrative measures
624 | Switzerland |  |  | It is recommended to include a time schedule with original and possibly updated target dates for the implementation of each activity
625 | Switzerland |  |  | As the decision to shut down Mühleberg has been recently reconsidered, what effects does the new situation have on the actions related to the plant?
626 | Ukraine |  |  | Some additional information requested by the ENSREG is missing from the report, such as: nationally identified good practices and challenges during implementation so far (Part II)
627 | Ukraine |  |  | Some additional information requested by the ENSREG is missing from the report, such as: Relevant outcomes of studies and analyses identified in the 2013 action plan and completed since the 2013 ENSREG workshop (Part II)
628 | UK |  | 8 | According to point 30: "…ONR is leading the development of guidance on natural hazards on behalf on the Western European Nuclear Regulators Association in addition to the work undertaken in the UK…" This is the same statement as in 2012. Would it be possible to get some information about the progress made regarding the development of this WENRA guidance on natural hazards?
629 | UK |  | 41, 47-48 | According to table 1 or 3 of 2014 NAcP, the STF-5 and STF-7which are related to completion of studies regarding flooding and extreme weather have been postponed to Q2 2015, so 2 years later than in the 2012 NAcP. Could you please provide explanation for this delay?
630 | UK |  | 48 | According to table 3 of 2014 NAcP, The STF-3 covering Actions from operators in mitigation external hazards – initial operator action review – seismic have been postponed to Q2 2015, so 2 years later than in the 2012 NAcP. Could you please provide explanation for this delay?
631 | UK |  | 49 | According to table 3 of 2014 NAcP, the IR-17 – National Grid resilience assessment has been postponed to Q1 2015, so 2 years later than in the 2012 NAcP. Could you please provide explanation for this delay?
632 | UK |  | 55-56 | According to table 3 of 2014 NAcP, the IR-24 & STF-16 – SBERGs and SAGs – Beyond Design Basis Task Analysis and Weather and Seismic Human Factors analyses have been postponed to Q2 2015, so 2 years later than in the 2012 NAcP. Could you please provide explanation for this delay?
633 | UK |  | 57 | According to table 3 of 2014 NAcP, the STF-18 – Installation of filtered venting system (if applicable) for Sizewell PWR – Decision to be taken in 2015 so 2 years later than in the 2012 NAcP. Could you please provide explanation for this delay?
634 | UK |  | 58 | According to table 3 of 2014 NAcP, the FR-6 – estimating radioactive source terms. This action is ongoing since 2012. It was supposed to be finalised later at that time and now it is supposed to be part of normal business. Could you please elaborate on this topic and explain what kind of studies have been performed or are ongoing to re-assess the source terms for all UK NPPs?
635 | Belgium |  | general | 1 In April 2011, following the Fukushima accident, Electrabel commissioned a probabilistic seismic hazard analysis (PSHA) using a state-of-the-art methodology. This PSHA resulted in a considerable increase of intensity of the design basis earthquake (DBE): For the Tihange site the value of the peak ground acceleration (PGA) increased from 0.17 g to 0.23 g (increase of 35%), for the Doel site from 0.056 g to 0.081 g (45%). A more elaborate PSHA study, e.g. with due consideration of results arising from the EC-project SHARE (seismic hazard harmonization in Europe) was required. NAcP: Detailed studies for both sites have to be conducted by the Royal Observation of Belgium (ROB); target date was 31/12/2014. (No. 1 and No. 429).The updated NAcP does not mention these studies.Question 1: What are the results of these detailed studies? Which PGA values have been calculated?
636 | Belgium |  | general | 2 Adequacy of the design basis earthquake (DBE): The updated NAcP states, Doel 1 and 2 were not assessed for this aspect, because of their imminent shutdown. Question 2: Will FANC require evaluating the adequacy of the DBE for the Doel 1 and 2, because the imminent shutdown has been cancelled? Will there be a new time schedule for completing this evaluation?
637 | Belgium |  | general | 3 Adequacy of the design basis earthquake (DBE) Tihange NPP: According to the updated NAcP, the re-evaluation of the seismic hazard is currently still in progress. Electrabel plans to have the final report ready by early 2015.Question 3: What are the results so far? Which time schedule will be set for necessary back-fitting measures?
638 | Belgium |  | general | 4 The seismic margin review[1] in the frame work of the stress tests has highlighted that 28 Structure, Systems and Components (SSC) of Doel and Tihange have a low probability of resisting an earthquake exceeding the "Review Level Earthquake" (RLE). 22 systems, structures and components (SSC) were identified at Tihange 1, 3 at Tihange 2, 1 at Doel 1/2, 1 at Doel 3 and 1 at Doel 4. The necessary back-fitting was to be finished by 2013.According to the updated NAcP, the back-fitting is not finished.Question 4: Which measures have to be performed in 2015? Does the new seismic hazard evaluation indicate the need to define a new Review Level Earthquake (RLE) (Tihange RLE = 0.3g, Doel: RLE = 0.17g)? What would be the consequences?
639 | Belgium |  | general | 5 Concerning the necessary reinforcement of the electrical auxiliary building (BAE) at Tihange 1 a feasibility study was to be performed by 2012.According to the updated NAcP this feasibility study showed that the actions necessary for reinforcement are technically difficult or impossible. In spite of this, some specific and feasible improvements could be considered. The improvement of the BAE has been incorporated in the action plan for the Long Term Operation (LTO) of this reactor.Question 5: What are the specific reasons that the reinforcement of electrical auxiliary building (BAE) at Tihange 1 was assessed to be technically difficult or impossible? Was the construction of new electrical auxiliary building (BAE) at Tihange 1 considered? What is the consequence of incorporating the improvement in the action plan for the LTO?
640 | Belgium |  | general | 6 The reinforcement of the re-fuelling water storage tank at Doel 1/2 was to be completed by 15/12/2014.According to the updated NAcP when the Belgian government decided in 2013 to permanently shut down these two nuclear reactors in 2015, the Regulatory Body deemed it unreasonable to still demand the implementation of this action. At the end of 2014, debates on the permanent shut-down of Doel 1/2 were re-opened again, so it is possible that the regulatory body will demand implementation of this action after all, as part of the Long Term Operation requirements.Question 6: Does FANC demand the reinforcement of the refueling water storage tank at Doel 1/2? What is the status of reinforcement of the re­fueling water storage tank at Doel 1/2? What is the consequence of demanding the implementation of this action as part of the LTO requirements, in particular concerning the time schedule for its implementation ?
641 | Belgium |  | Flooding hazard for the Tihange NPP site: | 7 A peripheral protection of the site (first level of flood protection) which shall consist of a wall including coffer dams to close the opening necessary for normal operation of the NPP is to be implemented by the end of 2014.According to the updated NAcP, the construction began in October 2013. By the end of 2014, the peripheral protection (wall, pumping chambers, isolation of the release structures, etc.) was almost completed. According to the licensee's schedule, the peripheral protection will be ready for commissioning by September 2015. Question 7: Does FANC expect the commissioning of the flood protection wall by September 2015?
642 | Belgium |  | Flooding hazard for the Tihange NPP site: | 8 According to the updated NAcP: As requested by the regulatory body, a safety margin for the wall height to adequately cover uncertainties associated with the new design basis flood was considered. However the NAcP does not explain which safety margin is added.Question 8: Which safety margin is added to the flood protection wall? Which are the known values of the uncertainties associated with the new designbasis flood? Are there any new results indicating that the possible extreme water level could be higher than height of the protection wall?
643 | Belgium |  | Flooding hazard for the Tihange NPP site: | 9 The NAcP required a second level of flood protection (local volumetric protections). According to the updated NAcP the second level of protection is cancelled. It explained that further analysis had shown that the implementation of the second level of flood protection would not provide an infallible protection and would decrease the reliability of the protection strategy against flooding due to the complexity of the interactions with the other levels of protection. The licensee and the Regulatory Body have therefore decided to abandon this second level.Questions 9: What are the specific reasons to cancel the second level of protection? How is this justified in regard to the ENSREG recommendation 3.1.3 (volumetric protection)?
644 | Belgium |  | Flooding hazard for the Tihange NPP site: | 10 When conventional equipment is rendered unavailable through flooding, the non- conventional means (NCM) (third level of flood protection) should be used. According to the updated NAcP the licensee has decided to reinforce the third level of protection, the non-conventional means to compensate for the delay in the construction of the site's peripheral protection. All the corresponding actions to these non-conventional means were finalized by the licensee in 2013. At the end of 2014, the regulatory body carried out the assessment of the modifications and officially closed the actions linked to this level of protection. This level of protection is now considered fully operational.Question 10: Is FANC convinced that Tihange NPP could cope with an extreme flooding event and prevent a severe accident using the non- conventional means (NCM)?
645 | Belgium |  | Flooding hazard for the Tihange NPP site: | 11 According to the updated NAcP only twelve of the 38 necessary actions against flooding are completed, the majority still being analysed by the regulatory body (16), the review of three actions are finished but additional questions have arisen and Electrabel is currently implementing seven actions?Question 11: Which actions is FANC reviewing, which actions led FANC rise questions and which actions is Electrabel currently implementing?
646 | Belgium |  | Flooding hazard for the Tihange NPP site: | 12 Flood protection at Doel NPP/ According to the updated NAcP two actions planned against flooding are closed, three actions the regulatory body is analysing, and the review of one actions led to additional questions.Question 12: Which actions is FANC reviewing, which actions led FANC rise questions and which actions is Electrabel currently implementing?
647 | Belgium |  | Flooding hazard for the Tihange NPP site: | 13 Regarding flood protection at Doel 1 and 2 Question 13: Was this aspect assessed for Doel 1 and 2? Were back-fitting measures performed or not because their imminent shutdown was assumed? Will FANC require assessment and subsequent flood protection measures now?
648 | Belgium |  | Flooding hazard for the Tihange NPP site: | 14 The stress tests revealed that the design parameters for extreme weather conditions for the Belgian NPPs are mainly based on historic data and therefore on a return period in the order of 100 years. ENSREG recommends the derivation of design basis parameters with 10,000 years return periods.Question 14: Did FANC follow the ENSREG recommendation using 10,000 years return periods of natural hazards for the reassessments?
649 | Belgium |  | Flooding hazard for the Tihange NPP site: | 15 Regarding heavy rainfalls, a reassessment of the capacity of the sewer system for return periods up to 100 years was required (target date Tihange: 31/12/2013; Doel: 01/11/2012). According to the updated NAcP at Doel, the licensee finalized its revaluation of the impact of heavy rains in 2014. The regulatory body is currently assessing these studies for Doel. At Tihange, important improvements of the sewer systems have to be realized by the licensee during 2015. The related project has been presented to the regulatory body. Question 15: What are the results of these reassessments? Why was a return period of up to 100 years only for these reassessments required?
650 | Belgium |  | Flooding hazard for the Tihange NPP site: | 16 According to the updated NAcP: At Tihange, regarding the actions against extreme weather conditions only one of five actions is closed by FANC, one action is under review by FANC, one action led to additional questions from FANC, one action is currently being implemented by Electrabel. Question 16: Which action is under review by FANC? Which actions led to additional questions and why? Which action is ongoing?
651 | Belgium |  | Flooding hazard for the Tihange NPP site: | 17 According to the updated NAcP: At Doel, regarding the actions against extreme weather conditions only one of six measure is closed by the FANC, the review of three action resulted in additional questions from the FANC, one action is under review by FANC, one action Electrabel is currently implementing. Question 17: Which action is under review by FANC? Which actions led to additional questions and why? Which action is ongoing?
652 | Belgium |  | Flooding hazard for the Tihange NPP site: | 18 According to the updated NAcP more than one hundred actions have been planned in the action plan for the enhancement of the power and the water supply in the Belgian NPPs. The licensee has currently finalized a little more than 50% of these actions. Question 18: When does FANC expect that all actions regarding the enhancement of the power and water supply will be completed?
653 | Belgium |  | Flooding hazard for the Tihange NPP site: | 19 In case of a total SBO and/or loss of ultimate heat sink, Electrabel plans to use new non-conventional means (NCM): to refill the steam generators and the spent-fuel pools, to ensure make-up for the primary circuit in open configuration, to avoid the over-pressure in the reactor building, to restore the electrical power supply to instrumentation and control panels, and to make operable the emergency compressed air circuit. Question 19: Is the operability and practicability of all the listed non- conventional means (NCM) under severe accident conditions assured?
654 | Belgium |  | Flooding hazard for the Tihange NPP site: | 20 According to the updated NAcP Electrabel had to delay several actions related to the CSBO project in order to primarily focus on the flooding project at Tihange in 2012­2013. Only some priority actions have already been executed during plant outages. Question 20: Has FANC considered requiring prolonged plant outages, because of the delay with all projects at Tihange?
655 | Belgium |  | Flooding hazard for the Tihange NPP site: | 21 According to the updated NAcP CSBO actions specific to Tihange 1 unit have been included in the action plan of the Long Term Operation of this reactor and are not any more considered in the stress test action plan. These actions are ongoing and have to be finalized before the second outage of the reactor following its lifetime extension (2016). Question 21: Why does FANC not require all actions of the LTO action plan being finalized before the approval of life time extension? Which actions of the NAcP are now part of the LTO action plan instead of the stress test action plan and what is the reason for moving them to another action plan?
656 | Belgium |  | Flooding hazard for the Tihange NPP site: | 22 To strengthen the power grid of Tihange, Electrabel had to study the feasibility of a better geographical separation of the high-voltage lines (150 kV and 380 kV), in collaboration with ELIA (the Belgian high-voltage network manager). In this framework, a request was sent to ELIA in 2013 to add new high-voltage lines from the other side of the Meuse, passing over the river. This solution was not judged realistic by ELIA. Question 22: Has a solution been found to this issue until now?
657 | Belgium |  | Flooding hazard for the Tihange NPP site: | 23 According to the updated NAcP FANC has requested for Tihange 2 and 3 to carry out alignment and operating tests of the emergency deep water intakes from the Meuse River and to justify the availability of the emergency intakes in accordance with the requirements of US NRC RG 1.27. The related actions have been finalized in 2013 by Electrabel and analysed by FANC in 2014. The licensees conclusions and the consequent proposed actions FANC still does not find fully satisfying, they were discussed at the end of 2014. Question 23: Why is FANC not fully satisfied with the proposed actions? What is the current status of this project?
658 | Belgium |  | Flooding hazard for the Tihange NPP site: | 24 Concerning the actions against the loss of water and power supplies, FANC closed only a few actions. Question 24: Which actions are under review by FANC? Which actions led to additional questions and why? Which actions are ongoing?
659 | Belgium |  | Flooding hazard for the Tihange NPP site: | 25 The NAcP requested a study of the potential design problems with the siphon breakers in the spent fuel pools (Deadline 31/12/2013). The updated NAcP does not mention this issue. Question 25: What is the result of the study?
660 | Belgium |  | Flooding hazard for the Tihange NPP site: | 26 None of Belgian NPPs is equipped with a filtered venting system. ENSREG emphasizes its importance to protect containment integrity and recommended itsurgent implementation. Nevertheless only a study of a filtered venting system was to be performed by 31/12/2012. According to the updated NAcP filtered vent systems will be installed on every NPP in operation. The realization phase has finally begun in 2014. The licensee plans installation depending on the NPP outages, up to end of 2017 for the latest unit. However the planning does not yet include the installation of filtered vent systems at Doel 1 /2. Question 26: Will FANC request the installation of filtered vent systems at Doel 1/2 soon after the extension of operation time has been approved? According to FANC, is there any possibility to accelerate the implementation process for the filtered venting systems at all NPPs?
661 | Belgium |  | Flooding hazard for the Tihange NPP site: | 27 The evaluation of the hydrogen risk of the spent fuel pools during a severe accident needs to be completed by 31/12/2012 (Status 2013: in progress). According to the updated NAcP the assessment of the risk of hydrogen production and accumulation in spent fuel buildings have been carried out in 2013. At the end of 2014, the study performed by the operator shows that there is no explosion risk due to the accumulation of hydrogen in the SPF buildings. FANC is still assessing this study. Question 27: What is the conclusion of this issue by FANC? Will FANC follow the recommendation by the peer review team and request the installation of PARs? The peer review team recommended in 2012, regardless of the outcome of this study, considering the installation of passive autocatalytic hydrogen re-combiners (PARs).
662 | Belgium |  | Flooding hazard for the Tihange NPP site: | 28 NAcP: To ensure containment integrity during total SBO, checks need to find out whether all penetrations through the containment building can be closed in due time and whether the building isolating systems remain functional, in particular during reactor shutdown states (target date 31/12/2013). Question 28: What is the outcome of these checks?
663 | Belgium |  | Flooding hazard for the Tihange NPP site: | 29 According to the updated NAcP most actions that had to be implemented at Doel 1 and 2 in the context of the stress test action plans (e.g. improving the reliability of the water supply to the steam generators) were originally scheduled to be integrated into the Long Term Operation of these reactors. Following the governmental decision to shut down these two reactors, the licensee was granted permission to refrain from implementing these actions. However, if the licensee decides to apply for a Long Term Operation of these two reactors, the regulatory body will need to reconsider its former decision in the upcoming months. Question 29: Which actions originally requested to implement in context to the stress test action plans at Doel 1 and 2, than cancelled were taking into account the limited operation time, are not required again and what is the reason for this decision? Does FANC consider requesting all identified stress test actions as necessary to be implemented before the approval of the operation time extension?
664 | Czech Republic |  | Tremelin | 1 Secondary effects of earthquakes were to be assessed by 2014. A seismic PSA including earthquakes, induced floods or fires with a proposal for remedial measures are to be performed by 2015. (No.4 No 70) According to the updated NAcP these activities are finished. Question 1: What has been the outcome of this assessment? Which remedial measures are proposed by the operator and which additional measures are required by SUJB?
665 | Czech Republic |  | Tremelin | 2 The reinforcement of the fire brigade building to withstand earthquakes is to be completed by 2014 (No. 2) According to the updated NAcP this action has been finished. Question 2: Please give the figure of the earthquake severity the fire brigade building should be able to withstand?
666 | Czech Republic |  | Tremelin | 3 Furthermore an assessment of the consequences of the seismic hazard for the site (e.g. damaged of the infrastructure) was to be performed in 2012 (status 2013: in progress). (No. 45) Question 3: What are the relevant outcomes of the assessment?
667 | Czech Republic |  | Tremelin | 4 Procedures for managing extreme conditions at the site regarding wind, temperature, snow, and earthquakes are to be developed by 2013. (No. 8) According to the updated NAcP this action has been finished. Question 4: How was the recommendation by the peer review team taken into account? The peer review team emphasized that the procedures for special handling of weather related threats need to be elaborated and some specific additions to the emergency management procedures might be necessary. The considerations for extreme low temperatures may be too simple, not taking into account the realistic related effects, e.g. station blackout.
668 | Czech Republic |  | Tremelin | 5 The current severe accident management (SAM) includes instructions for using ventilation systems which were not originally intended for venting: this unfiltered release would lead to the emission of large amounts of radioactive products into the environment. The installation of a filtered venting system, allowing to avoid containment over-pressure in case of a severe accident, is depending on the selected strategy for molten corium stabilization as well as the strategy to prevent over-pressure of the containment in case of severe accidents. Analysis and a proposal for a strategy and schedule for implementation of measures for preservation of long-term containment integrity (to stabilize melt and prevent over-pressure) are to be done by 2014. (No. 49) According to the updated NAcP this activity is completed. A deadline is set for the "implementation of measures for maintaining long-term containment integrity according to selected severe accident management strategies" by 2022. (No. 50) Question 5: Does SUJB consider the year 2022 as being an adequate deadline for a measure concerning containment integrity during severe accidents?
669 | Czech Republic |  | Tremelin | 6 ENSREG emphasized the need for additional investigations of the potential for re- criticality of the molten core for the relevant SAM strategies.Question 6: Why does not the Action Plan for Temelin explicitly mention the issue of re-criticality?
670 | Czech Republic |  | Tremelin | 7 The existing hydrogen removal system is designed for design basis accidents (DBAs) only. The installation of additional hydrogen re-combiners for severe accident conditions is planned for 2014 (Unit 1) and 2015 (Unit 2). According to the updated NAcP the project is in progress (No. 47).Question 7: Is the implementation of PARs also planned in the area of the spent fuel pools?
671 | Czech Republic |  | Tremelin | 8 The verification of the correctness of assumptions about the functioning of the severe SAM equipment during beyond design conditions and external risks, including possible measures to ensure functionality according to severe accident management guidelines (SAMGs), is to be completed by 2014. (No. 51) According to the updated NAcP this activity has been completed.Question 8: What results have been achieved? Have been all assumption verified?
672 | Czech Republic |  | Tremelin | 9 Sufficient number of personnel available during for multi-unit accidents is to be ensured by 2013. (No. 41 ) According to the updated NAcP this activity has been completed.Question 9: What was the result? Is it necessary to increase the number of personnel?
673 | France |  |  | 1 ASN requested EDF to conduct a more in-depth seismic margin assessment (SMA), which was performed during the stress tests in a simplified manner. The review of the equipment likely to suffer cliff-edge effects, and the initiating of the necessary corrective measures is to be done until mid-2014. (FLE-3) According to the updated NAcP EDF submitted the first elements of this assessment in mid-2014. Question 1: Which safety important Structures, Systems and Components (SSCs) proved to have small safety margin? Which corrective measures are proposed by EDF and which additional correction measures are required by ASN?
674 | France |  |  | 2 A study evaluating the resistance to an earthquake of fire-fighting systems (fire detection and fixed extinguishing systems) and a program of necessary modification was to be done by 30/12/2012 (ECS-12). According to the updated NAcP this measure is completed. EDF has submitted the required studies and proposed a program of modifications aiming to ensure the seismic resistance of its facilities at these increased levels. These modifications will be carried out during the periodic safety reviews of the reactors concerned. Question 2: Which modifications are proposed by EDF and which additional modifications are required by ASN?
675 | France |  |  | 3 Earthquake induced flooding represents a hazard for Fessenheim: The seismic robustness of the Grand Canal d'Alsace embankments and other structures designed to protect the NPP against flooding and the possible consequences of a failure of these structures were to be analyzed by 31/12/2013. (ECS - 11) According to the updated NAcP EDF submitted the synthesis of its studies at the end of 2013. The studies necessitated additional analyses. ASN has tasked IRSN, its technical support organization to evaluate the robustness of the embankments and other protective structures against earthquakes including more specifically surveys of the in situ structures. The conclusions should be available at the end of the first quarter of 2015. Question 3: What are the results of the IRSN analyses? How does IRSN assess the robustness of the embankments and other protective structures against earthquakes? In the opinion of ASN, is the seismic robustness sufficient? What could be the result of a possible earthquake induced flooding event for Fessenheim?
676 | France |  |  | 4 ASN asked EDF to propose a hardened safety core ("noyau dur" (ND)) of robust material and organizational measures designed in response to the extreme situations studied in the stress tests, by 30/06/2012. The hardened safety core includes systems that are independent and diversified with respect to the existing systems in order to limit common mode risks. The systems, structures and components (SSCs) shall be protected against on-site and external hazards. (ECS - 1). According to the updated NAcP a specific meeting of the Advisory Committee of Experts for nuclear reactors (GPR) was scheduled for 13 December 2012 to decide on the objectives associated with the hardened safety core. The GPR concluded on the need to supplement the functional perimeter of the hardened safety core and to detail the design hypotheses, particularly with regard to earthquakes. On this basis ASN has issued complementary prescriptions through a set of resolutions dated 21 January 2014. On 30 June 2014, EDF submitted the list of new and existing equipment items intended to form part of the hardened safety core, the general hypotheses for the design, construction, verification, qualification and testing of these new or existing equipment items, the seismic levels for each site in response to ASN's demand of 21 January 2014. These files will be examined by the GRP in the first half of 2015. Question 4: The time schedule for the definition of the ND was postponed. Does ASN expect further delays? What is the main reason for the delays in the opinion of the ASN? What will be the earliest and what the latest year of implementation of the ND in the opinion of the ASN?
677 | France |  |  | 5 None of the French reactors is equipped with an alternative ultimate heat sink, but recent events highlighted the vulnerability of the ultimate heat sinks (UHS).[1] An overall review of the design of the heat sink was to be submitted before the 30 June 2012. According to the updated NAcP EDF has submitted these studies.[2] EDF has proposed several changes which improve the monitoring of heat sinks and their protection against external hazards. ASN nevertheless considers that further improvements are necessary, particularly in the identification of hazards and their combinations, in the requirements applicable to equipment for dealing with a massive influx of clogging debris, in the operational control documents and maintenance programmes, and in the monitoring of functions important for safety in the pumping station. (In addition, in the long term, as part of the implementation of a hardened safety core, EDF will build an alternate heat sink, based on either artesian wells or existing tanks, whose seismic behaviour will be verified for earthquakes beyond the initial design­basis of the facilities (hardened safety core level earthquake).) Question 5: Which time schedule is set for the remedy of the identified weaknesses?
678 | France |  |  | 6 EDF presented the planned modifications for installing technical backup devices for long-term heat removal from the reactor and the spent fuel pool in the event of loss of UHS (emergency water supply resources). These devices must meet the requirements on the hardened safety core. No schedule for implementation was set. According to the updated NAcP a report on the modifications has been submitted for all sites and ASN is currently reviewing it? (ECS- 16I) Question 6: What are the results of ASN's review? Until when will the modifications have to be installed?
679 | France |  |  | 7 The fuel building[3] is not designed to contain steam generated by the boiling of the water of the spent fuel pools (SFP) during events with a pressure increase. The thermohydraulic development of a pool accident, i.e. a study of behaviour of the fuel and the water in the SFP under loss of cooling and loss of water situations (in particular the radiological ambient atmosphere, along with the hydrogen concentrations) including measures to be taken was to be performed by 31/12/2012. (ECS - 24) According to the updated NAcP the studies submitted describe the kinetics and consequences of the boiling crisis phenomenon in the pool. The proposed mitigation measures consist of restoring the water inventory in the pools through water makeup which forms part of the hardened safety core. These measures shall be examined at the G PR meeting planned for June 2015. Question 7: Which time schedule will be set for the implementation of these measures?
680 | France |  |  | 8 The mobile equipment necessary for emergency management was not managed satisfactorily yet; the storage conditions did not guarantee permanent availability, particularly in the event of external hazards. The adequate storage of these mobile devices is to be completed by 30 June 2013. (ECS-30)According to the updated NAcP this measure, implemented by EDF is investigated as part of the ASN inspections. Question: What are the results of these inspections by ASN?
681 | France |  |  | 9 A detailed study of the possible improvements to the venting-filtration system, taking into account the existing deficiencies (resistance to hazards, limitation of hydrogen combustion risks, efficiency of filtration in the case of simultaneous use on two reactors, improved filtration of fission products, in particular iodines, radiological consequences of opening the device for the site and the control room) is to be performed by 31 December 2013. (ECS-29) According to the updated NAcP the studies were submitted. EDF was also to submit the study of a solution enabling the U5 filter by end 2014 (container venting-filtration system) not to be used in a severe accident situation. ASN will give a ruling after analysing these two studies. Question 9: Which deadline will be set for the necessary back-fitting measures?
682 | France |  |  | 10 A feasibility study for the installation or renovation of a geotechnical containment or equivalent technical measure to prevent the transfer of radioactive contamination to groundwater in the event of a severe accident leading to corium melt-through of the vessel was to be performed by 31 December 2012. (ECS -27-1) According to the updated NAcP EDF concluded that a geotechnical containment at an economically acceptable cost is not feasible. ASN is currently reviewing this file. Question 10: What is the result of the ASN review?
683 | Germany |  |  | 1 The last re-evaluation of the seismic hazard at the Gundremmingen NPP site took place twenty years ago (in 1993) and is completely outdated. The margins as well as the cliff edge effects for seismic events have not been determined. Nevertheless, the specific NAcP does not require any analysis concerning earthquake resistance of Gundremmingen B/C.Question 1: When did the most recent re-evaluation of the seismic hazard for the Gundremmingen NPP site take place and what are the outcomes?
684 | Germany |  |  | 2 According to the evaluation during the stress tests, the water level of the calculated design basis flood (DBF) is 33 centimeters higher than the grade elevation of the Gundremmingen NPP site. The NAcP requires the flood protection of German NPPs to fulfil at least Level 1 of the criteria specified in the RSK safety review[1]. However, according to RSK 2011, this was not the case for Gundremmingen B/C. The specific NAcP for Gundremmingen NPP asked for the review and improvement of flood protection by 2012 (No 9; N-15).According to the updated NAcP this action was completed. Recent studies have shown that the site will not be flooded in case of design basis flood (this is at least our interpretation of "discharge amount from the postulated underlying the construction"). The safety margins until the design flooding levels are reached are greater than originally assumed. Notwithstanding, provisions have been made for the temporary installation of mobile sheet pile walls to improve the accessibility of those access doors for which structural flooding protection (staircases) has been built within the buildings.Question 2: What are the exact differences between the assumption for the new and the previous evaluation of the water level of the design basis flood? Who has performed this new evaluation? Has the nuclear authority reviewed the new flooding study?
685 | Germany |  |  | 3 The NAcP requires "ensuring the vital safety functions in case of beyond design basis external or internal hazards, a systematic analysis should be conducted."However, the site specific NAcP for the Gundremmingen NPP requires "Obtaining boats to improve accessibility of the plant grounds in a flood." (No 8; N-13, N-15) According to the updated NAcP this action is done. Three boats for conveyance of passengers have been obtained.Question 3: Was the required systematic analysis conducted? Which results were obtained?
686 | Germany |  |  | 4 The peer review team recommended considering the assessment of margins with respect to extreme weather conditions. Because RSK has not completed its studies and discussions on this topic, Germany has not included specific requirements regarding extreme weather conditions in the original NAcP. However the updated NAcP includes the following new requirement:"Assessment of the coverage of extreme weather conditions by the existing design with regard to whether it is possible that additional measures can make a contribution to further risk prevention that is not merely slight." (No. 14, N-24).According to the updated NAcP this action has been completed. However no information beyond mentioning that review was carried out was provided.Question 4: What are the results of this review? Has the nuclear authority already finished reviewing the operator s report? Which measures has the operator suggested? Which additional measures has the nuclear authority required?
687 | Germany |  |  | 5 In case of a total station black-out (SBO) and loss of ultimate heat sink (UHS), accident management (AM) measures have to ensure decay heat removal from the spent fuel pool. Because the spent fuel pools are located outside the containment in the upper part of the reactor building, the injection of water is quite difficult. The evaporation losses of water can be made up by mobile pump(s) only. Therefore a permanently installed injection path into the spent fuel pool from outside the reactor building was to be installed in 2013. (No 6; N-8, N-22)According to the NAcP the measure is still in progress (New deadline: April 2015). The report mentioned that an injection path is permanently installed so that there is no need to enter any rooms that are at risk.Question 5: Why is this measure still in progress? What is lacking and what exactly will be the procedure in the mean time, and is this acceptable?
688 | Germany |  |  | 6 The demonstration of spent fuel pools integrity for the temperature rising to 100 °C was to be finalized by 2013 (No. 12, N-22). According to the updated NAcP this activity has been completed: Compliance with the protection goals "Spent fuel pool cooling through evaporation and make-up feeding of water in beyond-design-basis events" has been demonstrated. Question 6: Does the nuclear authority evaluate the operator s report?
689 | Germany |  |  | 7 The introduction of new/improved accident management measures[2] was required by 2013 (No 5; N-8, N-18, N-19).Among others purposes this action intends to gain an additional option of being ableto use fire engines as mobile pumps for reactor pressure vessel (RPV) injection. According to NAcP this action is done.Question 7: Which new accident measures have been introduced? Which accident measures have been improved?
690 | Germany |  |  | 8 A systematic review of the robustness of emergency measures with consideration of external hazards was scheduled for completion by the end of 2013 (No. 2; N-5, N-6, N-9, N-16).According to the updated NAcP the activity has been completed - a report has been prepared.Question 8: Which results does the mentioned report cover? Which measures has the operator proposed? Which additional measures has the nuclear authority required?
691 | Germany |  |  | 9 The German NAcP also required reviewing the performance of the filtered venting system under severe accident conditions (e.g. long lasting SBO). According to the updated NAcP, this review is not required for Gundremmmingen B/C without any explanation given.Question 9: Why is the activity "review of the performance of the filtered venting system" lacking in the NAcP for Gundremmingen?
692 | Germany |  |  | 10 After having visited the Gundremmingen NPP, the ENSREG fact-finding team voiced concerns about the scope of back-fitting measures: A challenge may exist in implementing improvement measures for plants with (legally) limited operational time. For complex measures requiring long lead times for analysis and implementation, a plant might be closing on its scheduled shutdown at the time an improvement measure would finally be in place. Regardless of this circumstance, nuclear safety is an overriding priority and has to be maintained at a high level until the end of the operation time [ENSREG GE 2012].Question 10: What were the specific reason/issues for this statement of the fact finding team? How does the nuclear authority respond to this concern? Has the scope of back-fitting measures been extended? Were differences between the requirements resulting of the site specific action plan for Gundremmingen B or C taking the different operation time into account?
693 | Germany |  |  | 11 The regulatory body in Germany is composed of authorities of the Federal Government (Federal Ministry for the Environment, Nature Conservation and Nuclear Safety (BMU)) and authorities of the Länder governments. Licensing and supervision, inspection and enforcement as well as plant specific safety assessments and reviews of nuclear power plants are executed by the Länder. The national regulator BMU sets up the NAcP, but the Länder define the plant specific actions. This double layered system takes time and results in insecurities concerning competencies. Question 11: Does the BMU evaluate the site specific action plans? Does the BMU evaluate specific safety aspects? What is the role of the BMU in the context of the NAcP?
694 | Slovak Republic |  |  | 1 Resistance against earthquakes: A value of the peak ground acceleration (PGA) of 0.1 g was used during plant construction. During a reassessment in 2003, the value was increased to 0.143 g. ÚJD SR decision No. 100/2011 ordered the implement seismic resistance to a new value of 0.15 g by December 31, 2018.The ENSREG peer review team recommended considering prioritization of the seismic upgrading measures. The NAcP includes this recommendation: The seismic reinforcement of structures with the highest priority is planned to be finished by 31/12/2015. (ID 6)According to the updated NAcP priorities of the tasks defined. The Priority 1 (highest) includes buildings where equipment important for long-term residual heat removal after a seismic event is situated: Fire station, access point for external power supply, pipeline of emergency SG feed, emergency response centre, etc. Other systems, structure and components (SSCs) will be seismically reinforced up to 2018. Question 1: Is the reinforcement project being implemented according to the time schedule?
695 | Slovak Republic |  |  | 2 However, no analysis of the resilience of this equipment under beyond design earthquake conditions is available yet. Therefore cliff edge effects cannot be excluded. The NAcP requires analyzing seismic margins of selected SSCs by 31/12/2013. (ID 5) According to the NAcP the measure is completed: Seismic margins of civil structures evaluated.Question 2: Which results have the seismic margins analyzes delivered? Which back-fitting measures are necessary and which time schedule is set for their implementation?
696 | Slovak Republic |  |  | 3 Question 3: How does UJD SR assess the reliability of the current seismic hazard assessment? Are there any open questions regarding seismic hazard assessment and fault investigations?
697 | Slovak Republic |  |  | 4 The protection against the design basic flood (DBF) of Mochovce 1/2 is adequate mainly due to the relatively high difference in altitude between the site and the closest rivers. However, an assessment of the safety margins against extreme flooding events was required; places where water accumulates were to be identified. Immediate implementation of temporary solutions and the proposal of a final solution were scheduled to be finished by 31/12/2013 (ID 12).According to the updated NAcP the measure is completed. New metrological studies for the site were developed. Immediate measures (flood protection bags) were implemented. In December 2013 a draft time schedule of implementation of measures for 2014 - 2018 to enhance the resistance of selected civil structures was prepared, and an overall assessment of impacts of extreme meteorological events on safety and reliability of civil structures, including margins to withstand these events was prepared. Question 4: Which measures to enhance the safety margin against flooding events has the operator proposed and which additional measure has UJD SR required?
698 | Slovak Republic |  |  | 5 Concerning extreme weather events, precise quantitative specification of the cliff-edge effects was not available. Evaluation is required of the resistance of selected SSCs against extreme weather events (floods caused by heavy rain, high and low external temperatures, direct wind and other relevant events) on the basis of updated new studies on meteorological conditions, and to consider events with intensity corresponding to the probability of occurrence once per 10,000 years or less. The plan for implementing these measures was to be prepared by 31/12/2013 (ID 4). According to updated NAcP the measure has been completed. As mentioned above new metrological studies for the site were developed and in December 2013 a draft time schedule of implementation of measures for 2014 - 2018 to enhance the resistance of selected civil structures was prepared.Question 5: Which measures are envisaged? Why is the deadline for the implementation not early as 2018? Which measures has the operator proposed and which additional measure has UJD SR required?
699 | Slovak Republic |  |  | 6 The emergency power sources are to be diversified by deploying mobile diesel generators (DG) that can also charge the accumulator batteries; to be finished by 31/12/2013 (ID 20). According to the updated NAcP the measure is completed. Mobile DG (0.4 kV) with connecting cabling were purchased in 2012. In 2013, mobile rectifiers to charge accumulators from this DG were supplied. Question 6: Is the operability of the mobile DGs assured also under severe accident conditions?
700 | Slovak Republic |  |  | 7 Alternative cooling and heat sink: To analyse and if needed to ensure means for cooling water make up from in-site and off-site water sources in the case of lack of cooling water, including preparation of respective procedures by 31/12/2013. (ID 18) According to the updated NAcP necessary equipment has been analysed and purchased for example: portable pumps, portable switchboards. Training programmes for the diverse mobile devices for cooling water make up from in-site and off-site water sources were prepared and tested during emergency exercises.Question 7: How does UJD SR assess the reliability of the measure concerning alternate cooling and heat sink? Does the operator consider installing an independent diversified alternate ultimate heat sink (UHS)? Does the nuclear authority consider requiring the installation of an independent alternate UHS?
701 | Slovak Republic |  |  | 8 The SAM project being currently implemented is based on originally defined scope with assumptions for occurrence of a severe accident on only one of two units. The analysis and the modification of the SAM project from the viewpoint of severe accidentmanagement at both units are necessary. The plan of implementation of additional measures shall be prepared by 31/12/2014 (ID 39; ID 44)According to the updated NAcP the measure is completed. NAcP states that the analysis of severe accident management at all units on the site (including reactors at full power reactors in shutdown and spent fuel pool) has been prepared (Report No. CVV12/2014-01 "Management of Severe Accidents on All Units on Site"). The licensee performed a self-assessment on the implementation of severe accident management. A plan of implementation of additional measures is under preparation. The analyses has been completed and at present evaluated by the licensee. The plan of implementation of measures is dependent on the evaluation of the analyses results. Question 8: When are the analyses expected to be completed? Why is the measure announced to be "completed", despite the fact it is not completed. Why are the measures delayed? Which time schedule for implementation of measures is envisaged?
702 | Slovak Republic |  |  | 9 The NAcP requires analysing the need for filtered containment venting and other potential technical measures for long-term heat removal from the containment by 31/12/2015 (ID 2). According to the updated NAcP, the project is in the phase of elaboration with the contractor VUJE. Finishing of the project expected by the defined deadline.Question 9: Is there a tendency in favor or against the implementation of a filtered venting system?
703 | Slovak Republic |  |  | 10 Instrumentation and monitoring: To analyse the availability of important parameters, and if needed, to ensure mobile measuring units which can use stable sensors also without standard power supply by 31/12/2015.According to the updated NAcP the technical specification and procurement of the mobile measuring unit in progress. (e. g. equipment for measuring of temperature and pressure in the primary circuit and water level in the SG).Question 10: What are the technical specification of these mobile units regarding earthquake resistance and duration of long-lasting events?
704 | Slovak Republic |  |  | 11 The conditions of the environment of rooms with safety relevant equipment during long-term station blackout (SBO), loss of ultimate heat sink (UHS) and severe accidents were to be analyzed. The plan of the required measures was to be prepared by 31/12/2013 (ID 25). According to the updated NAcP, the measure is completed. The impact of extreme external climate conditions in selected rooms was analyzed. A plan on the implementation of some additional measures resulting from the analyses was prepared.Question 11: What is the time schedule for the necessary back-fitting measures?
705 | Slovak Republic |  |  | 12 The leak-tightness of all penetrations through the containment under severe accident conditions (in particular leak-tightness of seals) have to be verified. Another task wasto analyze the SAM project from the viewpoint of resistance of seals and penetrations of the containment under severe accident conditions by 31/12/2015 (ID 54).According to the updated NAcP the project is completed. A study was prepared by UJV Řež to test the sealing under SA conditions. Replacement of seals at the reactor pressure vessel cavity lids and doors is in progress.Question 12: When will the replacement of seals at the reactor pressure vessel cavity lids and doors be finished?
706 | Slovak Republic |  |  | 13 To analyze the SAM project from the viewpoint of potential migration of hydrogen to other places by 31/12/2015 (ID) According to the updated NAcP, the project is in the phase of elaboration with the contractor UJV Řež. Preparation of the initial study which will be followed by other investigations in progress. Partial project outputs can be expected at the beginning of 2015.Question 13: Will there be the need for the installation of additional PARs or other measures?
707 | Slovak Republic |  |  | 14 One of the most important modifications concerning the prevention of major radioactive releases during accidents is the external cooling of the reactor pressure vessel (RPV). This so-called in-vessel retention (IVR) concept aims to ensure the integrity of the RPV during a severe accident. Until now proof that this concept fulfils all the intended functions was delivered only with limited experimental analyses. Therefore the peer review team recommended considering a failure of the reactor pressure vessel (RPV), despite the fact this is claimed to be very unlikely. However, the evaluation of the consequences of RPV failure is not included in the NAcP.Question 14: Why did UJD not follow the recommendation of the peer review team to consider a RPV failure?
708 | Slovenia |  |  | 1 The Krško NPP is located in a seismically active region. The national stress tests report refers to several active faults which were identified in the immediate region of Krško. In line with US NRC nuclear regulation and standards the peak ground acceleration (PGA) of 0.3 g was used for the safe shutdown earthquake (SSE). Seismic hazard assessments in 1994 and 2004 led to raising the PGA values for the SSE: In 1994 to PGA= 0.42g and in 2004 to a PGA= 0.56g, which is nearly twice the original PGA. Question 1: Has a new seismic hazard assessment been conducted? Does SNSA have knowledge of any investigation which indicates that ground motion acceleration higher than 0.6 g is possible? Are any new seismic hazard assessment envisaged by SNSA? Are all the assumptions and results of the previous PSHA also today justified in the opinion of SNSA?
709 | Slovenia |  |  | 2 Today Krško NPP complies only with the current requirements for the original design basis of 0.3g. But the additional systems, structures and components (SSCs) which will be implemented within the SUP (Safety Upgrade Project), will be designed and structured in accordance with the design extension conditions (DEC) requirements specific for the Krško NPP design and site location. However the extended design condition seismic value is 0.6 g PGA. This value offers nearly no seismic safety margin (0.04g) regarding the current value of the SSE.Question 2: Why do the design extension conditions (DEC) requirements obtain so little seismic margins? Are there any new requirements in the pipeline?
710 | Slovenia |  |  | 3 SNSA claims that in case of an earthquake with a PGA over 0.6 g, core cooling can be assured by alternative means, but pointed out that implementation of alternative means requires that manual actions are performed in relatively short time.Question 3: Is SNSA convinced that it is possible to prevent a core melt accident with alternative means after an earthquake with a PGA over 0.6g taking into account the destruction of the NPP and the infrastructure? What is this conviction based upon?
711 | Slovenia |  |  | 4 An earthquake with a PGA in the range of 0.8 g or higher would be likely to cause core damage. Mechanical damage could disturb the reactor core geometry and thus the insertion of the control rods. Radioactive releases cannot be excluded. A recurrence period of 50,000 years was estimated for seismic events with a PGA of 0.8 g. Question 4: What are the uncertainties in the calculated recurrence period of 50,000 years for the seismic events with a PGA of 0.8 g?
712 | Slovenia |  |  | 5 The plant is located in an area prone to flooding. The average altitude of the surrounding area is about 154.5 meters above sea level. The plant itself is located at155.20 m on a plain, which is 0.69 m below the water level of the probable maximum flood (155.89 m). Thus, flood protection has to be assured by dikes around the site. Increasing the dike height upstream from the plant is in progress. The improved flood protection dikes are designed with very limited safety margins against extreme flooding or earthquake events.Question 5: Which safety margins are attributed to the new flood protectionsdike against natural hazards (earthquake and flooding) with a return frequency of 10,000 per year? When will the reinforcement project of the dyke be completed?
713 | Slovenia |  |  | 6 The flood protection of the nuclear island and the bunkered building are to be enhanced by 2015.According to the updated NAcP this measure is still in progress.Question 6: What is the current status of the flood protection upgrade?
714 | Slovenia |  |  | 7 SNSA plans to include in its legislation requirements regarding both the use of advanced deteriorating weather warning systems and the use of seismic monitoring systems by 2014. (No. 2.1). According to the updated NAcP the activity is in progress. The SNSA is in the process of amending / revising its legislation based on the above stated commitments and/or considerations. The drafts of the amendments have already been prepared, which also consist of the last WENRA Reference Level updates (adopted in September 2014). Final internal revisions are needed before the amended rules can be submitted to public hearing and then to the Government for approval. The new deadline for adopting the revised legislation is the end of 2015. Question 7: Which time schedule will be set for the implementation of the necessary back-fitting measures after the legislation requirements were issued?
715 | Slovenia |  |  | 8 To prevent total station-black out (SBO), the SUP includes a comprehensive safety upgrade of AC power to be acquired by 2015 (SUP, 1.1). Regarding DC power supplies, the plant has in place several mobile diesel generators for recharging the batteries; improvement for the connection between diesel generators and charging buses is planned, as well as installation of additional train of batteries.According to the updated NAcP the action is in progress. However the finalisation is postponed until 2018. In September 2013 the Krško NPP applied for the extension of the final SUP deadline. The main reasons for the delay were the size of the project, complexity of design documentation, delivery times of some of the main components, as well as inclusion of the Krško NPP into the Public Procurement in Water Management, Energy, Transport and Postal Services Area Act, which further complicated, delayed, and finally failed the bidding of the project. The SNSA approved the extension of the deadline until the end of 2018.Question 8: Is the safety upgrade project (SUP) proceeding in accordance with the postponed time schedule?
716 | Slovenia |  |  | 9 To prevent the loss of ultimate heat sink (UHS), an alternate UHS need be installed by 2015. The alternate UHS is to be seismically qualified and independent from the ultimate heat sink (Sava River). (SUP, No 1.3).To assure core cooling in case of SBO and/or UHS, the installation of additional high pressure pump for feeding steam generators (SGs) installed in the separated bunkered building with dedicated source of water is scheduled by 2015 (SUP, No. 1.2) . Furthermore additional pumps (low and high pressure, as well as a special pump for seal injection[1]) are to be implemented by 2015 (SUP, No. 1.4). The pumps will beinstalled in the separated bunkered building with a dedicated source of water for 8 hours and with provisions to refill with the help of mobile equipment from different water sources.According to the updated NAcP these activities are in progress. However the finalisation is postponed "after 2018". In the beginning of 2014 the Krško NPP notified the SNSA that the implementation of the SUP until the end of 2018 is going to be challenged due to financial constraints. Namely, the two owners of the Krško NPP (the Slovenia's state owned GEN Energija d.o.o. and the Croatia's stated owned HEP d.d.) became unwilling to finance the SUP due to doubts that the plant could, after the implementation of the project, still continue to provide electricity at a competitive price. The owners ordered a financial viability study, after which they will decide about the continuation of the "BB2 project"Question 9: When will the financial viability study be completed? When is the decision about the implementation of this measure expected to be taken? What is the consequence for the safety, if the BB2 project will be cancelled? How will SNSA react to the BB2 project being abandoned?
717 | Slovenia |  |  | 10 To assure containment integrity during a severe accident, the safety upgrades program (SUP) includes the implementation of containment filtered venting systems and passive auto-catalytic re-combiners (PARs) to avoid hydrogen explosion (SUP, No. 1.5). According to the updated NAcP these activities are completed.Question 10: What is the size of seismic margins of the filtered venting systems and the PARs?
718 | Slovenia |  |  | 11 The installation of a fixed spray system around the spent fuel pool with provisions for quick connection from different sources of water (deadline 2015, SUP, No. 1.7). According to the updated NAcP the activity is in progress. However, the action is postponed to 2016.Question 11: Is the implementation of the necessary back-fitting in accordance to the postponed deadline?
719 | Slovenia |  |  | 12 Mobile heat exchanger with provisions to quickly connect to SFP containment sump or reactor coolant system are to be provided by 2015, (SUP No. 1.8).According to the updated NAcP the activity is in progress. However, the action is postponed to 2018.Question 12: Is the implementation of the necessary back-fitting in accordance to the postponed deadline?
720 | Slovenia |  |  | 13 A new emergency control room (including expansion of existing remote shutdown panels) in the above mentioned separate bunkered building is to be installed by 2016. (SUP, No. 1.6)According to the updated NAcP this activity is in progress. However, the action is postponed to 2018.Question 13: Is the implementation of the necessary back-fitting in accordance to the postponed deadline?
721 | Spain |  |  | 1 The CNS requires re-analysing the seismic hazard at each NPP site in Spain. As suggested by the ENSREG peer review team the analysis needs to consider geological and paleo-seismological data characterizing relevant active faults of the Iberian Peninsula. The CSN required the licensees to submit the new assessments by 2016 (S1) . According to the updated NAcP the issuing of a new ITC (foreseen in 2013) by the CSN is postponed to the first quarter of 2015. A new schedule for the seismic hazard assessment has not been announced yet.Question 1: Which time schedule has been set to finalize the new seismic hazard assessment and complete the CSN review?
722 | Spain |  |  | 2 The Spanish licensees have analysed possible secondary effects of earthquakes during the stress tests (31/12/2012). Significant improvements have been identified and scheduled for implementation by 31/12/2014 (A1and A2).One of the EC staff working document's recommendations is not mentioned in the Spanish NAcP: "Within the framework of the on-going analyses on the effects of pipe rupture (non-seismic and seismic), it is suggested to consider in particular verifying that there are no common cause failure issues."According to the updated NAcP the implementation of improvements (regarding internal flooding due to the circumferential rupturing of non Seismic Class piping, and water containers rupturing with major fluid releases) is completed.Question 2: Which severity of an earthquake was assumed to assess the expected secondary earthquake effects? The EC staff working document recommended evaluating common cause failures - has this been undertaken?
723 | Spain |  |  | 3 The site is located on the left bank of the Arrocampo brook reservoir; the Valdecañas dam is situated upstream (storage capacity 1146 hm3). The dam break analysis was re­assessed to check against the dam emergency plans and to resolve the identified inconsistencies. The analysis was completed by 31/12/2012 (A3).According to the updated NAcP, this activity is listed as completed despite the fact that "certain specific cases pending. " It is mentioned that the revision and acceptance by the CSN of the analyses of dam rupture scenarios have undergone something of a delay due to the existing uncertainties, these having emerged during the review being performed by the CSN.Question 3: Please name the mentioned "existing uncertainties." When is the completion of the review due? Are some interim results available?
724 | Spain |  |  | 4 The necessary improvement of external flood protection of buildings containing safety related systems, structures and components (SSCs) was implemented in 2012(I2) According to the updated NAcP, this measure is completed.Question 4: Does the external flooding protection include protection against a possible dam break scenario?
725 | Spain |  |  | 5 Studies of the site accessibility in the event of extreme natural events (including possible proposals for improvement) were to be performed by (31/12/12, A6)According to the updated NAcP, the analyses have been completed and resulted in incorporating improvements at several plants.Question 5: Has CSN completed reviewing this measure? If new results of the natural hazards assessment were found, would they be followed up with new studies?
726 | Spain |  |  | 6 Adopting a consistent approach for the return periods associated to heavy rain and extreme temperature scenarios at individual sites is planned in line with the ENSREG Peer Review team (S2) suggestion. In this context, the new WENRA Reference Levels for external events should have been implemented in the Spanish regulation in 2014. According to the updated NAcP the implementation of the WENRA RL is pending. Question 6: What time schedule is envisaged for the assessment of heavy rain scenarios (i.e. implementation of WENRA Reference Level into the Spanish regulation, review of the operator s studies, and implementation of measures)?
727 | Spain |  |  | 7 The impact of potential combinations of natural external events credible at the site was to be identified by 31/12/12 (A4).According to the updated NAcP the analyses of potential combinations of natural external events have been completed without significant aspects for the implementation of improvements having been identified.Question 7: Please list the combinations of natural external events which were assumed to assess each individual NPP site s ability to withstand.
728 | Spain |  |  | 8 If the ultimate heat sink fails, the only possibility to cool the core is via the steam generators (SGs). This measure cannot be used in shut down operation modes.However, there are no plans to implement an alternate ultimate heat sink.Question 8: Why does CSN not require an alternate heat sink?
729 | Spain |  |  | 9 New equipment (fixed or mobile) to cope with prolonged station black-out (SBO) was to be implemented (31/12/2014, I4).According to the updated NAcP the implementation is completed.Question 9: Which kind of new equipment (fixed or mobile) has been installed?
730 | Spain |  |  | 10 The feasibility of the manual actions required in a situation of total loss of electric supply (including batteries) was to be demonstrated. (31/12/2012, I5).According to the updated NAcP this measure is completed despite the fact that "certain specific cases pending".Question 10: Which manual actions are required in a situation of total loss of electric supply (including batteries)? Which "certain specific cases" are pending?
731 | Spain |  |  | 11 Possible improvements to reinforce the existing capacities of de-pressurizing the primary system and avoid possible high pressure core damage sequences were to be analysed (30/06/2013, I16).According to the updated NAcP the measure is completed. However evaluation by CSN is ongoing, further details are not mentioned. .Questions 11: Are improvements to avoid possible high pressure core damage sequences considered necessary? Are improvements envisaged (if yes, in which time schedule; if not, why not)?
732 | Spain |  |  | 12 Analysis of critical instrumentation required for accident management, and guarantee of its operability under SBO and severe accident conditions (31/12/12, I17).According to the updated NAcP, evaluation by CSN is ongoing. A number of difficulties has been encountered due to scarce international experience.Question 12: What is the current status of the evaluation by CSN? When will the evaluation be finished? Is the implementation of new instrumentation considered necessary?
733 | Spain |  |  | 13 Containment integrity during severe accident is not assured yet: A dangerously weak point is the lack of a filtered containment venting system to prevent containment overpressure; implementation is planned until 31/12/2016(114)According to the updated NAcP implementation will be carried out during the 2016 and 2017 refuelling outages.Question 13: Regarding the potential risks, why is the implementation of filtered venting not accelerated? Has it been considered to stop operation until the implementation of the filtered venting system will have been completed?
734 | Spain |  |  | 14 No adequate measures to manage the large amount of hydrogen expected to accumulate in the case of a severe accident in the containment are installed yet; they are necessary to prevent explosions. The installation of passive autocatalytic re-combiners (PARs) should be finished by 31/12/2016. (I15).According to the updated NAcP the work is on-going.Question 14: Taking the potential risks into consideration, why is the implementation of PARs not being accelerated? Were considerations made to stop operation until the implementation of the PARs will have been completed?
735 | Spain |  |  | 15 Potential hydrogen hazard in other buildings surrounding the containment should be analysed by 31/12/2013 (A7).According to the updated NAcP the activity is completed. The licensees have carried out the studies requested. The CSN is currently evaluating these analyses. No information was provided on the completion of the evaluation or whether back-fitting will be necessary.Question 15: Did the licensee suggest back-fitting measures? What is the result of CSN evaluation?
736 | Spain |  |  | 16 The possible consequences of containment flooding strategies for equipment (instrumentation) located inside containment were to be analysed by 31/12/2012 (A8). According to the updated NAcP the analyses have been completed and meant the incorporation of improvements at some plants. However, the evaluation by CSN is ongoing.Question 16: What is the result of CSN's evaluation so far?
737 | Spain |  |  | 17 Analysis of possible improvements to be implemented in relation to severe accidents that might develop from an initial shutdown situation were to be performed by 31/12/14 (A9). According to the updated NAcP the analysis is on-going. It is stated that a number of difficulties have been encountered due to the scarcity of international experience (A9). The final implementation of Severe Accident Management Guidelines (SAMG) for accidents initiated during shutdown operation is scheduled for 2016.Question 17: CSN has reviewed the improvement of severe accidents which result from initial shutdown situations - which results are already available?
738 | Spain |  |  | 18 Analysis of additional SFP instrumentation measures, taking into account also the prolonged SBO situation was to be performed by 31/12/12 (I19).According to the updated NAcP the measure is completed. No further details were provided.Question 18: Are additional SFP instrumentation measures already implemented or which time schedule is planned for this measure?
739 | Spain |  |  | 19 Integrate into the Spanish legal framework; the completion was scheduled for December 2013.According to the updated NAcP publication is now foreseen during the first half of 2015 Question 19: Why has the publication been postponed? Will the new deadline be met?
740 | Spain |  |  | 20 Possible improvements of electrical feeds to control room habitability systems for situations of prolonged SBO was to be analysed by 31/06/12. (I20).According to the updated NAcP the analyses have been completed and meant the incorporation of improvements at all the plants.Question 20: Has CSN already finished reviewing the analysis? Are all required improvements implemented already? Why is the implementation of an ECR not required by CSN?
741 | Spain |  |  | 21 Analysis of the suitability of the human resources currently assigned to the ORE (Emergency Response Organisation). Implementation of improvements deriving from the analysis were to be performed by 31/12/13 (I7)According to updated NAcP CSNs assessment is on-going.It also mentioned that within the framework of the review of the plant plans in order to define the composition of the plant Emergency Response Organisations, CSN is addressing the verification of the time margins for the control or mitigation of severe accidents. The ENSREG peer review team recommended verifying the assumptions on which these margins are based on. Thus CSN is performing a detailed review of the analyses submitted by the licensees on September 15th 2012 in relation to their Emergency Response Organisations, in which they were required to explain the time available for each manual action, including the margin with respect to the appearance of cliff-edge situations.Questions 21: The licensees submitted results of Emergency Response Organisation analyses on September 15th 2012 - what did the results show? Does the CSN consider the time margins for undertaking manual actions during severe accidents sufficient?
742 | Sweden |  |  | 1 The original design of the Ringhals units did not take into consideration protection against earthquakes. The Swedish NPPs became subject to general requirements imposed on resilience against earthquakes when the new Swedish regulations entered into force in 2005. The deadline for taking measures was determined to be 2013. Identified deficiencies were for example the spent fuel cooling systems, the roof of the reactor building at Ringhals-1 ; anchors at Ringhals-2, -3 and -4; control room ceiling at Ringhals-3 and -4. The original NAcP mentioned that work is on-going at all units in order to fulfil the regulation regarding design basis earthquake (DBE). The updated NAcP does not report about the status about the reinforcement.Question 1: Have all back-fitting measures to meet the current Swedish regulation concerning protection against design basis earthquake completed?
743 | Sweden |  |  | 2 The NAcP asked for an investigation of seismic margins; an evaluation of structures, systems and components (SSCs) against ground motions exceeding DBE is to be performed by 2015 (T1 .LA.9). According to the updated NAcP the margin analyses are ongoing.Question 2: Are any results of the seismic margins investigations already available?
744 | Sweden |  |  | 3 In April 2012, the ENSREG peer review team recommended to the Swedish Nuclear Authority (SSM) to consider a more timely manner for the implementation of protection against earthquake-induced flooding of for example damaged water storage tanks. The NAcP demands investigations regarding these secondary effects of earthquakes by 2014 (T1.LA.2). According to the updated NAcP this action has been completed by having analysed seismically induced fires. Minor weaknesses have been addressed. However, the NAcP does not provide further details.Question 3: Has SSM finished reviewing the licensee s investigation? Which back-fitting measures have been performed? Does the licensee plan the implementation of additional measures and does SSM require additional back-fitting measures?
745 | Sweden |  |  | 4 The ENSREG peer review revealed that the methodology used for seismic hazard assessment (SHA) is not fully compliant with current international standards and research results. Thus, SSM will start a research project concerning the influence of paleo-seismological data on the existing model regarding frequency and strength of the ground response spectra in 2013 (T1 .RA.1). According to the updated NAcP this measure is completed: A literature search has been initiated.Question 4: In which time frame the research project concerning the influence of paleo-seismological data on the existing model regardingfrequency and strength of the ground response spectra will be completed? Are there any new results so far?
746 | Sweden |  |  | 5 The Ringhals units are located near the sea and thus they can be significantly affected by flood events. Full compliance for protection against external flooding in accordance with the current Swedish requirements (2005) is expected to be reached in 2013. The updated NAcP does not mention whether this measure is completed or not. Question 5: Have all back-fitting measures designed to meet the current Swedish external flooding protection regulation (2005) been completed?
747 | Sweden |  |  | 6 After having visited the Ringhals NPP, the ENSREG fact-finding team concluded: The definition of high sea level for assessment of the margin against flooding remains an open issue because the site platform is at 3 m level, while the high sea level is at 2.65 m, which could be a concern regarding adequacy of the margin. In connection with this issue the team visited the on-site emergency control centre (ECC) and underlined the importance of re-assessing the vulnerability of the ECC [ENSREG SE 2012]. Question 6: How does SSM deal with this conclusion of the ENSREG fact­finding team? How does SSM assess the flooding risk of the Emergency Control Centre (ECC)? Has SSM required the immediate installation of flood protection?
748 | Sweden |  |  | 7 The NAcP requires a flooding margin assessment in line with the initial ENSREG specification for the stress tests of 2014 (T1.LA.6).According to the updated NAcP weaknesses have been addressed and physical measures will be taken at some plants. However the NAcP does not present the measures nor the deadlines.Question 7: Which weaknesses have been identified, and which time schedule for the back-fitting measures are set?
749 | Sweden |  |  | 8 The investigation of extreme sea water levels is necessary. SSM underlined the fact that historically extreme sea water levels in Scandinavia have always been accompanied by very high wind speeds. An analysis of the combined effects of waves and high water including potential dynamic effects is scheduled for completion by 2015 (T1.LA.5) .According to the updated NAcP the work is ongoing.Question 8: Are any results regarding extreme sea water levels in particular the new values already available?
750 | Sweden |  |  | 9 ENSREG recommended to conduct a new evaluation of the flooding protection (volumetric approach)[1] which was scheduled for completion by 2014 (T1.LA.7). According to the updated NAcP this measure has been completed. However the result of this evaluation is not presented. The NAcP only stated that "[bjased on performed stress tests, measures will be performed at some plants. " Neither measures nor time schedule of the implementation are provided.Question 9: Which measures will be performed and which time schedule has SSM determined for the implementation?
751 | Sweden |  |  | 10 A formal assessment of margins for all external hazards (including seismic, flooding and severe weather) plus identification of potential improvements is to be performed by 2015 (T1.LA.9). According to the updated NAcP the work is ongoing.Question 10: Are any results already available?
752 | Sweden |  |  | 11 The current Swedish regulation addresses extreme weather without quantification of the loads. An investigation of plant characteristics in extreme weather conditions is required to be performed by 2015. This investigation will assess plant robustness against extreme weather combined with events such as ice storms and heavy snow load on structures. (T1 .LA.4) According to the updated NAcP the work is ongoing. Question 11: Has the back-fitting of the already identified weaknesses during the stress tests (e.g. vulnerability of the reactor building of Ringhals 1 against tornado and heavy snow load) been completed? Which additional weaknesses regarding the plant robustness against extreme weather were identified? What is the time schedule for the necessary back-fitting measures?
753 | Sweden |  |  | 12 SSM was obliged to initiate a study with the target of a more precise assessment of extreme weather conditions in 2013. (T1 .RA. 1 ) According to the updated NAcP the action is completed. This study has been performed by the Swedish Meteorological and Hydrological Institute (SMHI).Question 12: Are results of the study Swedish Meteorological and Hydrological Institute (SMHI) already used to investigate the protection of the NPPs against extreme weather events?
754 | Sweden |  |  | 13 The improvement of an early warning notification was to be investigated by 2013 (T1.LA.8)According to the updated NAcP the action is completed. The licensees have introduced instructions ordering the control room staff to check the weather forecast once per shift with the Swedish Metrological Institute (SMHI). Discussions are ongoing with SMHI to create a routine where SMHI provides the licensees information directly on weather situations that may pose a threat to a plant.Question 13: Why has this routine not been established already?
755 | Sweden |  |  | 14 To prevent SBO situations, the re-assessment of the AC and DC power supplies and distribution systems is required by 2014 (T2.LA.3; T2.LA.4).According to the updated NAcP this measure is completed. Concerning AC power: All licensees have drafted plans to strengthen the power supply. Concerning DC power: Measures are envisaged to expand the battery capacity of existing battery systems or to apply load shedding or a combination thereof.Question 14: When will the envisaged improvements to strengthen the AC and DC power supplies and distributions be completed?
756 | Sweden |  |  | 15 The integrity of the primary system especially of the primary pumps seal for the PWRs were to be reassessed (T2.LA.5). According to the updated NAcP this measure is completed. For PWR the integrity of the primary system has been further evaluated and reassessed for prolonged extreme situations resulting from natural phenomena and other events. This included reassessment of the primary pumps seals which will be replaced.Question 15: Which primary pumps seals will be replaced and what is the time schedule for this back-fitting measure?
757 | Sweden |  |  | 16 To define the fundamental design principles of an independent core cooling system for water injection into the reactor pressure vessel to cope with SBO was to be completed by 2013 (T3.LA.2).According to the updated NAcP the measure is completed. In a joint project the licensees have developed a" Position Paper" defining the requirements to be adopted. Question 16: Does SSM assess the requirements defined in the "Position Paper" for the fundamental design principles of an independent core cooling system to be sufficient?
758 | Sweden |  |  | 17 SSM decided in December 2014 on the implementation of Independent Core Cooling by 2020. It stated that the need to increase the reliability of core cooling in a nuclear power reactor by introducing an independent function was brought up already when drafting the Swedish Nuclear Power Inspectorate's (SKI) in the early 2000s.Question 17: Why did only the early draft include the requirement for the Independent Core Cooling system?
759 | Sweden |  |  | 18 SSM issued a decision on 15 December 2014 requiring an independent Core Cooling function to be in place by 31 December 2017 for all reactors. These transitional measures do not have to fully meet the design basis for the independent Core Cooling. Furthermore the measures consist mainly of enforcing the emergency power by upgrading the existing gas turbines and purchasing new mobile equipment, with new connection points and new power feed trains. The licensee may choose to apply this transitional solution in part or in its entirety as a component of the final design. The transitional solution may be applied during the remaining period of operation to reactors that the licensees only intend to operate for a limited period of time after 2020. In those cases the licensees have the opportunity to apply for exemptions. Question 18: Why does SSM consider the very limited transitional solution for the independent core cooling function sufficient? Which plants can assume that they will be allowed to operate on the transitional solution only?
760 | Sweden |  |  | 19 The primary ultimate heat sink for all units at Ringhals is sea water.[2] Ringhals-2, -3 and -4 (PWR) have another option to release residual heat to the atmosphere via the steam generators. However, this procedure is dependent on the water sources available for the auxiliary feed water system, and is thus, limited. Ringhals-1 (BWR) has no alternateultimate heat sink at all.Question 19: Have the licensees or SSM considered implementing an alternate ultimate heat sink?
761 | Sweden |  |  | 20 Improving the capability of cooling the spent fuel pools SFP (e. g. installation of permanent pipes for make-up water from a protected location) and their instrumentation is to be considered by 2014 (T3.LA.1 ; T3.LA.3). According to the updated NAcP this measure is completed. The concept of the preliminary studies and analyzes is based on the feed-and-bleed cooling concept of the fuel pools. The necessary instrumentation to monitor temperature and water level in the fuel pools will be installed in connection with the implementation of alternative measure for cooling the fuel in the pools.Question 20: Has SMM completed reviewing the concept for the improvements of the SFP cooling capability? Which results were found?When will the implementation be performed and finished?
762 | Sweden |  |  | 21 The containment filtered venting system is not designed to cope with accident scenarios with the duration and aggravated conditions at the site which have occurred during the Fukushima accident. Therefore, the use of the containment filtered venting system during prolonged severe accident conditions of more than 24 hours is also scheduled for review until 2014 (T3.LA.16).According to the updated NAcP this measure is completed. Investigations and assessments of the ability to manage a severe accident have been performed by the licensees. Different solutions to the case have been suggested.Question 21: How does SSM assess the different suggested solutions regarding the filtered venting system? When will the implementation of the necessary back-fitting measures be finished?
763 | Sweden |  |  | 22 New analyses are necessary to answer questions relating to the long-term management of hydrogen in the containment. Also the possibilities and consequences of hydrogen accumulating in the reactor building were to be investigated by 2014 and suggestions made on necessary instrumentation and management (T3.LA.17). According to the updated NAcP this measure is completed. The licensees performed investigations and assessments of the ability to manage severe accidents. The study concluded that none of the examined phenomena are expected to cause substantial degradation of the containment and increase the emissions. Uncertainties remain for some plants regarding the risks of corrosion and degradation of polymeric materials; research in these areas should be followed.Question 22: How does SSM assess the results of the long-term management of hydrogen study, which the licensees have performed? Does SSM require additional measures in regard of the remaining uncertainties?
764 | Sweden |  |  | 23 The operability and habitability of the Main and Emergency Control Rooms (MCR and ECR) as well as the Emergency Control Centre (ECC) were to be re-assessed by 2013. (T2.LA.6)According to the updated NAcP, this measure is completed. Some weak points have been identified and will be addressed. For example the inner roofs in control rooms have been strengthened to withstand strong earthquakes.Question 23: Which additional measures did the licensee suggest and which additional measures demands SSM? Has a time schedule been drawn up for implementation ?
765 | Sweden |  |  | 24 The risk of criticality and/or re-criticality was to be reassessment of by 2014 and measures to manage re-criticality are to be improved (T2.LA.19; T3.LA.6).According to the updated NAcP these measures are completed. For Ringhals PWRs re-criticality must be considered in the long term. Measures have been identified and addressed. Further information was not provided. The overall probability for re- criticality that endangers the containment integrity is judged to be very low for the BWRs. The review of existing emergency operating procedures with bearing on re- criticality has resulted in updating the the Emergency Operating Procedures (EOP) instructions.Question 24: Which measures are addressed to avoid re-criticality at the Ringhals PWRs? Does SSM consider those measures sufficient? Does SSM require additional measures?
766 | Sweden |  |  | 25 The Swedish strategy for dealing with a BWRs core melt is letting the core debris fall into a large volume of water in the lower regions of the containment. This is a relatively unusual approach and only a few reactors in the world apply this strategy. An extensive national research programme was set up in the 1980s to highlight all important aspects which need to be addressed; this programme is still under way. There are uncertainties connected with the Swedish strategy which need to be addressed. The Swedish strategy could most likely avoid a major initiating interaction between concrete and core melt. However, some open issues have been identified. They are related to steam explosions which could occur when the core melt interacts with the water and the ability to cool the core debris in the containment. The severe accident research is now directed towards providing prove that the uncertainties of the chosen solution are acceptable. Since the governmental decision in the 1980s, the Swedish utilities and the regulator have collaborated to conduct further research on severe accidents and to monitor international research in the area of severe accidents. Question 25: What is the current status of the open issues concerning the Swedish strategy for dealing with SWRs core melts?
767 | Switzerland |  |  | 1 An earthquake exceeding the design basis can possibly occur at the Muehleberg site. The seismic hazard assessment of the PEGASOS project (2004) indicates that the current design maximum PGA of 0.15g for safety significant buildings and systems could be exceeded at a frequency of approx. 6 x 10-4 per year, which is not extremely rare. The resistance against earthquake is not in compliance with the ENSREG recommendation. In order to reduce the uncertainty of the PEGASOS results, the PEGASOS Refinement Project (PRP) was initiated. The re-assessment should define the updated site-specific seismic hazard levels (H3). The PRP project was expected to be completed in 2013 (PP1). According to the updated NAcP, the results of the PEGASOS Refinement Project (PRP) were submitted to ENSI for final review. It is stated that depending on the outcome of the review a renewed seismic safety assessment by the operators may be required.Question 1: What are the outcomes of the PRP? Which site-specific values (PGA) for the seismic hazard (H3) have been evaluated? Will ENSI request a new seismic safety assessment? If so, what will the time schedule for reassessment and the subsequent back-fitting measure look like?
768 | Switzerland |  |  | 2 The PEGASOS Refinement Project (PRP) should define the updated site-specific seismic hazard levels (H3). During the EU Stress Tests the outdated hazard levels H1 and H2 were used to evaluate seismic margins of the SSCs. Nevertheless, the evaluation revealed that only small safety margins exist (e.g. for one safety train for core cooling and spent fuel pool cooling).Question 2: Will ENSI demand a new seismic margin assessment using the updated site-specific seismic hazard level (H3) for all plants?
769 | Switzerland |  |  | 3 The potential failure of the Wohlensee dam located 1 km upstream is a serious seismic hazard for the Muehleberg NPP. The dam is very old and might break in case of a severe earthquake. The dam break will possibly be followed by a clogging of the NPP cooling water intakes, potentially causing the reactor cooling to fail. (PP1)Question 3: According to the updated NAcP, the reinforcement project of the Wohlen Lake dam was finished in 2014. However, the results of the PRP could show the need for a new assessment. Will ENSI demand a new assessment and/or for new reinforcement project? If not, why not and if yes, what would be the time frame?
770 | Switzerland |  |  | 4 Regarding seismic robustness of the containment and primary circuit, ENSI will complete the reviews for all the NPPs by issuing evaluation reports in the course of 2013. Possible further actions will be decided upon in 2013(OP 2-2).Question 4: According to the updated NAcP, ENSI will require a more detailed examination of the seismic robustness of the isolation of the containment and the primary circuit. What is the status of this action? Will the same scope of measures for all NPPs (including Muehleberg NPP) be required by ENSI?
771 | Switzerland |  |  | 5 In 2013, ENSI has set up a working group to investigate the necessity to implement automatic scrams triggered by seismic instrumentation. Once the information including international practice is collected and structured, ENSI will issue an evaluation report. Based on these results a demand for back-fitting could be sent to the licensees, if considered necessary. (OP 2-1). According to the updated NAcP, ENSI is analyzing the advantages and disadvantages of an automatic shutdown of the plants triggered by the seismic instrumentation. Depending on the results of the analysis, upgrades could be initiated.Question 5: When will the decision be made? When could the implementation be finished?
772 | Switzerland |  |  | 6 ENSI will follow up on the impacts of a total debris blockage of hydraulic engineering installations at the Muehleberg NPP. According to the updated NAcP the Muehleberg NPP started a project for reinforcing flooding protection of an additional water intake on the Aare River by building a new pump station on an elevated location in 2014. The implementation is still ongoing.Question 6: When will the implementation be completed?
773 | Switzerland |  |  | 7 In 2012, a project was initiated in Switzerland to develop the scientific data necessary to further redefine the flood hazard assessment. In 2013, ENSI started a project with the aim of increasing the safety margins in case of accidents beyond the design basis (including seismic and external flooding events) (PP1, OP 2-2, PRT-1). According to the updated NAcP the operators1 reports on increasing the safety margins regarding external flooding were submitted to ENSI and are under review. Depending on the results of the review, ENSI will consider to demand further improvements to enhance safety margins.Question 7: Did the licensee suggest back-fitting measures? What is the status of ENSI s review? Has ENSI already identified the need for necessary improvements to enhance safety margins?
774 | Switzerland |  |  | 8 The stress tests revealed that margins for extreme weather events (besides winds and tornadoes) and combinations thereof were not considered adequately. In 2012, ENSI defined specifications for analyses on the protection against extreme weather conditions, including combinations thereof, to be performed by the licensees. The probabilistic hazard analyses, as well as the proof of sufficient protection of the NPPs against these hazards, have to be submitted by the end of 2013, including submission of the existing margins. Subsequently ENSI will evaluate the licensees' reports in 2014 (PP1, OP 4-1). According to the updated NAcP the updated hazards for extreme weather conditions were submitted at the beginning of 2014 and safety cases will be submitted to ENSI by the end of 2014.Question 8: Did the licensee suggest back-fitting measures? What is the status of ENSI s review? When will ENSI finalize the review and what are the results so far? Does ENSI already identify the need for necessaryimprovements to enhance safety margins? Which back-fitting measure are necessary and what is the time schedule for their implementation?
775 | Switzerland |  |  | 9 In addition to the normal heat sinks, at all Swiss NPP core cooling and residual heat removal can also be achieved by use of well water as an alternate ultimate heat sink, the only exception being Muehleberg NPP. According to present knowledge, a flood- induced blockage of both intake structures cannot be excluded. As a consequence of such an event the water supply will be lost, causing a threat to the core cooling and the fuel integrity [BMLUFW-CH 2014]. In order to assure core cooling and residual heat removal in case of loss of the ultimate heat sink, ENSI ordered the Muehleberg NPP to implement a diversified heat sink that is independent from the Aare River by the end of 2017 (project DIWANAS). According to the updated NAcP in 2013 the Muehleberg NPP decided to permanently shut-down the plant in 2019 and informed ENSI about its intention of abandoning the approved concept for the alternate ultimate heat sink. In 2014, the Muehleberg NPP submitted a proposal of alternative measures for a diverse ultimate heat sink taking into account its limited remaining operating lifetime. In its evaluation (currently in draft form) ENSI approved the proposed concept for the diverse ultimate heat sink, which has to be implemented by the Muehleberg NPP by 2015.Question 9: Does ENSI approve of the current concept for the diverse ultimate heat sink? How does the approval take the limited remaining operation time into account? Does the approval include, for example, the requirement to install a diverse ultimate heat sink according to previous concept in case operation time will be prolonged after 2019?
776 | Switzerland |  |  | 10 In 2012, the ENSREG peer review team criticized the hydrogen management, i.e. the prevention of hydrogen explosion in case of severe accident. It recommended to require a passive systems for hydrogen management for severe accident conditions. It is also recommended to conduct further studies on hydrogen management for the venting systems. Within its action plan for 2013, ENSI requested the NPPs to investigate systematically the issue of migration of hydrogen (PP7, OP6-1 ; PRT-2). According to the updated NAcP the licensees submitted the requested studies on hydrogen mitigation in the containment and about migration of hydrogen to buildings outside the containment. Some licensees proposed to equip their containment with Passive Autocatalytic Re-combiners (PARs). ENSI's review of all these studies is ongoing. Preliminary results seem to confirm the need of back-fitting measures in those NPPs without inertization. Further updates of the plant-specific SAMGs may be required to complement the hardware implementation. It is also mentioned that ENSI will follow up on the extent to which the current deployment strategies for the containment venting systems in severe accidents should be retained.Question 10: When will ENSI finish the review of these studies? Does the licensee propose back-fitting measures? At which plants will the strategies for the containment venting system in severe accident be retained?
777 | Switzerland |  |  | 11 The restoration of the containment integrity in case of a total Station Black-Out (SBO) during shutdown ENSI also identified as an open issue at the end of the EU stress tests. (see OP6-2) The first EU Stress Tests Follow-Up workshop in April 2013 recommended ENSI to put additional emphasis on this issue. According to the updated NAcP the specifications for the analyses to be performed by the operators were issued at the end of 2013. The operators submitted the relevant studies in October 2014. These reports are currently under review.Question 11: When will ENSI finish the review of these studies? What are the results so far? Do the licensees propose back-fitting measures?
778 | Switzerland |  |  | 12 The installation of seismically robust SFP cooling systems was required for the older NPPs (by 2015). According to the updated NAcP the back-fitting project is ongoing. Question 12: What level of earthquake resistance (e.g. H3 plus safety margin?) is required for the new additional SFP cooling system at the Muehleberg NPP?
779 | Germany | 1 | Table 7-1 (Annex, page 68; No. E-5) | Regarding the global scope of recommendation N-13, has this already been covered in all involved plants? The report is not very clear on this regard. Please, do you mind explain any more about it? Apart from some seismic aspects, are there any other activities on going relating to N-13 and natural hazards?
780 | Germany | 1 & 2 & 3 | Table 5-2 (page 46; No. 12) | The report mentions "Performance of an adapted robustness analysis" like an activity "in progress" and too "finalisation 2014". Could be explained better this situation? Has this any relation with the specific consideration of extreme external events (natural or human-induced)?
781 | Germany | 1 & 2 & 3 | Table 5-2 (page 53; No. 13) | Same as before, the report mentions "Performance of an adapted robustness analysis" like an activity "in progress" and too "finalisation 2014". Could be explained better this situation? Has this any relation with the specific consideration of extreme external events (natural or human-induced)?
782 | Germany | 1 & 2 & 3 | Generic | A systematic review in the event of a beyond design earthquake (objective:guarantee of vital functions) has been carried out as part of a robustness analysis of the plants. Question: Please explain the criteria in order to assess margins beyond design basis earthquake ( minimum values HCLPF for equipment needed in strategies against SBO and Severe Accident Management)
783 | Germany | 1 & 2 & 3 | Generic | Question: Regarding the equipment mentioned in the previous point: is there any action planned to verify the maintenance of seismic margins obtained in assessments?.
784 | Germany | 2 | 22 and generic | GKN II/PWR: Battery capacities by plant design are higher than 10 h. Is this the minimum capacity required for German NPPs? Is there any analysis to increase the time until batery depletion?
785 | Germany | 2 | 22 | GKN II/PWR: What are multiple-cell coolers? How is river Neckar the diverse heat sink available (pumping water from the river or from wells)?
786 | Germany | 2 | 25 and generic | KBR. "Creation of a diverse source of cooling water (water intake from a source other than the river". Can you provide additional information about the nature of this additional water sources? Additionally, in general, what engineering solution have German NPPs adopted when the UHS is a river?
787 | Germany | 2 | 16 | To reach the 10 hours duration for batteries, is load shedding considered, or 10 hour sized batteries are implemented?
788 | Germany | 2 | 16 | Please comment about improvements in communications systems in order to coordinate actions from different places during the emergency.
789 | Germany | 2 & 3 | Generic | "Mobile shortened residual-heat removal chain" What does it refer to?
790 | Germany | 3 | 24 | GKN II/PWR: "The operability in an emergency of the permanently installations for fuel pool cooling has been demonstrated". Please, provide clarification of this point, it is not clear if the sentence means that no additional cooling means (neither fixed nor mobile) have been implemented.
791 | Germany | 3 | 33 | KKG/PWR: "Development and preparation of Severe Accident Management Guidelines (SAMG), as well as introduction and instruction at the plant. Development, preparation, plant-specific adaptation, introduction and instruction completed" Which are de Basis that have been used for the SAMGs development? What has been the validation processes performed by the specific NPP for the plant specific adaptation?
792 | Germany | 3 | 47 | GKN I/PWR: "GKN I have developed manual actions for low-power and shutdown operation that can also be used as recommended actions within the framework of SAM" Which are these manual actions mentioned above for low-power and shutdown operation?
793 | Germany | 3 | 17 | Please summarize provisions, or performed upgradings, to initiate actions from the remote shutdown stations.
794 | Germany | 2 | 16 | Please indicate provisions, or credit, taken for the use of hydraulic units, external to the plants, in case of station blackout.
795 | Germany | 2 | 16 | Please comment about the extention of provisios for using portable instrumentation. Is this the first option, or using plant instrumentation supported by batteries is preferred?
796 | Germany | 2 | 16 | During the first 10 hours of the accident, is the ac power supplied by one (or more) portable DG located at the site? Please indicate the time goal for such availability, and the guarantees for extending the performed exercises for a real case a(vailability of personnel at the site).
797 | Germany | 3 | Tabla 7.2 | Paragraph C-2, please explain: How are going to be guaranteed and justified competent and sufficient human resources to face emergencies?
798 | Germany | 3 | Table 7.2 | Paragraph C-13: How often are going to be performed such long term exercises?
799 | Germany | 3 | Table 7.2 | Paragraph C-22, please give more information on which medical and human aspects of the response have to be analyzed to support emergency workers.
800 | Sweden | All | n/a | It is commendable that the activities of the NAcP have been completed according to the planned schedule, or are proceeding according to plan. In many cases, assessments and analyses which have been performed led to the identification of additional measures which are to be implemented. Generally, no deadlines are provided in the NAcP for these consequential measures. In some cases, the measures are not specified. This is addressed in more detail below.
801 | Sweden | 1 | 16/42 | Action T3.LA.1 consists of two parts: Further studies regarding the structural integrity of various buildings; and evaluation of of pipes for controlled pressure relief, between the reactor building and the scrubber system. In table 8.2, only the first part is addressed. No information is provided regarding the second part (outcome of evaluation, further measures...)
802 | Sweden | 1 | 43 | The actions T1.LA.6 and T1.LA.7 concern analyses and studies, and they are completed according to plan. In both cases, it is stated in the NAcP that as a consequence, measures will be performed at some plants. These measures are not specified, and no deadlines are given for them.
803 | Sweden | 2 | 44 | Reassessments of AC power supply have been performed in action T2.LA.3. It is reported that all licensees have drafted plans for the strengthening of the electric power supply. The measures which are planned are not specified, and no deadlines are given for them.
804 | Sweden | 2 | 44-47 | For the actions T2.LA.4, T2.LA.5, T2.LA.6, T2.LA.8 and T2.LA.19, measures which have resulted from the assessments are described. However, no deadlines are given for them.
805 | Sweden | 3 | 47 | As an outcome of action T3.LA.1, overall requirements for an alternative function for cooling the fuel in the fuel pools have been developed. The further course of action is not specified - which measures are planned, what is the deadline? Also, as outcome of T3.LA.3, monitoring instrumentation is to be introduced in the fuel pools in connection with the introduction of the alternative function for cooling. Again, no deadline is provided.
806 | Sweden | 3 | 47 | Action T3.LA.4 led to recommendations for more dose rate monitors in the reactor building. No deadline is given for the implementation of this measure.
807 | Sweden | 3 | 48 | Actions T3.LA.7 and T3.LA.8 concern strategies to manage loss of containment function and other accident management programmes. As a consequence, EOPs will be modified and the emergency preparedness organization is developed further. No deadline is given for these measures.
808 | Sweden | 3 | 48/49 | T3.LA.11 concerns the investigation of the management of hydrogen after a severe accident. It is reported that a number of potential shortcomings have been identified. These shortcomings are not specified, and no deadline is given for the implementation of counter-measures.
809 | Sweden | 3 | 49, 55 | Actions T2.LA.13 - 15 refer to a new emergency regulation, SSMFS 2014:2, which is the revision of SSMFS 2008:15. According to the NAcP 2012 (p, 30), the revised regulation SSMFS 2008:15 was to be implemented in 2013. According to T5.RA.3, the revision has been delayed and the revised regulation enters into force at the beginning of 2015. What is the reason for the delay? Actions T3.LA.13 - 15 were to be completed 2014; are they also delayed, due to the delay of the revised regulation?
810 | Sweden | 3 | 49 | Investigations and assessments concerning filtered containment venting in th long-term have been performed (action T3.LA.16) and it is reported that the licensees suggested different solutions. These solutions are not specified, and no deadline is provided for implementation of measures.
811 | Sweden | 2, 3 | 66 | Regarding the new provisions for independent core cooling, it is stated that SSM will impose a requirement for the definitive solution to be in place by 2020. When will this requirement be issued?
812 | Sweden | All | 68 | It is commendable that only published documents are listed as references. However, a number of these references appear to be available only in Swedish. For transparency and better understanding of the NAcP, it could be seen as desirable for the reference documents to be written in English.
813 | Slovak Republic | All | n/a | It is commendable that most activities of the NAcP have been completed according to the planned schedule, or are proceeding according to plan. Some activities have been completed well before the planned deadline. As far as can be seen from the NAcP, no drastic delays have occured so far. The delay of one important task, which affects 9 activities of the NAcP and the length of which is not specified in the NAcP, is addressed below.
814 | Slovak Republic | 2, 3 | Section III | The integration of improvement programs which started pre-Fukushima with new activities, and the generation of a consistent overall schedule was identified as a complex task in 2013 in the rapporteur's report. Such a schedule had been developed at this time. The consideration of the management of multi-unit severe accidents was mentioned as an example for the coordination of pre-Fukushima and post-Fukushima activities. According to the NAcP 2014, the work concerning multi-unit accidents has been delayed. Analysis of the SAM project and preparing a plan of implementation of additional measures were to be completed by the end of 2014. However, while the corresponding analyses have been completed, the plan of implementation of additional measures is still under preparation. This delay affects a considerable number of activities of the NAcP: 27bis, 32, 34, 39, 41, 43, 44, 48 and 52. The reason for the delay is not provided in the NAcP; also, no revised deadline is given for preparing the plan of implementation of additional measures for multi-unit accidents. Due to the high relevance of this work, it might be appropriate to give some indication as to the reason of the delay, and the expected schedule.
815 | Slovak Republic | 3 | n/a | The rapporteur’s report for Slovakia from the 2013 NAcP Peer Review Workshop mentions the implementation of in-vessel retention which is already completed as a good practice. The report also states: Analyses of consequences of IVR failure and the preservation of containment integrity in case of a severe accident are on-going and were emphasized to be important in the discussion at the Workshop. However, analyses (or any other activities) related to the consequences of IVR failure are not mentioned in the NAcP. Since this issue was seen as important at the 2013 Workshop, it might be appropriate to provide information on the status and - as far as already available - the results and consequences of the analyses. Also, it might be of interest in which framework the analyses are being performed (or have been performed); in particular, whether there is a joint project with other countries with reactors of the type VVER-440/V213.
816 | Slovak Republic | All | p. 11 and Section III | The NAcP lists additional measures which have resulted from analyses defined by originally planned medium-term measures. However, in some cases it is not clear whether measures listed as "original" have not, in fact, already been part of the action as originally planned. For example, for activities 20, 26 and 28, mobile rectifiers are mentioned as additional measure (which already has been supplied). However, activity 20 refers to diversify emergency power sources by assurance of mobile DG for charging of accumulator batteries. In order to charge battery with a DG, a rectifier is indispensable. What is covered by the "additional measure" in this case? Similarly, the activities 18, 28, 29, 30 and 31 refer to [p]rojects for shelters for placing the 0.4 kV mobile DG and cabling between the 0.4 kV mobile DG and selected consumers. The procurement for these shelters is is in progress. However, activities 28 and 31 concern connection of diverse feed water sources ensuring physical accesss and resistance under conditions evoked by an external event. It could be expected that appropriate shelters are an integral part of providing protection against external event. What is covered by the "additional measures" in this case? In activity 54, concerning resistance of seals and penetrations of the containment under severe accident conditions, [r]eplacement of seals at the reactor pressure vessel cavity lids and doors is mentioned as additional measure. Were these important seals not part of the activity right from the beginning?
817 | Slovak Republic | All | Section III | In several cases, no schedule is provided for the "additional measures" which are planned according to the NAcP. This concerns, for example, activities 6, 9, 25 as well as the above-mentioned case of the activities 18, 28, 29, 30 and 31. Furthermore, in the case of activity 25, a plan of implementation of additional measures is reported as having been elaborated, without an indication what these measure might be.
818 | Slovak Republic | All | 67 | Information on the references is very brief; in several cases, even the year of publication is not mentioned. Furthermore, it appears that at least part of the references listed are not publicly available. It could be argued that for reasons of understandability and transparency, NAcPs should only refer to documents which are published. It would be useful if the references which are published are specified so that they can easily be found. Unpublished references should be avoided; if they contain crucial information relevant for the NAcP, a brief account of this information should be included in the NAcP.
819 | Netherlands | All | n/a | It is commendable that most activities of the NAcP have been completed according to the planned schedule, or are proceeding according to plan. For some actions for which new deadlines are given, it is not clear whether there is a genuine delay, or whether the new deadline refers to additional measures which were not planned originally. Additional measures are not always clearly denoted as such, see below.
820 | Netherlands | All | n/a | It is commendable that the Netherlands' NAcP is compiled as a stand-alone report, and is referring only to published material.
821 | Netherlands | 2 | 94/95 | For the NL Action No. 1, a delay is noted in table 8.1 (from 2014 to 2017), which also has effects on NL Action 2. However, the original NLA 1 refers to study and consider options to better protect ERC; whereas the "status end 2014" appears to refer to a proposal for the building of a new ERC, which would be an additional step not part of the original action. Is it the actual building of the ERC which is to be finalized by mid-2017, or is the planning for the ERC to be finalized by then, after resolving issues concerning earthquake risks etc. which are mentioned? Likewise, the original NLA 2 refers to study and consideration of options for storage facilities for mobile equipment, and the building of a facility for heavier equipment is noted as delayed (from 2014 to 2017). Is it the actual building which is to be finalized by end-2017 (which would be an additional measure), or just the planning?
822 | Netherlands | 3 | 101 | For NLA 19B, it is not clear whether the two actions listed in "status end 2014" in table 8.1 which are to be finalized 2015 and 2017 are part of the original activity, or whether they are additional measures which have been derived as a consequence of the original activity.
823 | Netherlands | 3 | 103 | NLA No. 26 was to be finalized in 2013, according to the NAcP from 2012. It is now delayed until end-2016. Under "status end 2014", cooperation with Westinghous is noted as an alternative to PWROG membership as originally envisaged. It is not clear whether this alternative has already been definitely chosen, or whether it is presently under consideration. Also, it is not clear why the original plan has not been followed and what is the reason for the delay.
824 | Netherlands | 2 | 105 | It appears that an important part of NLA No. 33, determining RLE, is delayed (from 2013 to 2015). The reason for the delay is not provided. Furthermore, an additional measure (modifications to enhance seismic margins) is mentioned which presumably was not part of the original planning?
825 | Netherlands | 2 | 107 | NLA No. 39 deals with the hydrogen threat. It appears that the originally planned activities are completed, and [a]dditional studies are ongoing to look for further improvement. What is the schedule for these additional studies?
826 | Netherlands | 2 | 108 | The original activity NLA No. 43 includes implementing extra external connection points for mobile diesel generators. Under "status end 2014", it is noted that [a]dditional connection points to connect a small diesel generator will be implemented, by 2017 Are the "additional connections" an additional measure on top of the "extra external connections"? If so, what is the reason for this additional measure? If the "additional connections" were part of the measure from the beginning, what is the reason for the delay?
827 | Netherlands | 3 | 95 | For NLA No. 4, it is noted that post core melt dose rates were evaluated and dose rates at the refuelling floor in relation to the SFP level were calculated. However, the outcomes of these evaluations and calculations are not reported.
828 | Netherlands | 2 | 107 | For NLA No. 38, it is noted that the impact of aircraft was studied and documented. However, the outcomes of these studies are not reported.
829 | Netherlands | 3 | 44/107 | The rapporteur's report 2013 noted the [w]ithin the frame of the ongoing PSR and NAcP also the possibilities for in-vessel retention of molten core are investigated. In Table 3.1, ENSREG item 3.1, it is noted that the analysis of in-vessel retention in the PSR 2013 is completed. Under the same ENSREG item, NLA 39 concerning hydrogen threats is also addressed. However, in table 8.1, the results of the analysis of in-vessel retention are not reported; this work is not mentioned at all in table 8.1. (Whereas information is provided for NLA 39.)
830 | Romania |  | 2 | CNCAN intend to periodically inform the public about progress with the implementation of the action plan. How will this be done, and how often?
831 | Romania |  | 4 | “Protection against extreme weather events” – Why are winds up to a 10-3/year described here. Is there suitable resistance to wind loads in excess of this?
832 | Romania |  | 5 | Overvew of activities performance and planned by the regulator”. Has the CNCAN regulation for external events of natural origin been published (it was promised for December 14/January 15)? What does CNCAN understand is the state of progress with common EU guidance on the identification of ultimate load capacity for safety related systems and structures?
833 | Romania |  | 8 | Overview of Activities performed and planned by the licensees”. When is the review and revision of the SAMGs due for completion?
834 | Romania |  | 8 | Overview of Activities performed and planned by the licensees”. When will the set-up of the Alternative Off-Site Emergency Control Centre be complete?
835 | Romania |  | 8 | “Overview of Activities performed and planned by the licensees”. When will the final containment resilience improvements be completed?
836 | Romania |  | 9 | “Overview of Activities performed and planned by the licensees”. How have the improvements to the instrumentation and monitoring been solved? This may be a good practice worth sharing with the community. More detail would be helpful.
837 | Romania |  | 9 | “Overview of Activities performed and planned by the licensees”. When will the improvements to instrumentation be completed? Table 1 Action 24 states this will be complete for Unit 1 in the 2016 outage. If the work starts for Unit 2 in the 2015 outage, when will it all be completed and commissioned and operable?
838 | Romania |  | 9 | “Topic 4 – National Organisation” As the first 5 year strategy for nuclear safety and security was presented to the government in July 2014, what is progress with developing a process for annual monitoring? Has a process been developed, or is it still being developed alongside the first progress report which is presumably due in the middle of 2015?
839 | Romania |  | 10 | “Emergency Preparedness and Response” What is the IGSU organisation?
840 | Romania |  | 10 | “Emergency Preparedness and Response”. Have the recommendations made by CNCAN been incorporated in the revision of the national response plan, or what is the timescale for completion?
841 | Romania |  | 11 | “International Cooperation” What are the aims and objectives of the CNCAN and NRPA joint programme?
842 | Romania |  | 11 | “International Cooperation” What relevant IAEA peer-review services are being considered by CNCAN? How can this item be considered as “implemented” at Action 42.
843 | Romania |  | Table 1 | Actions 8 & 9. How can this action be consider completed – the table gives a date of when it is envisaged published as Dec 14 or Jan 15. Is this complete now?
844 | Romania |  | Table 3 | Item 35. Does CNCAN consider a further review of SAM exercise planning will be needed to ensure the exercise programme tests all of the changes yet to be competed to the on-site and off-site emergency response centres and associated instrumentation and monitoring?
845 | Romania |  | Table 3 | Item 39. This question was about both voice and data communications. The responses in Table 1 actions 30 and 39 appear to address voice communication systems only. Are plant parameters and radiological data also now available at emergency centres?
846 | Romania |  | Table 3 | Item 40. What international development activity is in hand for the handling of large volumes of contaminated water?
847 | Romania |  | Whole report | Have any improvements been delayed or de-prioritised?
848 | Netherlands | All | n/a | Revised NAcP informs that the majority of measures to improve nuclear safety planned by the end of 2014 have been done, remaining measures are in progress. There is certain delay for some measures due to objective reasons (e.g. a decison to build a new ECR). The RB is in the process of determining its position regarding the rescheduling delayed Actions. Thus the new dates only constitute proposed rescheduling dates. What is the schedule for final determining the new completion dates by the RB?
849 | Netherlands | 5 | 5 (NR 6.1.5) | Reassessment of ERO Staffing - regarding its adequacy 24/7. The measure has been implemented. The ERO is adequate and can be deployed 24/7. What is the organization of shifts concerning the number and profile of people?
850 | Netherlands | 5 | 27A (NR 7.3.2) | Assessment of the need to upgrade equipment and/or instrumentation dedicated to SAM purposes (hardened core approach). Part A includes: study increasing robustness existing equipment & study protection of equipment against BDB extreme hazards. According the revised NAcP the measure have been implemented since 2013 The existing equipment is robust only the robustness of the SFP level measurement must be enhanced. What is the current status of the SFP level measurement enhancement (or date of enhancement)?
851 | Netherlands | 5 | 29 (SI) | Study of a reserve SFP cooling system independent of power supply A study was finished by determining the possibilities of an AC power independent SFP cooling system. Proposed solution consists of external makeup water injection and filtered steam relief from the containment. What type of the external makeup water system it will be (separate building, vessel, mobil....?.)?
852 | Netherlands | 2 | 38 (S6) | Study impact aircraft impact on safety functions The project has been implemented im 2013. The impact of relevant aircraft on the containment were studied and documented. What type of aircraft was defined for the study and what conclusions were made from the study?
853 | Netherlands | RB | RB-4.002 | The RB is drafting requirements for the design and construction of new nuclear reactors including internal & external hazards - they will be implemented in the regulatory framework. Draft exists since 2013. What is the current status of the DSR and when it will be issued?
854 | Sweden | All | n/a | Revised NAcP informs that the majority of measures to improve nuclear safety planned by the end of 2014 have been done, remaining measures, which are due by 2015, are in progress. Conclusions of a number of studies lead to further actions, having the character of "hardware changes". It would be desirable to supplement the action plan on a specific list of these changes, with a timetable for their implementation. Conclusions of a specific interest are identified in questions bellow.
855 | Sweden | 1 | T1.LA.7 (p. 43) | Evaluation of the protected volume approach NAcP asked to perform a study by 2014 to identify critical areas and spaces regarding flooding of the sites. In the revised NAcP it is stated that "Based on performed stress tests, measures will be performed at some plants". Which measuers and in what time these measures will be implemented?
856 | Sweden | 2 | T2.LA.5 (p.44) | Reassess the integrity of the primary system NAcP asked to further evaluate and reassess the integrity of the primary system for prolonged extreme situations resulting from natural phenomena and other events. This included also reassessment of the primary pumps seals which will be replaced. Does the replacement of the seals solve the problem what kind of seals it will be and whet they will be replaced?
857 | Sweden | 2 | T2.LA.19 (p. 46) | Reassess the risk of criticality and/or re-criticality NAcP asked to evaluate and reassess the risk of criticality and/or re-criticality during prolonged extreme situations resulting from natural phenomena and other events. Evaluations should have especially considered the risk of criticality in PWR during boron dilution. In the revised NAcP it is stated that "For Ringhals PWRs re-criticality must be considered in the long time scenario. Measures have been identified and addressed". How is the potential re-criticality (boron dilution) of Ringhals PWRs linked with extreme situations resulting from natural phenomena and other events (which scenarion has benn considered)? What measures will be implementedand when?
858 | Sweden | 3 | T3.LA.2 (p.47) | Define the design basis for an independent core cooling system NAcP asked to define a fundamental design principles of an independent core cooling system for injection of water to the reactor pressure vessel to handle SBO. This shall include a conceptual design of the system as well as definition of major system parameters. In the revised NAcP it is stated that "The licensees have in a common project developed a ”Position Paper” that defines requirements that shall be adopted". Provide more detail infomation regarding the conclusions and measures to be addopted.
859 | Sweden | 3 | T3.LA.5 (p. 47) | Develop a plan to handle more than one affected unit NAcP asked to develop a thorough plan for managing several, simultaneously affected units, including staffing and procedures. In the revised NAcP it is stated that "As a direct measure after the Stress tests the licensees have developed training scenarios and emergency exercises in which more than on reactor is involved". Is the training scenario and emergency excercises sufficient for "a thorough plan for managing several, simultaneously affected units, including staffing and procedures"?
860 | Sweden | 5 | T5.RA.2 (p. 55) | SSM and the nuclear facilities are currently working towards establishing a system for electronic transmission of plant data from the Swedish nuclear power plants to SSM’s Emergency Response Centre. Project is in progress. What is the status of the project and when it will be completed?
861 | Slovak Republic | All | n/a | Revised NAcP informs that the majority of measures to improve nuclear safety is implemented in accordance with the planned schedule. Conclusions of some studies lead to further actions, having the character of "hardware changes". It would be desirable to supplement the action plan on a specific list of these changes, with a timetable for their implementation. Conclusions of a specific interest are identified in questions bellow.
862 | Slovak Republic | 1 | ID 4 (page 15-16), ID 8 (p. 18) and othres | New metrological studies for the site were developed for EBO and for EMO. A draft time schedule of implementation of measures for 2014 - 2018 to enhance the resistance of selected EBO and EMO1,2 civil structures was prepared. Currently the design documentation for implementation at EBO and EMO is being prepared. What are the main conclusions of the studies and what measures are going to be implemented in EBO and EMO.
863 | Slovak Republic | 2 | ID 19 (p. 28) ID 34. (p. 49) | A project for instalation of a 400 kV circuit breaker in the local substation for disconnection of units from the power grid has been approved. Installation is expected in 2017 – 2018. Why there is such a long time needed for implementation.
864 | Slovak Republic | 2.3 | ID 27. bis (p. 37) ID 39 (p. 53) ID 41 (p. 55) ID 44 (p. 57) ID 48 (p. 60) ID 52. (p. 62 - 63) | NAcP asked to prepare a plan of implementation of additional measures for extension of the SAM project to improve the severe accident manageability at its simultaneous occurrence in all units at the same site. Analysis and plan of implementation of additional measures were completed by 31/12/2014. What kind of measures do you intend to implement and in what time?
865 | Slovak Republic | 3 | ID 46 (p. 59) ID 47 (p. 59) | Issues of presence of hydrogen in unexpected places and large volumes of contaminated water are in progress. Partial outputs can be expected at the beginning of 2015. Are there already any outcomes?
866 | Slovak Republic | All | n/a | To what extent is the implmentation of meaures for NAcP coordinated with other VVER 440 operators?
867 | France | 1 | 20 | Implementation of automatic shutdown in the event of an earthquake: Under which conditions can the system to be installed detect an earthquake early enough to trigger an automatic reactor shutdown at a suitable moment?
868 | France | 1 | 24 | Can you provide more information on the present state of defining the design of the hardened safety core?
869 | France | 1 | 34 | Reinforcement of the U5 venting-filtration system ("sand-bed filter"): Could you provide more information on the present state of actions related to the reinforcement of the U5 venting-filtration system? Under which conditions would alternative strategies be acceptable?
870 | France | 1 | 45 | Was there anything surprising in the results of the feasibility study on installing a geotechnical containment?
871 | UK | 1 | 6, 47 (78) | Secondary Effects of Earthquakes: this topic addresses the potential for seismically induced fire and for seismically induced external flooding (including from tsunamis); which were the conclusions of the licensees and of the safety authority regarding the assessment of other seismically induced risks, like internal flooding resulting from the rupture of tanks, pipes, cooling-tower parts, or from the fall of packing in a cooling-tower basin?
872 | UK | 2 | 9, 10, 14, 15 (78) | Some mobile devices like backup generators or mobile autonomous pumps are stored on site or close to the site because they are needed quickly after the event occurrence; what is the protection level of these devices against the extreme events they are intended to cope for (including the seismic qualification level)? Same question for the connection points and the instrumentation and monitoring.
873 | UK | 3 | 11, 17, 44 (78) | Filtered Containment Venting (FCV): besides already installed Passive Autocatalytic Recombiners and already performed penetrations for containment-cooling water injection, a feasibility study for the installation of a FCV at Sizewell B is now complete and a decision on FCV installation will be made in the early part of 2015. Assuming the decision is taken, what is the expected planning for FCV operation, what are the expected FCV performances (in terms of decontamination factors in particular) and what is the expected protection level of the FCV against extreme events (including the seismic qualification level)? And what would be the RB position in case the licensee would decide not to install a FCV?
874 | UK | 3 | 12, 13, 14, 17, 22, 27, 28, 51 (78) | Emergency Response Centre (ERC) at Sizewell B: the new ERC of Sizewell B, located close to the site, is claimed to be "hardened", without further details; a short summary of main design principles is asked (in terms of resistance to extreme events to manage, location, habitability, capacity in terms of operators and mobile means, communication means, plant parameter control, power supplies, fire protection, radio-protection, ...).
875 | Netherlands | 3 | 17, 103 (126) | The robustness increase of existing equipment and the protection of equipment against extreme hazards were the subject of a study that concluded that the robustness of the spent-fuel-pool level measurement had to be upgraded. What main design aspects have to be upgraded (like qualification to earthquake and to accident conditions, location of the measurement reading (control room, local, other), backup power?)? Is it the study alone, or the robustness upgrade that was (were) finalized in 2013? If no, what is the planning of robustness upgrade?
876 | Netherlands | 3 | 25, 34, 38, 51, 94, 95 (126) | Emergency Response Center (ERC): an alternative location was implemented in 2013; this location is claimed to be flood resistant; what is the level of resistance against other extreme natural events like earthquakes, bad weather conditions? A new ERC is proposed for 2017, to shelter the emergency response organization after all foreseeable hazards: what does "all foreseeable hazards" mean? What are the other main design principles (in terms of location, habitability, capacity, communication means, plant parameter control, power supplies, fire protection, radio-protection, ...)? Only a few of them are addressed in the report.
877 | Netherlands | 1 | 26 (126) | Flooding margin assessment is claimed to be a continued practice; in which framework (other than stress tests) and with which recurrence is this practice continued? Is margin assessment for other natural hazards or external events also a continued practice? If so, in which framework and with which recurrence? And if no, why?
878 | Netherlands | 2 | 31, 108, 109 (126) | Reassessment of alternative power sources (action 43) and better arrangements of mobile diesel generators and batteries (action 44) are linked together and aim at installing an earthquake-resistant backup UPS in the bunker. They are rescheduled from 2013 to 2017. What compensatory measures are taken in the meantime?
879 | France | 2 | 8 (73) | Installation of Intermediate-capacity emergency diesels are now installed for supplying power to I&C and lighting in the control room. Are these diesels the only emergency power supplies presently available? If so, what safety functions can be ensured in case of prolonged SBO, before the power-supply improvements scheduled by the end of 2018 in the frame of the Hardened Safety Core? Are there associated compensatory measures in the meantime, and if yes, which ones, and if no, why?
880 | France | 1 | 20 (73) | The safety authority recently accepted (October 2014) the introduction of an automatic scram in case of an earthquake; a consequence of such an automatic scram is the possible superposition of earthquake and shutdown loadings, given the earthquake average levels expected in France compared to those expected in Japan for instance. How were the consequences of this possible loading superposition taken into account in the decision taken?
881 | France |  | 21 (73) | Design review of the heat sink: based on studies performed by the licensee, the safety authority concludes that improvements are needed for the design basis (hazard identification, requirements for equipment) and organizational provisions (operational procedures, maintenance programs, surveillance of safety functions). What is / are the related planning(s) of implementation?
882 | France | 2 | 30 (73) | By the end of 2013, the spent-fuel-pool level measurement has been made operational in case of total loss of electrical power. What main design aspects of the spent-fuel-pool level measurement have to be upgraded in the frame of the Hardened Safety Core (like qualification to earthquake and to accident conditions, location of the measurement reading (control room, local, other), backup power?)? What is the expected planning for this upgrade?
883 | France | all | 72 (73) | The global planning in section 5 is dated December 2012; is it a misprint or is there a more recent planning update?
884 | Lithuania | 1.3 | 5 | Some recommendations were related to the potential construction of a new NPP at Visaginas, Reference to this new plan has been deleted ( version 2012 of action 2: "All other requirements dedicated to Visaginas NPP that encompass other fields should be checked in the light of post-Fukushima lessons learned and proposal of update if necessary"). Is there still a project of a new NPP? Are the checks done? If yes, what are the results and eventually foreseen adaptations of the requirements?
885 | UK | 1 | 47 | Concerning the protected volume approach, one understands that the implementation of site resilience modifications are completed while the flooding studies are not. Are another modifications to be realized following the completion of the studies? Or all modifications have been decided before the realization of the studies?
886 | UK | 1 | 21 | Large volumes of contaminated water. Is the strategy considering a mutliple-unit event or a mutliple-sites event? As the means are centralized, is there a solution in case of event preventing acess to the sites? Earthquakes, …
887 | Belgium | generic | whole report | Thank you for a very clearly written report! It gives a good overview of the most significant actions without exhausting tables.
888 | Belgium | generic | 3 | It is mentioned that some actions were cancelled because the remaining operating lifetime made them irrelevant (Doel 1 and 2). According to the recent Government decision, life extension of these reactors is no longer opposed. What is the current situation with continued operation of Doel 1 and 2, has Electrabel made an official request for LTO? What actions were included in the original NAcP for Doel 1 and 2 and will they all be required if licensee applies for LTO (e.g. filtered venting systems=?
889 | Belgium | 1 | 10-11 | Quite many actions are taken at Tihange NPP against flooding. Has the licensee made an assessment of the core damage frequency, how large fraction of CDF came from external flooding before the plant changes and what is the situation after the plant changes?
890 | Belgium | 4-6 | whole report | Topics 4-6 are not included in the report. A short description on the current situation with those actions should be added.
891 | Czech Republic | 3 | 48 | Recommendation from Luxembourg peer review (3.3.2.3.2) states that "The means for maintaining containment integrity should in particular include depressurization of the reactor coolant system, prevention of damaging hydrogen explosions, and means of addressing long-term containment over-pressurization, such as filtered venting. (§ 7.3.4)" Depressurization has not been discussed in the report. Is the status considered adequate, or are there any plans to ensure primary depressurization in SAM
892 | Germany | generic | whole report | The report mainly includes tables of different actions and links to national requirements and European recommendations. It is difficult to get an overview of the most significant actions at the NPPs. Also the plant specific action tables are little bit different in the level of details. E.g. table including actions for GKNII is more generic than for other NPPs (does not clearly describe the plant modifications or reasons for additional information requests).
893 | Hungary | 3 | 50 | Description of tasks 29 and 31 say that installation of hydrogen monitoring system (task 29) and modification for molten core stabilisation (task 31) have been implemented for units 1 and 2, and will be implemented for units 3 and 4 in 2013 and 2014. Have these measures been implemented for units 3 and 4 according to the plan?
894 | Netherlands | 1-3 | the whole report | Quite many actions have been rescheduled. What is the reason for that?
895 | Netherlands | 1 | 23 | It is said that implementation measures are rescheduled from 2016 to mid 2017. Does this mean that the study of fire fighting systems is rescheduled? When would the implementation of possibly needed actions take place?
896 | Netherlands | 2 | 33 | It is said that the assessment of the need to upgrade equipment and/or instrumentation to SAM purposes has been completed. Did this result any actual modifications at the plant?
897 | Netherlands | 3 | 44 | It is said that the molten corium stabilization has been analysed in PSRs. What was the result, were there any needs for changes identified or additional study needs?
898 | Netherlands | 3 | 44 | It is said that the reviews of hydrogen management studies has been completed. What was the result of the extended studies (e.g. the management of hydrogen from the SFP, in the filtered venting system, and in the neighbouring buildings)? Were there any additional needs for plant changes identified?
899 | Netherlands | 3 | 50 | It is said that the study was finished in 2013 concerning the potential dose to workers. Implementations is said to be rescheduled from 2014 to mid 2017. Table does not specify what are the rescdeduled actions. Are there some plant modifications planned related to this subject?
900 | Ukraine | General | 3 | It is said that “the schedule for a series of safety improvement measures at operating NPPs that require substantial funding has been extended, taking into account the situation on the territory of Ukraine over the last year and the decision made by the operating organization to shut down the power units when their design-basis life expires in order to implement all safety improvement measures needed to justify long-term operation.” What does this mean in practice? What improvement measures in the report’s tables are linked to long-term operation and what measures are taken even if the plant will be shutdown when their design-life expires? Are the schedules presented in the report’s tables still valid or will they be somehow extended according to this sentence in the introduction?
901 | Ukraine | Other | 8 | Table 1, Action 23. The action related to the decisions on the management with large volumes of contaminated water is interesting since not many countries are having any measures related to this topic. Are there any preliminary results concerning the analyses?
902 | Switzerland |  | 12 | 1. What is the timescale for completion of the Muhleberg flood protection work on the intake structure? (Page 12)
903 | Switzerland |  | 12 | 2. Are the revised proposals for Muhleberg ultimate heat sink worth sharing with the wider community as an example of a pragmatic engineering solution for a short period of operation?
904 | Switzerland |  | 16 | 3. What is the timescale for completing all of the SFP modifications? (Page 16)
905 | Switzerland |  | 19 | 4. What compensatory measures have been taken at Beznau for the delay in the SFP building upgrade? (Page 19)
906 | Switzerland |  | 34 | 5. What is the status of the 56 recommendations from the working group IDA-NOMEX – previously identified as a good practice in the 2012 peer review. (page 34)
907 | Switzerland |  | 39 | 6. Is ENSI concerned that the manadatory plant evaluations after an INES level 1 in their plant or an INES Level 2 at any plant in Switzerland or internationally loses some focus on self evaluation and reporting of lower tier events? (Page 39)
908 | Switzerland | Fukushima Action plan 2014 & 2013 |  | 7. Several designated items have been given a status of LA (within ongoing supervisory activities) when the implementation seems incomplete – is this correct, see for example, PP3, PP20.
909 | Switzerland | Fukushima Action plan 2014 & 2014 |  | 8. It is very difficult to confirm topics for which progress has been made and those which have had limited or no progress. By comparing the 2013 and 2014 Fukushima action plans it appears there has been limited or no progress on items, PP!, PP5, PP6, PP15, PP21, PP25, PP34, OP6-1, PRT-1 is this correct?
910 | Switzerland | Fukushima Action plan 2014 & 2015 |  | 9. Could ENSI provide a summary to show how topics have progressed, such as NI to 2014 or NI to B, or NI to LA. I could try to do this, but only have the 2013 and 2014 reports from the internet so I can’t compare progress in 2014 with the last Peer Review in 2012.
911 | Switzerland | Fukushima Action plan 2014 & 2016 |  | 10. Have any delays been introduced by other higher priority work?
912 | Belgium |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
913 | Belgium |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
914 | Belgium |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
915 | Belgium |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
916 | Bulgaria |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
917 | Bulgaria |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
918 | Bulgaria |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
919 | Bulgaria |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
920 | Czech Republic |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
921 | Czech Republic |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
922 | Czech Republic |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
923 | Czech Republic |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
924 | Finland |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
925 | Finland |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
926 | Finland |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
927 | Finland |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
928 | France |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
929 | France |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
930 | France |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
931 | France |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
932 | Germany |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
933 | Germany |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
934 | Germany |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
935 | Germany |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
936 | Hungary |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
937 | Hungary |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
938 | Hungary |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
939 | Hungary |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
940 | Lithuania |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
941 | Lithuania |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
942 | Lithuania |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
943 | Lithuania |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
944 | Netherlands |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
945 | Netherlands |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
946 | Netherlands |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
947 | Netherlands |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
948 | Romania |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
949 | Romania |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
950 | Romania |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
951 | Romania |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
952 | Slovak Republic |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
953 | Slovak Republic |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
954 | Slovak Republic |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
955 | Slovak Republic |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
956 | Spain |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
957 | Spain |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
958 | Spain |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
959 | Spain |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
960 | Sweden |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
961 | Sweden |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
962 | Sweden |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
963 | Sweden |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
964 | Switzerland |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
965 | Switzerland |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
966 | Switzerland |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
967 | Switzerland |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
968 | UK |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
969 | UK |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
970 | UK |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
971 | UK |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
972 | Ukraine |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
973 | Ukraine |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
974 | Ukraine |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
975 | Ukraine |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?
976 | Slovenia |  | Generic | 1. If the same flaws as in Doel 3/Tihange 2 were to be found at one of the reactor pressure vessels, could these flaws pose a risk to the emergency core cooling measures?
977 | Slovenia |  | Generic | 2. Which recommendation/suggestion by the EC working document, ENSREG, the peer review team, the fact finding team or formulated by the National Action Plan Workshop are not followed up and what is the justification for this decision?
978 | Slovenia |  | Generic | 3. For which reactor and which measures did the regulator grant exemptions from the requirements with the argument of the reactor's limited remaining operating lifetime?
979 | Slovenia |  | Generic | 4. In a letter of 20 Feb 2013 to the permanent representatives to the EU, the European Commission warned the member states that the implementation of the stress test action plans likely fall under the scope of Directive 2011/92/EU on the assessment of the effects of certain public and private projects on the environment (the EIA Directive). Which of the so far implemented stress test actions have been subject to an Environmental Impact Assessment?