## Sheet0 (hidden)
Belgium | 01- General information
Bulgaria | 02- Overall ageing management programme requirements and their implementation
Czech Republic | 03- Electrical cables
Finland | 04- Concealed pipework
France | 05- Reactor pressure vessels
Germany | 06- Calandria/pressure tubes (CANDU)
Hungary | 07- Concrete containment structures
Italy | 08- Pre-stressed concrete pressure vessels (AGR)
Netherlands | 09- Overall assessment and general conclusions
Poland
Romania
Slovak Republic
Slovenia
Spain
Sweden
United Kingdom
Norway
Switzerland
Ukraine

## ALL REPLIES COLLATED
All replies to questions on Topical Peer Review (Article 8e of Directive 2014/87/Euratom)
QUESTION-ID | Country's own id | Reviewer | NAR | Topic | Page number | Question, comment | Source | Country Response | Remarks/ Cross reference to Question-ID
BE-1 | 1 | Slovak Republic | Belgium | 01. General information | 3 | Is there licensee´s ageing management database in place? How is it structured? Does it include acceptance criteria and trending to decide on the required steps for corrective actions? |  | There exists no other database or list than what is described in the National Assessment Report (scoping document, ageing summaries, etc.). The overall ENGIE Electrabel maintenance and ageing policy is to avoid corrective maintenance on important to safety SSC. Nevertheless, the Ageing Summaries and Ageing Management Programs cover the various corrective measures for each possible ageing phenomenon. Corrective actions are applied following feedback from preventive and corrective maintenance activities, post-job debriefings, re-work analyses, etc. or whenever tests, maintenance activities or daily operations reveal component failure. Afterwards, the applied measures can result in adaptations to maintenance plans, maintenance strategy documents, AMPs, or even equipment modification projects. ENGIE Electrabel uses the health reporting tools to monitor the performance and availability of the SSCs. A part of the health reports consist of rework analyses and a track record of all registered events on a specific system.
BE-2 | 2 | Poland | Belgium | 01. General information | 5 | Do they consider the risk of aging VENUS and BR 1 to be negligible and why? Please explain. |  | Venus and BR1 are two research reactors that are part of the Belgian Nuclear Research Center (SCK CEN), which is a class I nuclear facility according to the Belgian regulation. In accordance with this regulation, all the nuclear installations of SCK CEN are submitted to the regulatory framework of Class I installations. The same regulations applicable to BR2 are therefore also applicable to Venus and BR1, such as the requirements on Periodic Safety Review or ageing management (i.e. Article 10 of the Royal decree of 30 November 2011 [1A] on the Safety Requirements for Nuclear Installations (SRNI-2011)). Venus and BR1 are not included in the Belgian NAR for the TPR Ageing, mainly for the reason that they do not meet the criterium to being included in the scope of the TPR (see Technical Specifications for the TPR). In addition, the number of pages to describe the ageing management of both nuclear power reactors and research reactors was limited within these specifications. Proactively adding these two reactors within the scope of the TPR would have had a negative impact of the level of reporting details requested to the licensees for the BR2 research reactor and the nuclear power reactors.
BE-3 | 3 | EC | Belgium | 01. General information | 5 | 1.1: The BR1 research reactor is not included in the TPR, although it has a thermal output of (exactly) 1MWth. In the report it was mentioned that: "It was proposed by the licensee SCK CEN and the FANC to not consider the BR1 in the national report for the topical peer review on ageing". To whom was this proposed (and accepted)? |  | FANC presented its interpretation of the WENRA technical specifications for the TPR at WENRA RHWG.
BE-4 | 4 | Netherlands | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 5 | According to the technical specifications: research reactors with a power equal to 1 MW or above will be covered in the NAR. Even with the reduced power the BR1 reactor would be expected to be included in the NAR. Could Belgium explain why BR1 was not included in the NAR although it has a power of 1 MW? |  | The Belgian Safety Authority has considered that the BR1 was out of scope of the TPR, as the maximal authorized operating power is 1 MWth and that the reactor works most of the time at lower power. It was decided to focus on the BR2 research reactor.
BE-5 | 5 | Czech Republic | Belgium | 01. General information | 5 | What was the reason to decrease operational thermal power of BR1 research reactor to 1MWt? |  | In fact, it was impossible for years now to operate the BR1 research reactor at the original design thermal power of 4 MWth, due to technical constraints in the cooling systems. In addition, as a consequence of 50 years of improvements, license amendments and changes in the federal and regional regulations, the general license of the Belgian Nuclear Research Center (SCK CEN) was very complicated and difficult to comprehend. It was then decided to simplify and rewrite the global license and to take advantage of this administrative work to have the license limits coincide with the actual technical limits of operation of the BR1, which is 1 MWth.
BE-6 | 6 | General AMP expert group | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 5 | Comment:The BR2 reactor is operating for more than 50 years. As a consequence, most of the SSCs have undergone some kind of ageing management, such as replacement, redesign, inspections, testing. A limited number of ageing requirements were prescribed in the license. Others are listed in the safety report. Some of the SSCs were followed using procedures, while others were tested and maintained based on the judgement and experience of the responsible persons. A formal Ageing Management Program (known as Plant Asset Management – PAM) for BR2 started in 2011 and is still under development. The implementation of the ageing management program has to be completed before June 2019. The SCK•CEN was required to improve and implement the ageing management program of the BR2 to reach a level that is commensurable with the best international standards and practices for research reactors |  | Thanks for the comment.
BE-7 | 7 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 6 | The Belgian National Assessment Report as such relies heavily on the self-assessment procedures of the power plant operators. The Belgian Safety Authority requires the licensee, in this case Electrabel, to provide the basic content of the Belgian National Assessment Report. Even though regular meetings between each licensee and the Safety Authority took place during the year 2017, this may still leave room for errors or even manipulation regarding the subsequent processing of the data. 1. With regard to future topical peer reviews, does the Belgian Safety Authority intend to carry out assessments by independent bodies in addition to the self-assessments of power plant operators? 2. Would the Belgian Safety Authority support the idea of an independent EU-supervision carrying out such assessments? |  | 1. This question is quite confusing and indicates a misunderstanding concerning the functioning of the nuclear safety supervision and the ENSREG Topical Peer Review process. In a first step, a self-assessment is performed by the licensee itself, and this assessment is also reviewed by the internal health physics department of the licensee. Then, in addition to the self-assessments by the licensees, independent assessments were performed by the Belgian Safety Authority (taking into account input from its inspections and review & assesssment activities on the topic of ageing management) . The Belgian Safety Authority (FANC and its subsidiary Bel V) is an independent body who has as one of its primary goals the independent assessment of the safety level of nuclear facilities. Thus, the independent assessment has already been performed and is documented in the Belgian NAR. 2. The second part of the question is considered out of the scope of the TPR The Belgian Safety Authority does not feel that the TPR is the adequate forum to reply to questions on the idea of an independent EU-supervision. Such political questions have to be addressed to the adequate political authorities, such as the federal government of Belgium.
BE-8 | 8 | Switzerland | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 9 | According to chapter 2.1 no regulatory guide for the implementation of an overall AMP exists up to now. Is the development of such a guide planned in the near future? |  | Not for the moment. The Belgian Safety Authority relies on the international guidances from IAEA for the implementation of an overall AMP. Nevertheless, two regulatory guides have been developed in the past for preparing LTO periods for NPPs and research reactors.
BE-9 | 9 | Switzerland | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 9 | Do requirements exist in the national regulatory framework for the licencees to report periodically about progress and adaption of the existing AMP? |  | Yes. First , a requirement exists within the PSR process to report on the AMP. In addition, the article 10.3 of SRNI-2011 requests to continuously revise and update the AMP based on OEF. The actual progress and updates of existing AMPs are also reviewed during periodic thematic inspections on ageing management, which are now part of the new Global Inspection Plan by the Belgian Safety Authority that comes into force in 2018.
BE-10 | 10 | Concrete containment PCPV expert group | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 9 | 2.1.3.1 Have you made special arrangements for examining differential settlements of the buildings (Tihange 1) ? If so, did it apply to these arrengements in other units ? |  | ENGIE Electrabel made special arrangements to survey the differential settlements of the buildings, wherever appropriate and for all Belgian nuclear power plant units.
BE-11 | 11 | Poland | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 11 | Are they going to implement the requirements of the latest IAEA safety standards (GSR part 2) in AMP? Can you explain it more widely? |  | GSR Part 2 is related to 'Leadership and management for safety'. This document is not linked to an Ageing Management Program, but to 'Organisation design'. In the framework of its Ageing Management Program, ENGIE Electrabel follows a series of IAEA and U.S. NRC guidelines and standards, as explained in chapter 2.A.2 International Standards and Guidance of the National Assessment Report.
BE-12 | 12 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 12 | On page 13, it is stated that the current aim is to update the Ageing Management Program for units Doel 3 and 4 and Tihange 2 and 3 to the program installed for the Long Term Operation units. Why wasn’t this already the case before and when and how will the update be carried out? |  | Ageing Management Program of the nuclear NPPs is in line with with the prevailing regulations and FANC requirements : - The Ageing Management Program (AMP) for nuclear power units Doel 1&2 and Tihange 1 has been addressed in the framework of the Long-Term Operation Study Program. The AMP for these LTO units is in line with the FANC’s Strategic Note and follows the methodologies specified in 10 CFR 54, NUREG-1800 Rev.1 and NUREG-1801 Rev.1. This approach and the resulting lifetime extension of the nuclear power units Doel 1&2 and Tihange 1 has been endorsed by the IAEA during a Safety Aspects of Long Term Operation (SALTO) mission. - The ageing of the other Belgian nuclear power units (Doel 3&4 and Tihange 2&3) has been evaluated in the framework of the PSR Program and is in line with the prevailing regulations and FANC requirements. The AMP for these units is updated as part of the continuous improvement process and will be re-evaluated during the next PSR.
BE-13 | 13 | Switzerland | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 13 | Do programmes exist for the qualification of non-destructive testing methods to be applied and are these programmes also linked to the AMP? |  | See question 113. | ref to BE-113
BE-14 | 14 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 13 | 2.3.1.: The WENRA TS, asks for indicators that are used to asses the process' effectiveness (p11 of the TS). These however were not discussed in the document. Does this means that they do not exist? In the paragraph on review/update of the AMP (§2.4.d, page 13 of WENRA TS) as similar indicator was also asked, but it was not found in the corresponding § of the NAR. On page 30, however, it is stated that ENGIE has developed KPI's the monitor the progress of the AMP processes: does this mean that they only concern the LTO-units? Could you clarify what these KPI's are and to which units they relate? |  | As explained in chapter ‘2.A.4.3 Licensee Self-assessments and Audits’, ENGIE Electrabel has developed KPIs to monitor the progress of the Ageing Management Program (AMP) processes. Three set of KPIs are monitored : KPIs from Health Reporting, KPIs from Ageing Summaries & KPIs from AMPs process for all units (Tihange 1-2-3 and Doel 1-2-3-4) The most important parameter to assess ageing management effectiveness is the systems or component status, which is monitored using health reports. The health report indicates a system’s or component condition based on a set of KPIs and the operational events that have occurred on this system or components during the period of analysis. Some examples of health report KPIs are: - The number of justifications for continued operation (JCO) - The number of observation files, the number of (unforeseen) unavailabilities of the system - A re-work analysis - The evolution of the leakage - Etc. Based on these KPIs, the system’s operational performance and their own expertise, the ENGIE Electrabel system experts assign a colour-coded health status to each system: - Green: System / components are reliable and operation parameters are stable. - White: System / component are considered to be reliable, but some parameters need specific attention or additional monitoring (e.g. action plan to green is performed, but some additional monitoring is needed to be sure that the situation remains stable). - Yellow: Availability and/or reliability of some components / systems is degraded as some operational parameters operate outside of their ‘normal’ band. They require specific attention and an action plan to ensure no punctual degradation could lead to partial or complete unavailability of the system’s function. - Red: Availability of the system is degraded - performance of the system is not acceptable. These circuits / components require a deep and quick action plan. ENGIE Electrabel also developed specific KPIs for the Ageing Summaries and AMPs: - Number of recommendations open, closed. - Rate of recommendations planned, in completion, completed or delayed. All those KPIs are implemented for all our NPPs.
BE-15 | 15 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 14 | 2.3.1: The scope of the AMP: the use of ageing summaries for NPPs seems very well supported in the organisation. However, in the document, precise information on the summaries is not given. Since this might be a good practice, it might be very interesting to have. |  | Page 14 details the content of the Ageing Summaries. These documents typically have the following structure: 1. Equipment: Identifies and describes the concerned System, Structure or Component. 2. Problem description: Describes the ageing phenomenon 3. Understanding of the phenomenon 3.1. General description of the ageing phenomenon and its current understanding which includes the reference to the LTO AMPs. 3.2. Contributing causes: Identifies the parameters responsible for the ageing phenomenon, its initiation, propagation, severity, etc. (e.g.: temperature, fluence, material, stress level, fluid nature and velocity, age, etc.). 3.3. Operating experience: Review of national and international operating experience concerning the ageing issue, in particular the most significant events by which the issue was first identified and those contributing to the understanding of the phenomenon or to the assessment of the severity and extent of the issue. 3.4. Research Programs: Summary of past or ongoing research programs in this field (if any) and of the main results contributing to understanding the ageing phenomenon. 4. Problem significance: Explanation of why the ageing phenomenon affects the Belgian nuclear power plants or may affect them in the future. The following situations are examples of problem significance: • The phenomenon is already affecting one or more Belgian units • The phenomenon is affecting units whose design is close to that of a Belgian unit • The significant parameters of the Belgian units (e.g.: operating conditions, materials, type of equipment, age, etc.) are close to those of the affected units • The phenomenon affects a complete generation or family of NPPs 5. Risks 5.1. Technical/Safety risks: Lists the technical and safety-related risks. 6. Surveillance 6.1. Type of surveillance: Describes the surveillance activities (monitoring, NDE, analyses, etc.) required to reveal the phenomenon, to check its onset, its progress, to control the stressing factors, etc. Examples: • Management of the RPV surveillance capsules and associated predictive toughness calculations • In-service inspections of components and analyses • Transformer oil analyses • Monitoring of the packing weight in cooling towers • Etc. 6.2. Frequency: Specifies the surveillance frequencies. 7. Acceptance criteria: If acceptance criteria are applicable, this paragraph specifies criteria beyond which new surveillance or remedial actions must be considered. 8. Preventive and remedial actions 8.1. Preventive actions: Describes remedies aimed at preventing the onset, or mitigating the progress, of the ageing phenomenon (e.g. a change in operating conditions). 8.2. Repairs: Describes possible repairs, which may involve material removal or deposition, installation of reinforcements, thermal treatment, etc. 8.3. Replacement unchanged: Only in a limited number of situations can the replacement by a component of identical design be technically and economically justified, e.g.: • The existing component operated without significant problems for a period longer than the remaining life of the unit • Very slow progress of the ageing phenomenon combined with high cost and risk of the alternative new design • The ageing phenomenon can be prevented using new preventive / remedial actions 8.4. Replacement with redesign: Describes the items that must be (or have been) changed in the design of the component to prevent, mitigate or control the ageing phenomenon (material, geometry, welds, fabrication procedures, etc.). 8.5. Other remedies: Describes any other remedy which does not fit into the preceding categories. 9. Condition Assessment - Situation in the Belgian units: The following paragraphs are completed for each individual Belgian unit, as well as for generic activities common to all Belgian nuclear power plants. 9.1. All units 9.1.1. Present situation: Describes only the aspects that are common to all Belgian units. 9.1.2. Common recommendations: Only recommendations that generally apply to all units. Unit-specific recommendations are described in the following paragraphs. Recommendations are summarized in the Follow-Up Action (FUA) sheet, see section 5. 9.2. KCD1 (-2-3-4 & CNT1-2-3: 1 paragraph per unit) 9.2.1. Condition Assessment: Provides information on the current performance of the structure or component, including indications of material degradation or ageing related failures. 9.2.2. AMPs review: The effectiveness of the existing Ageing Summaries (or AMPs in IAEA language) should be periodically evaluated to update or adjust the program as necessary. The aspects to be considered include mainly information on the operation of the structure or component, maintenance and surveillance histories, but also international operating experience and results from research programs. Performance indicators that can be used depend on the structure or component but could be: • Trends of degradation data • Number of failures • Material condition with respect to acceptance criteria 9.2.3. Recommendations: This paragraph describes the specific recommendations for this unit to detect, monitor or mitigate the considered age-related degradation. Reference is made to specific reports dealing with the recommended strategies (repair-replacement studies, etc.). Recommendations are summarized in the Follow-Up Action (FUA) sheet. 10. Administrative information 10.1. Cognizant engineers 10.1.1. ENGIE Electrabel 10.1.2. ENGIE Tractebel, ENGIE Lab and others 10.2. Project references: List of all projects related to the management of the ageing phenomena for this SSC. Please note that for I&C systems, reports are established following a specific template and focus more on the obsolescence aspects (availability of spare parts, existence of the supplier, is the technology still supported, etc.).
BE-16 | 16 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 14 | 2.3.1: For the non-LTO units (NPPs) , limited tools and follow-up seem to be available for civil structures and passive components. Are those considered in the maintenance plans or in the health reporting? (the same assessment was more or less made by the regulator on page 38, but not included in the action plan on page 39) - Area for improvement |  | The AMP is very much living and is continuously improved (see also question 21). Regarding the passive components and civil structures, ENGIE Electrabel monitors their condition via the Ageing Summaries, the maintenance plan and the in-service inspection program. Finally, ENGIE Electrabel's overall ageing management program is in line with international standards, as stated on page 38 of the National Assessment Report. | Ref to BE-21
BE-17 | 17 | Concrete containment PCPV expert group | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 15 | 2.A.3.1.1 Do you plan to use Equipment Qualification program for concrete structures (containmnet) ? |  | According to the IAEA SRS3 document “the qualification of Piping, structures and other passive NPP components is achieved directly by design, construction, inspection and testing according to the applicable code”. In that sense, ENGIE Electrabel has no dedicated qualification program for its structures. The inspection of structures is done through the in-service inspection (ASME code) program and meets the current regulation as well as FANC expectations. In addition, structure repairs meet the applicable code requirements.
BE-18 | 18 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 15 | 2.3.1: The scope of the AMP (NPPs): the Eqfs are implemented for all active components with a mission time longer than 3 minutes. Could you explain where this limit originates from and what are the deadlines for implementation? |  | A distinction is made between the active components with: - Very short mission time (< 3 minutes) - Short mission time (< 96 hours) - Mid-term mission time (< 3 months) - Long-term mission time (< 1 year) For the active components with a very short mission time, the hypothesis is made that the time of exposure to the occurring harsh service conditions is not long enough to jeopardize the realization of the required safety function, as this takes place immediately after the postulated initiating event (PIE) started. Consequently, our special interest for this evaluation goes to the active mechanical components submitted to harsh service conditions with a short, medium and long-term mission time during the PIE. The EQF methodology developed by ENGIE Electrabel was evaluated and validated by the IAEA experts team during the Tihange 1 SALTO Follow-up mission of December 2016. The methodology was also evaluated and validated by the Belgian safety authorities. The deadlines are in accordance with PSR requirements, as agreed with the FANC.
BE-19 | 19 | Bulgaria | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 15 | It was written, that ENGIE Electrabel has installed temperature and humidity data loggers on various locations to verify whether the environmental conditions are still equivalent to the original design inputs. Should we consider that additional radiation exposure loggers were installed as well, where needed? |  | ENGIE Electrabel uses the walkdown measurements, as well as the permanent measurements to monitor the radiation doses.
BE-20 | 20 | Bulgaria | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 15 | It was written that “…. EQfs… This tool is new and still under development”. Would you please clarify when that EQfs tool will be developed, and what is the percentage (%) of covered mechanical equipment by that tool for each of the nuclear units at the moment of national report completion? |  | The development of the EQF tool is currently ongoing in the framework of the PSR action plan on all units (2012-2015) . The deadlines are in accordance with PSR requirements, as agreed with the FANC. For the LTO units, the EQF is finalized. For D3T2, it is almost fully completed and it is ongoing in D4T3.
BE-21 | 21 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 16 | The preventive maintenance activities have the appropriate frequency and extent to ensure that the levels of reliability and functionality of the plant’s safety-related SSCs remain in accordance with the design assumptions and intent - please clarify |  | Preventive maintenance activities are living. There are updates from R&D programs, international standards and guidelines, internal and external operating experience, feedback from the original equipment manufacturers, regulatory requirements, etc. For more detail, see chapters: - 2.A.3.2.2 Use of R&D programs - 2.A.3.2.3 Use of internal and external operating experience - 2.A.3.3 Monitoring, Testing, Sampling and Inspection Activities - 2.A.3.4 Preventive and Remedial Actions
BE-22 | 22 | Concrete containment PCPV expert group | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 17 | Regarding scope of SCC. What method is used to find non‐nuclear safety classified civil structure having an consequential risk to nuclear safety? |  | For the non-LTO units, the scope is largely based on expert judgement, driven by internal and external operating experience. For the LTO units, the scope is based on the identification of the passive and active SSCs that are in the scope of LTO according to the criteria set forth in 10 CFR 54.4.
BE-23 | 23 | Switzerland | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 17 | Why is the AMR for LTO units restricted to passive components? |  | In Belgium, both active and passive SSCs are subject to ageing management. The reliability of active SSCs is addressed through Reliability-Centred Maintenance (RCM), to ensure component reliability and include maintenance and testing surveillance activities. SSC performance is monitored through health reporting. This approach covers the main characteristics of the scoping, screening and review of potential failures considering internal and external operating experience. Finally this approach has been validated by FANC.
BE-24 | 24 | Slovenia | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 18 | Could you explain how design, manufacturing and operations documents were used during project phase of preparing Ageing management program (AMP), namely how plant specific data was taken into account as basis for the AMP project? |  | The design, manufacturing and operations documents are used appropriately in each step of developing the Ageing Management Program. For instance, all TLAAs that were part of the original design base were re-examined and renewed (if necessary) to cover the entire LTO period. ENGIE Electrabel also defined additional TLAAs based on international references, especially with regards to fatigue mechanisms. In the Ageing Management Program, acceptance criteria were based on the design, manufacturing and operations documents as well.
BE-25 | 25 | Switzerland | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 21 | Are specific acceptance criteria for ageing established and where are these criteria laid down? |  | Acceptance criteria have been defined and are covered in the Ageing Management Programs (AMPs) and in the Ageing Summaries (AS). They are monitored by the AS and AMP owners during the execution of on-site activities, such as for example the regular condition assessment of transformer and the analysis of lubricant oil circuits. In addition, plant-specific acceptance criteria are included in the plant’s operational procedures (maintenance procedure, periodical tests, etc.).
BE-26 | 26 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 22 | 2.3.2: The document does not really describe how ageing is identified, assessed or accepted (points b, c and d of §2.3.2 of the TS). Most probably this is done in the AMP's (LTO-units) or Ageing summaries (all units) and will be dealt with by the maintenance plans or the monitoring or testing, but this paragraph should be clarified. |  | Ageing deviations are identified through: • The inspection and maintenance activities defined in the ageing tools (e.g. AS, AMPs, RCM, EQf, TLAAs, etc.) • The surveillance program • The health reporting process Whenever an ageing deviation is observed, the deviation is evaluated by ageing experts and the required mitigating or corrective measures are defined and implemented (as defined in the ageing tools).
BE-27 | 27 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 22 | Based on the AMR analysis, ENGIE Electrabel has developed additional Specific AMPs for ageing degradation mechanisms not covered in the GALL. Which ones? |  | - Steam generators: RPV Nickel-Alloy bottom-mounted instrumentation nozzles and welds - Steam generators: Components other than tubes - Polymers: Elastomers and other synthetic materials - Internal structures program (Bâtiment Réacteur, BAN & ISBP, BAE) - FW line baffle boxes
BE-28 | 28 | Netherlands | Belgium | 03. Electrical cables | 22 | For unique cables (population is 1), sample size is 0. Do unique cables occur and if so, are these not tested periodically? |  | There are no unique cables with safety related functions.
BE-29 | 29 | Switzerland | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 22 | What kind of automatic monitoring equipment is installed in the Belgian NPP to systematically evaluate possible ageing effects? |  | The following automatic monitoring equipment exists: - AREVA’s FAMOS (Fatigue Monitoring System) installed on Doel 1 pressurizer (covering also the Doel 2 pressurizer) - LVMS (vibration monitoring system) - LLPMS (loose part monitoring system) - Transformer hydrant analyzers - Environmental monitoring (data logger) - Automatic process measurements are registered and interpreted as part of the health reporting process or by an automatic system
BE-30 | 30 | Czech Republic | Belgium | 03. Electrical cables | 24 | What cable measurement method gives you the best results (reflectomery test , insulation resistance test, tan δ test ) on nuclear power plants? |  | There is no single best technique to assess electrical cables. Therefore, ENGIE Electrabel prefers to evaluate the condition of these cables based on the results of a combination of tests.
BE-31 | 31 | United Kingdom | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 26 | Outages are described as a closed-loop processes that contribute to the continuous improvement of the AMP. They also provide an opportunity to monitor the effects of ageing. Please provide information on any ageing monitoring that is performed proactively during outages. |  | Ageing-related maintenance activities (as defined in the AS, AMPs, EQF, RSQs or RCM) are executed during outages, as well as in service. The choice is made based on the feasability of the activity. As stated on page 45: “In a similar way, feedback on works performed during the cyclic outages may lead to similar adaptations as for daily maintenance”. This means that the anomalies that are detected during preventive ageing-related inspection and maintenance activities, which have been executed during outages, are also reported and analyzed, and may typically lead to corrective actions such as adaptations to the maintenance plans, the maintenance strategy documents and the AMPs, or may initiate modification projects.
BE-32 | 32 | United Kingdom | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 26 | Section 2.A.4.3. refers to KPIs developed to monitor the progress of the AMP process. What parameters are monitored? |  | As explained in chapter ‘2.A.4.3 Licensee Self-assessments and Audits’, ENGIE Electrabel has developed KPIs to monitor the progress of the Ageing Management Program (AMP) processes. Three set of KPIs are monitored : KPIs from Health Reporting, KPIs from Ageing Summaries & KPIs from AMPs process for all units (Tihange 1-2-3 and Doel 1-2-3-4) The most important parameter to assess ageing management effectiveness is the systems or component status, which is monitored using health reports. The health report indicates a system’s or component condition based on a set of KPIs and the operational events that have occurred on this system or components during the period of analysis. Some examples of health report KPIs are: - The number of justifications for continued operation (JCO) - The number of observation files, the number of (unforeseen) unavailabilities of the system - A re-work analysis - The evolution of the leakage - Etc. Based on these KPIs, the system’s operational performance and their own expertise, the ENGIE Electrabel system experts assign a colour-coded health status to each system: - Green: System / components are reliable and operation parameters are stable. - White: System / component are considered to be reliable, but some parameters need specific attention or additional monitoring (e.g. action plan to green is performed, but some additional monitoring is needed to be sure that the situation remains stable). - Yellow: Availability and/or reliability of some components / systems is degraded as some operational parameters operate outside of their ‘normal’ band. They require specific attention and an action plan to ensure no punctual degradation could lead to partial or complete unavailability of the system’s function. - Red: Availability of the system is degraded - performance of the system is not acceptable. These circuits / components require a deep and quick action plan. ENGIE Electrabel also developed specific KPIs for the Ageing Summaries and AMPs: - Number of recommendations open, closed. - Rate of recommendations planned, in completion, completed or delayed. All those KPIs are implemented for all our NPPs.
BE-33 | 33 | Slovenia | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 29 | Gap Analysis GALL versus IGALL (Page 30): Have you implemented any changes to individual ageing management programs (AMPs) or resulting maintenance program also, based on the evaluation of changes, derived from the 2. revision of GALL report? Has also been GAP analysis made for GALL rev. 1 versus GALL rev.2? |  | ENGIE Electrabel did not perform any gap analysis between GALL rev 1 and GALL rev 2. However, ENGIE Electrabel did conduct a gap analysis between the IAEA’s IGALL and their AMPs in 2016. Currently, the AMPs are under review according to the IGALL guideline, following the prioritization that resulted from the 2016 analysis.
BE-34 | 34 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 30 | SALTO peer review missions were organized at Tihange 1 in January 2015 and at Doel 1&2 in 2017. The IAEA teams concluded that those plants have worked extensively in the field of LTO and ageing management. A follow-up mission was conducted for Tihange 1 in December 2016 and almost all issues were solved. Which ones remain to be solved? |  | For Tihange 1: all IAEA recommendations and suggestions have been solved or evaluated as 'sastisfactory progress to date' in 2016. For Doel 1&2: a SALTO follow-up mission is already planned in 2019.
BE-35 | 35 | Netherlands | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 30 | It would be interesting for other countries to name the additional AMPs that have to be developped. |  | ENGIE Electrabel is not developping new AMPs as the program is already completed. ENGIE Electrabel has developped new AMPs for the AMPs that were not exisiting in GALL documentation - please refer to question 27 for more information. | ref to BE-27
BE-36 | 36 | United Kingdom | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 30 | Section 2.A.5. discusses the licensee's experience of the application of the overall AMP. Although originating from a fabrication issue, did the discovery of hydrogen flakes at Doel and Tihange in 2012/2013 result in any changes to the overall AMP or any learning that was applicable to plant other than the RPV? |  | As explained in the Safety Case established by ENGIE Electrabel, there is scientific consensus on the fact that hydrogen flaking occurred during the construction of the forged pieces. The hydrogen flakes in the RPV of Doel 3 and Tihange 2 were not reported at the time of construction, but they have been identified and reported in 2012. Nevertheless, the forged pieces have been declared in conformity with the construction code after completion of the regulatory checks. ENGIE Electrabel is confident about the structural integrity of the RPVs of Doel 3 and Tihange 2 with significant safety margins. This conclusion is documented in detail in the safety cases submitted to the FANC, which served as a basis for the safety authorities for giving the green light after having passed on the files to world-renowned experts. When the decision was made to restart the two units, it was agreed to install an inspection program for both RPVs to be executed during future scheduled overhauls. The inspections that have been conducted since then, have shown and confirmed that the hydrogen flakes have not changed. Hence, it can be concluded, that their non-evolutive behavior has been demonstrated by the safety cases as well as successive inspections. As the hydrogen flakes in Tihange 2 and Doel 3 are not an ageing phenomenon, the overall AMP was not modified. Nevertheless, ENGIE Electrabel has taken this operating experience into account and took the decision to inspect the RPVs of all Belgian units (no hydrogen flakes were detected) and to re-inspect the RPVs of Tihange 2 and Doel 3 one cycle after both plants had been restarted. These re-inspections revealed no flakes growth and no new indications. Tihange 2 and Doel 3 will be re-inspected (via UT) every three cycles to confirm the stability of the hydrogen flakes.
BE-37 | 37 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 30 | According to the report, the flooding protection measures that have been taken following last PSR and the stress test evaluation will be integrated gradually in the Ageing Management Program. Given the fact that the stress tests were carried out in 2012, when will the flooding protection measures be fully integrated in the Ageing Management Program? |  | The BEST program is nearing its completion at Doel and Tihange. For both units, when the installation is commissioned and transfered to the O&M, the maintenance plans based on requirements from the original equipment manufacturers and regulation have been implemented and are executed.
BE-38 | 38 | Slovenia | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 31 | Description of the overall ageing management program (Page 34): When is going to be Ageing management program (AMP) implemented also for Doel 3,4 and Tihange 2,3? |  | Ageing Management Program of the nuclear NPPs is in line with with the prevailing regulations and FANC requirements : - The Ageing Management Program (AMP) for nuclear power units Doel 1&2 and Tihange 1 has been addressed in the framework of the Long-Term Operation Study Program. The AMP for these LTO units is in line with the FANC’s Strategic Note and follows the methodologies specified in 10 CFR 54, NUREG-1800 Rev.1 and NUREG-1801 Rev.1. This approach and the resulting lifetime extension of the nuclear power units Doel 1&2 and Tihange 1 has been endorsed by the IAEA during a Safety Aspects of Long Term Operation (SALTO) mission. - The ageing of the other Belgian nuclear power units (Doel 3&4 and Tihange 2&3) has been evaluated in the framework of the PSR Program and is in line with the prevailing regulations and FANC requirements. The AMP for these units is updated as part of the continuous improvement process and will be re-evaluated during the next PSR.
BE-39 | 39 | General AMP expert group | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 32 | At page 35 it is mentioned that the quality assurance aspects related to the scope of the AMP are not addressed in the section. ENGIE Electrabel has developed KPIs to monitor the progress of the AMP processes. Could ENGIE Electrabel provide us more information about the KI used? |  | As explained in chapter ‘2.A.4.3 Licensee Self-assessments and Audits’, ENGIE Electrabel has developed KPIs to monitor the progress of the Ageing Management Program (AMP) processes. Three set of KPIs are monitored : KPIs from Health Reporting, KPIs from Ageing Summaries & KPIs from AMPs process for all units (Tihange 1-2-3 and Doel 1-2-3-4) The most important parameter to assess ageing management effectiveness is the systems or component status, which is monitored using health reports. The health report indicates a system’s or component condition based on a set of KPIs and the operational events that have occurred on this system or components during the period of analysis. Some examples of health report KPIs are: - The number of justifications for continued operation (JCO) - The number of observation files, the number of (unforeseen) unavailabilities of the system - A re-work analysis - The evolution of the leakage - Etc. Based on these KPIs, the system’s operational performance and their own expertise, the ENGIE Electrabel system experts assign a colour-coded health status to each system: - Green: System / components are reliable and operation parameters are stable. - White: System / component are considered to be reliable, but some parameters need specific attention or additional monitoring (e.g. action plan to green is performed, but some additional monitoring is needed to be sure that the situation remains stable). - Yellow: Availability and/or reliability of some components / systems is degraded as some operational parameters operate outside of their ‘normal’ band. They require specific attention and an action plan to ensure no punctual degradation could lead to partial or complete unavailability of the system’s function. - Red: Availability of the system is degraded - performance of the system is not acceptable. These circuits / components require a deep and quick action plan. ENGIE Electrabel also developed specific KPIs for the Ageing Summaries and AMPs: - Number of recommendations open, closed. - Rate of recommendations planned, in completion, completed or delayed. All those KPIs are implemented for all our NPPs.
BE-40 | 40 | Switzerland | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 32 | According to topic 2.A.3.1.2 the AMPs for LTO units were upgraded. What are the consequences of this upgrade concerning the scope of the AMP? Is the scope of AMPs for LTO units extended in comparison to the scope of the actually implemented AMPs in the non-LTO units? How is the scope of the AMPs in the non-LTO units to be evaluated with respect to international IAEA guidance on ageing management in operation? |  | Ageing Management Program of the nuclear NPPs is in line with with the prevailing regulations and FANC requirements : - The Ageing Management Program (AMP) for nuclear power units Doel 1&2 and Tihange 1 has been addressed in the framework of the Long-Term Operation Study Program. The AMP for these LTO units is in line with the FANC’s Strategic Note and follows the methodologies specified in 10 CFR 54, NUREG-1800 Rev.1 and NUREG-1801 Rev.1. This approach and the resulting lifetime extension of the nuclear power units Doel 1&2 and Tihange 1 has been endorsed by the IAEA during a Safety Aspects of Long Term Operation (SALTO) mission. - The ageing of the other Belgian nuclear power units (Doel 3&4 and Tihange 2&3) has been evaluated in the framework of the PSR Program and is in line with the prevailing regulations and FANC requirements. The AMP for these units is updated as part of the continuous improvement process and will be re-evaluated during the next PSR.
BE-41 | 41 | Germany | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 34 | It is concluded that the overall ageing management programme is in line with international standards but that its effective implemenation on site is improveable. In this connection it is outlined that some past and recent events still highlight ageing issues and inadequate monitoring of the ageing of some components and that the licensee has taken some neccessary steps to tackle these points. Can Belgium provide some more specific information on this issue, please? |  | See question 12 and 172 and chapter ‘2.A.4 Review and Update of the Overall Ageing Management Program’ of the National Assessment Report. This chapter explains in which way ENGIE Electrabel continuously reviews and updates its overall Ageing Management Program according to the ‘PLAN-DO-CHECK-ACT’ cycle. Chapter ‘2.A.5.4 Enhanced Ownership and Integration by ENGIE Electrabel since 2017’ details how ENGIE Electrabel reorganized its Maintenance & Engineering Department to improve the effectiveness of the Ageing Management Program. In view of the recent events, ENGIE Electrabel acknowledges the need to improve the effectiveness of its concrete ageing management program. This improvement has already been launched in the frame work of its continuous improvement program. | ref to BE-12 & BE-172
BE-42 | 42 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 35 | On page 38, it is stated “that the overall ageing management program is in line with international standards but that its effective implementation on site is improvable by ENGIE Electrabel”. How can this situation still be ongoing as serious doubts persist in neighbouring regions regarding the reactors Tihange 2 and Doel 3? |  | The ageing management program of Doel 3&4 and Tihange 2&3 (and also Tihange 1 and Doel 12) has been evaluated in the framework of the PSR Program and is in line with the prevailing regulations and FANC requirements. The AMP for these units is updated as part of the continuous improvement process and will be re-evaluated during the next PSR. In addition, the Doel 3 and Tihange 2 RPVs’ fitness-for-service was demonstrated in the RPV Safety Cases, which have been validated by the FANC and the IRB. These Safety Cases also demonstrated the non-evolutive character of the hydrogen flakes, which have been detected in the two RPVs. Moreover (as explained under question 36), ENGIE Electrabel has taken measures to make sure that no new hydrogen flakes pop up and that the existing hydrogen flakes do not grow. These measures consist of periodic UT inspections of the core shell base metal.
BE-43 | 43 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 36 | Because of the natural continuation of the ageing process, issues which have occurred in the recent past appear likely to become more frequently, which is why the components responsible for those incidents are supposed to be checked in detail. Given that the current situation is insufficient to prevent incidents from happening, can it be sufficient to simply “enhance the follow-up” to prevent further incidents? |  | Yes, it is: • The Ageing Management Program (AMP) for nuclear power units Doel 1&2 and Tihange 1 has been addressed in the framework of the Long-Term Operation Study Program. The AMP for these LTO units is in line with the FANC’s Strategic Note and follows the methodologies specified in 10 CFR 54, NUREG-1800 Rev.1 and NUREG-1801 Rev.1. This approach and the resulting lifetime extension of the nuclear power units Doel 1&2 and Tihange 1 has been endorsed by the IAEA during a Safety Aspects of Long Term Operation (SALTO) mission. • The AMP of the other Belgian nuclear power units (Doel 3&4 and Tihange 2&3) has been evaluated in the framework of the PSR Program and is in line with the prevailing regulations and FANC requirements. The AMP for these units is updated as part of the continuous improvement process and will be re-evaluated during the next PSR. • See chapter ‘2.A.4 Review and Update of the Overall Ageing Management Program’ of the National Assessment Report. This chapter explains in which way ENGIE Electrabel continuously reviews and updates its overall Ageing Management Program according to the ‘PLAN-DO-CHECK-ACT’ cycle. Recent events, have been analysed and the necessaries actions & operating experience has been developped.
BE-44 | 44 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 36 | "The fire detection and firefighting equipment and the security system is not included in the BR2 AMP, since these assets are under responsibility of the department of health physics and safety. " IAEA sets up the scope as "SSCs that are credited in the safety analyses (deterministic and probabilistic) as performing the function of coping with certain types of events such as (i) Internal fires and flooding, ... to be clarified. |  | The fire detection and firefighting equipment is covered by a maintenance contract for the I&C and active components. These contracts are managed by the internal safety department, as they are applicable to the entire site. The passive components inside the BR2 buildings are within scope of the BR2 AMP and periodically inspected/tested under the BR2 operator’s AMP. The passive components outside the BR2 buildings are being upgraded as part of the site wide action resulting from the 2016 periodic safety reassessment. The interface between the two is periodically tested within the scope of the BR2 operator’s AMP.
BE-45 | 45 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 38 | 2.3.1: Scope of the overall AMP (BR2): it is not clear if the AMP takes (civil) structures or passive systems into account - to be clarified |  | The BR2 AMP scope includes the civil structures and passive components such as piping.
BE-46 | 46 | Netherlands | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 38 | 2.B.3.1 The Belgian report states fire detection and - fighting equipment is not part of the AMP because it falls under a different organization. Is there only an organisational reason to exclude it? And does it mean that ageing management is not applied to the particular equipment? |  | The fire detection and firefighting equipment is covered by a maintenance contract for the I&C and active components. These contracts are managed by the internal safety department, as they are applicable to the entire site. The passive components outside the BR2 buildings are being upgraded as part of the site wide action resulting from the 2016 periodic safety reassessment. The passive components inside the BR2 buildings are within scope of the BR2 AMP and periodically inspected/tested under the BR2 operator’s AMP. The interface between the two is periodically tested within the scope of the BR2 operator’s AMP.
BE-47 | 47 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 38 | 2.3.1: Scope of the overall AMP (BR2): has the (potential) impact of non-SSC's on SSC's been evaluated? (seismic, high energy line break,…) in the scope? |  | This point has been addressed in the Belgian stress test, following Fukushima Daiichi accident (Belgium extended the ENSREG stress tests to all nuclear installations of classe I). Seismic effect impact of non-safety related SSCs on safety related SSCs has been evaluated. High energy line break events are not applicable to an MTR such as BR2.
BE-48 | 48 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 41 | 2.3.1: Scope of the overall AMP (BR2): part of the WENRA TS has not been answered (the indicators used to assess the effectiveness of the process). Are those indicators non existing (yet)? or just not mentioned? |  | As the formal AMP is established recently, the available indicators do not yet allow trending. Trending is foreseen as input for the periodic revision of the AMP.
BE-49 | 49 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 41 | 2.3.2: Ageing assessment (BR2): How is the PF score (probability of failure) determined? Are environmental effects (such as vibration, chemical, corrosion, fatigue taken into account?) |  | There are several sources for PF scores applied - Supplier data - Integrity analysis using codes and standards - Data from the operator’s extensive database on maintenance and non-conformities - Expert judgement and external REX As appropriate, environmental effects are included in line with the requirements of IAEA safety guide SSG-10.
BE-50 | 50 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 41 | 2.3.3: Monitoring, testing and inspection: are civil structures taken into account? |  | Civil structures are in scope of the AMP and therefore a monitoring, testing and inspection plan is in place or being defined within the AMP.
BE-51 | 51 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 42 | 2.3.3: Monitoring, testing and inspection: How are environmental conditions (such as corrosion/erosion, vibration, leaks, fatigue) monitored? |  | Water conditions are permanently monitored on both primary as well as secondary side and pool water. All are demineralised water. Periodic inspection is part of AMP and verification of corrosion issues is included if appropriate (as identified in the ageing risk asssessment for the SSC in scope). Periodic vibration measurement is applied as appropriate from the ageing risk assessment of the SSC in scope. Continuous leak monitoring is applied for the primary loop and secondary loop. Periodic visual surveys are performed for leak detection (all areas are accessible at least monthly); automatic water detection is installed in some locations.
BE-52 | 52 | Netherlands | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 44 | 2.B.3.2 Return of experience. The return of experience from external sources is claimed to be very limited because of the unique design. However one could argue this claim is too pessimistic as it should be possible to exchange information about ageing management approaches, ageing phenomena, monitoring and inspection methods. Nothing can be found in the text about sharing information about problems with other countries of RRs e.g. through the IRSRR database. Please elaborate on that. |  | REX is systematically monitored from IRS database (both power as well as research reactors) and other sources. (Mostly qualitative) data are extracted as continuous safety improvement activity, with feedback to AMP if applicable.
BE-53 | 53 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 44 | 2.4: Review and update of the AMP: Since the program is very young, a revision frequency of 10 year seems very high. Based on the information given, it is not clear if a continuous improvement process is in place and if all processes (modification, OE, engineering, ...) take ageing into account |  | Full revision with a maximum period of 10 years is defined as a minimum. Continuous feedback from inspections, internal and external REX and the impact of modifications/renovations is taken into account in the AMP.
BE-54 | 54 | Netherlands | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 47 | 2.B.6 The main results of the BR2 IAEA mission should have been provided in the report, because they might be of interest to other countries, even if the final (version of the) mission report was not yet published. |  | The Belgian Safety Authority always publishes on its website the conclusions of an audit mission from IAEA when these are available. In november 2017, the main results of the IAEA BR2 mission were already published on the FANC website immediately after the end of the mission. The full report will be published in 2018. In the framework of the TPR, this was not requested within the technical specifications to expand on the review and conclusions from IAEA missions, whether on nuclear power plants or research reactors. The purpose is to conduct an independent self-assessment and not to resume external outputs on the subject. Nevertheless all recommendations and suggestions from the IAEA audit mission have been taken into account within the PSR action plan.
BE-55 | 55 | Cables expert group | Belgium | 03. Electrical cables | 47 | Could you please identify cables “important to safety” presenting risks of being potentially submitted to stagnant water in Belgian NPP ? (estimated length and main locations) |  | Cables are buried, typically when starting at buildings that are separated from the main buildings without any cable galleries connecting these buildings. The type and length of the cables can be found in the cable databases. As stated on page 54 of the National Assessment Report: Environments with stagnant water (i.e. zones with periodic exposure to humidity or water, for a period exceeding a few days) are considered as adverse environments. As stated on page 55: “If both the environment and the condition of the cable indicate that the cable could age prematurely, a representative number of cables is tested periodically, following the methodology stated in the EPRI guidance. If cable measurement results surpass a certain threshold, the cable will be replaced, safety-related or not.” These cables are included in the cable database.
BE-56 | 56 | Cables expert group | Belgium | 03. Electrical cables | 47 | Cable deposit have been installed only in 1993 in Doel 2 and in 2013 in Tihange 2. What are the environmental conditions for those deposits ,a and which acceptance criteria is complied with *(CM methods) |  | The cable deposits are located near the primary loop. The mean temperature is above 40°C. Radiation is above 10mSv/h. The acceptance criteria for elongation at break is 50% absolute.
BE-57 | 57 | Cables expert group | Belgium | 03. Electrical cables | 50 | Could you please indicate this design criteria (maximal conductor temperature) for each insulation material retained (PVC, EPR, XLPE, PRC, EPDM-EVA) ? |  | The cables are qualified based on a mean ambient temperature of 50°C in the reactor building and 30°C in other buildings. Maximum conductor temperature is 70°C for PVC cables, 80°C for XLPE and EPDM-EVA MV and I&C cables, and 90°C for EPR and XLPE HV cables.
BE-58 | 58 | Finland | Belgium | 03. Electrical cables | 51 | In chapter 3 the first sub header is surprisingly 3.A.1.1.2. Section headers 3.A.1., 3.A.1., 3.A.1.1 and 3.A.1.1.1 seem to be missing. Are there some tests missing in this part of the text? |  | Section headers 3.A.1., 3.A.1., 3.A.1.1 can be found on page 53. Section 3.A.1.1.1 can be found on page 54 to page 56.
BE-59 | 59 | Cables expert group | Belgium | 03. Electrical cables | 53 | The arrangements on the selection of cables to be tested are not entirely clear in the report. Could you please clarify how did you use the EPRI guidance on sampling and how did you increase the sampling? |  | The number of cables to test according to the EPRI criteria depends on the number of cables in a certain population. The population is based on the cable family, the environment and the condition of the cable. In some cases, sample size is increased based on engineering judgement. For other specific cable populations, such as the NIS cables, 100% of the population is tested due to the requirements specified in the safety report.
BE-60 | 60 | Germany | Belgium | 03. Electrical cables | 53 | On p.58 it is described how cable deposits were installed in Doel 2&3 and Tihange 2 in the years 1993/2013 which is after several years of operation. Were the cables used for those deposits extracted from the operating plant? If so, was it possible to use cables whose operational loading has both radiological and thermal loads of all cables in the respective ageing management group covered? |  | The cables used in Doel 2 were new cables from the warehouse. The cables used in Doel 3 and Tihange 2 were new cables which had been pre-aged (thermally, radiation).
BE-61 | 61 | Germany | Belgium | 03. Electrical cables | 54 | On p. 58 it is mentioned that at certain intervals cables are extracted and tested. Which tests are conducted and how often? |  | For the cable deposits of Doel 3 and Tihange 2, samples are extracted every five years of operation. Due to the units extended shutdown period, no sample extraction is foreseen in 2018. For the cable deposit of Doel 2, tests are foreseen in 2018, including materials tests (e.g. tensile testing, OIT, IR, etc.). The acceptance criteria for elongation at break is 50% absolute.
BE-62 | 62 | Germany | Belgium | 03. Electrical cables | 55 | In the NAR on p.58 it is mentioned that not all cable types are represented on those cable deposits. What was the reasoning behind the exclusion of some cable types? |  | First of all, cable deposit is not a requirement, but has been developped on volontary basis by ENGIE Electrabel to support its ageing management program of cable. ENGIE Electrabel decided to focus on the MV/I&C generation 3 and 4 cables which are mainly used in Tihange 3 and Doel 4, and which are used for cable replacement purposes in all other units. MV/I&C PVC cables are not used in harsh environments (1EA applications). The installation of a cable deposit and the information obtained from the lab analyses executed on cable deposits is used as complementary information to continuously increase our understanding of the degradation mechanisms of the cable types. The ageing management process described in the report is applicable for all cable families. Walk-downs and visual inspections of cables in adverse environments are performed from once every year to once every four years, depending on the environment and condition of the cables. If visual inspection is combined with cable testing, both results are taken into account to determine the cable’s condition.
BE-63 | 63 | Cables expert group | Belgium | 03. Electrical cables | 55 | References [10] and [11] are missing. Could you please define these references |  | [10] In-service inspection rules for mechanical equipment of PWR nuclear islands (RSE-M) Edition 1990 – Article B7213 [11] In-service inspection rules for mechanical equipment of PWR nuclear islands (RSE-M) Edition 2010 – article B6311-2
BE-64 | 64 | EC | Belgium | 03. Electrical cables | 58 | Why are there no cable deposits of generation 1 & 2 cables? |  | First of all, cable deposit is not a requirement, but has been developped on volontary basis by ENGIE Electrabel to support its ageing management program of cable. ENGIE Electrabel decided to focus on the MV/I&C generation 3 and 4 cables which are mainly used in Tihange 3 and Doel 4, and which are used for cable replacement purposes in all other units. MV/I&C PVC cables are not used in harsh environments (1EA applications). The installation of a cable deposit and the information obtained from the lab analyses executed on cable deposits is used as complementary information to continuously increase our understanding of the degradation mechanisms of the cable types. The ageing management process described in the report is applicable for all cable families. Walk-downs and visual inspections of cables in adverse environments are performed from once every year to once every four years, depending on the environment and condition of the cables. If visual inspection is combined with cable testing, both results are taken into account to determine the cable’s condition.
BE-65 | 65 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 03. Electrical cables | 58 | Why do the cable deposits only contain generation 3 and 4 MV and I&C cables even though those of generation 1 (the life span of 33 years having ended at the very latest 2010) are still installed in Tihange 1? |  | First of all, cable deposit is not a requirement, but has been developped on volontary basis by ENGIE Electrabel to support its ageing management program of cable. ENGIE Electrabel decided to focus on the MV/I&C generation 3 and 4 cables which are mainly used in Tihange 3 and Doel 4, and which are used for cable replacement purposes in all other units. MV/I&C PVC cables are not used in harsh environments (1EA applications). The installation of a cable deposit and the information obtained from the lab analyses executed on cable deposits is used as complementary information to continuously increase our understanding of the degradation mechanisms of the cable types. The ageing management process described in the report is applicable for all cable families. Walk-downs and visual inspections of cables in adverse environments are performed from once every year to once every four years, depending on the environment and condition of the cables. If visual inspection is combined with cable testing, both results are taken into account to determine the cable’s condition.
BE-66 | 66 | Poland | Belgium | 03. Electrical cables | 58 | Is it possible to determine the number of cables with PVC insulation? Is their total replacement planned? Please explain. |  | In the framework of the LTO of Doel 1&2 and Tihange 1 all PVC cables linked to 1EA equipment have been replaced. For the other plants no PVC cables were used for 1E application.
BE-67 | 67 | Bulgaria | Belgium | 03. Electrical cables | 58 | In the table, different cable groups with cable families with different insulation materials were presented. However, after that table we could not find expected ageing mechanisms, associated with different insulation coating/materials. Would you please clarify which mechanisms were considered? |  | The ageing mechanisms can differ, depending on the type of cables, the insulation and the jacket materials. Due to the variety of materials, ENGIE Electrabel has described the different ageing mechanisms in general terms instead of going into detail for each cable group and material.
BE-68 | 68 | Cables expert group | Belgium | 03. Electrical cables | 58 | GEN 1 and GEN2 MV/I&C cables seems not to be in cable deposit. What is the AM strategy for those cables? |  | The ageing management program described in the report is applicable for all cable families (GEN 1 & 2 MV/I&C included). Walk-downs and visual inspections of cables in adverse environments are performed from once every year to once every four years, depending on the environment and condition of the cables. If visual inspection is combined with cable testing, both results are taken into account to determine the cable’s condition. Finally, cable deposit is not a requirement, but has been developped on volontary basis by ENGIE Electrabel to support its ageing management program of cable.
BE-69 | 69 | Germany | Belgium | 03. Electrical cables | 58 | According to the tables on p. 59-60 PVC cables are used in Belgian plants. The list of ageing mechanisms on p. 61-62 doesn't mention PVC-specific effects like plasticizer diffusion and migration. To which extent PVC specific effects have been taken into account in the AMP of electric cables? |  | The effect of plasticizer diffusion and migration for PVC cables is a known ageing mechanisms, but not detailed in the report. There is no difference in the approach to follow up the cables of different generations.
BE-70 | 70 | Cables expert group | Belgium | 03. Electrical cables | 59 | The Table 3A-3 seems to indicate numerous connection families for each type of cable. Are all of those used on safety related cables in Belgian plants? if not which are used? Could you simplify this table by restricting it to connection types that are effectively used on Belgian NPP for cables “important to safety” ? |  | For safety-related HV cables, crimped and connected connections are used. For safety-related MV and I&C cables, all types of connections are used, depending on the application and size of the cable.
BE-71 | 71 | Germany | Belgium | 03. Electrical cables | 59 | On p. 61 IGALL AMP 206 is referenced in relation to the acceptable representative sample size for connections. It says there that 20% of the population without exceeding a maximum of 25 components is representative. What is the mathematical reasoning behind that? |  | The sample size is taken from the most recent version of IGALL's AMP 206, wich has been written and validated by international experts. The sample size has also been validated by the Belgian safety authorities.
BE-72 | 72 | Netherlands | Belgium | 03. Electrical cables | 59 | Section 3.A.1.2 describes the ageing mechanisms for each cable type of intrest. However, it is unclear which design, manufacturing and operations standards and documents are used for this assesment, and whether R&D programmes/operating experience is taken into account. |  | The process and procedures for the identification of ageing mechanisms are described in chapter 3.A.1.1.3 of the National Assessment Report. Cables are qualified according to IEEE 383. ENGIE Electrabel enhances its cable ageing management program based on the results of its annual cable R&D programs, on international operating experience and its return on experience from the field.
BE-73 | 73 | Cables expert group | Belgium | 03. Electrical cables | 59 | Are there any cables in conduits that makes them inaccessible? Which methods are used for evaluation of the degradation of those cables ? |  | There are no safety-related cables in conduits that are not accessible. However, there are buried safety-related cables which are inaccessible. Those cables are assessed using electrical tests, as detailed in the report.
BE-74 | 74 | Cables expert group | Belgium | 03. Electrical cables | 60 | Are the cables above 6 kV considered in the scope of AMP? |  | The 150kV cables are not in scope of the TPR. The Ageing Management Program for 150kV cables is described in a separate ageing summary.
BE-75 | 75 | Bulgaria | Belgium | 03. Electrical cables | 61 | Above photo from Tihange NPP is mentioned about “white deposit found on the terminations”. Would you please give more information about its origin? |  | The degradation is linked to the short distance or clearance between the conductor and the semiconductor, resulting in a disturbance of the electromagnetic field.
BE-76 | 76 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 03. Electrical cables | 61 | Concerning the white deposit found on the terminations of the Tihange NPP, which was not found at Doel, how many of those incidents were there? Does this mean the cable termination situation in Doel can be generally considered better than in Tihange? What direct consequences, apart from the replacement, have been taken? |  | This phenomenon was observed on approximately ten cables for which all terminations have been replaced preventively. There was no risk for nuclear safety. The cause of the degradation has been identified as a disturbance of the electromagnetic field caused by a short distance or clearance between the conductor and the semiconductor. The installation of new terminations resolved the cause of the degradation.
BE-77 | 77 | Czech Republic | Belgium | 03. Electrical cables | 62 | 3.A.4.3.1 "nevertheless, the kinetics of ageing of the jacket exposed to high temperatures or strong dose rates exceeds that of the insulation. A visual inspection of the jacket can therefore make it possible to anticipate any harmful ageing of the insulation". Does somebody test it? There are many examples with opposite ageing effect. Insulation was totally degraded, while jacket was in well condition. What does mean high temperatures or strong dose rates? |  | This is mainly valid for 380V and I&C cables where the degradation of the jacket is often an indicator for the degration of the insulation when the cable is subjected to external heat sources of radiation. For the 6kV cables, the insulation material is more subjected to electrical degradation. The jacket material can indeed be in perfect condition while the insulation material is degraded. The set of electrical tests (insulation resistance, tan delta test, ...), as described on pages 65-66, determines the condition of these cables. If the 6kV cable is positioned in an adverse environment and if any degradation of the jacket is visually detected, the cable will be prioritized in the electrical test program.
BE-78 | 78 | Netherlands | Belgium | 03. Electrical cables | 62 | In Section 3.A.1.3.1 it is stated that: 'the kinetics of ageing of the jacket exposed to high temperatures or strong dose rates exceeds that of the insulation. A visual inspection of the jacket can therefore make it possible to anticipate any harmful ageing of the insulation'. So for cables not exposed to high temperatures or strong doses visual inspection is intrinsically inconclusive? How does inspection work in this case? |  | See question 77. This is mainly valid for 380V and I&C cables where the degradation of the jacket is often an indicator for the degration of the insulation when the cable is subjected to external heat sources of radiation. For the 6kV cables, the insulation material is more subjected to electrical degradation. The jacket material can indeed be in perfect condition while the insulation material is degraded. The set of electrical tests (insulation resistance, tan delta test, ...), as described on pages 65-66, determines the condition of these cables. If the 6kV cable is positioned in an adverse environment and if any degradation of the jacket is visually detected, the cable will be prioritized in the electrical test program. | Ref to BE-77
BE-79 | 79 | EC | Belgium | 03. Electrical cables | 64 | In 3.A.1.3.3 NIS electrical cables, it is stated that "For the LTO units, projects have been launched and will be realized by the end of 2019". Could you please specify what are these projects? |  | The projects (planning included) have been defined and evaluated in the framework of LTO and PSR. All in agreement with the FANC. Resulting from the ongoing project, the replacement of a first part of the cables is already planned and a qualification program following the IEEE 383 standard is ongoing..
BE-80 | 80 | Switzerland | Belgium | 03. Electrical cables | 64 | Textline1: What was the reason for termination explosion? |  | The termination was analyzed in the lab. The cable was a tri-phase cable. The termination was exploded due to the presence of partial discharges at the location where the 3 phases split. The failure occurred between 2 phases at the point where the phases split. Since the presence of the partial discharges between the phases caused the failure, a TEV measurement campaign was launched to check if partial discharges were present as well on other installed terminations of the same type
BE-81 | 81 | Switzerland | Belgium | 03. Electrical cables | 64 | Textline33: What are the differences between generation 1 and 2 cables? |  | Please refer to Table 3A-2 in chapter '3.A.1.1.4 Grouping criteria for ageing management purposes – Electrical cables'.
BE-82 | 82 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 03. Electrical cables | 64 | The report states that in case of nuclear instrumentation (NIS) cables the functional checks mentioned by the licensee do not really allow assessing the condition of the cable and cannot be used to detect ageing degradations before the cables fail. It is further said that only one method of condition monitoring is used (i.e. insulation resistance measurement) for the NIS cables and the MV cables buried or in trenches at the Doel NPP. The Belgian Safety Authority recommends to investigate for MV and I&C cables whether the testing methodology can be extended with more quantitative condition assessment techniques. 1. Will the Belgian Safety Authority and the licensee consider carrying out other checks to be able to assess the condition of the cable and to detect ageing degradations at an early stage in the future? 2. Will the licensee follow the recommendation of the Belgian Safety Authority to extend testing methodology? If so, what quantitative condition assessment techniques will be used? |  | 1. Next to the insulation resistance test, different other tests are currently being carried out. The monitoring tests applied to the NIS cables are detailed on page 67. The Belgian Safety Authority considers that the actual test plans is sufficient to detect ageing degradations. 2. A research project is currently ongoing. A selection of cables is thermally aged in the laboratory. After several time intervals, a set of different electrical tests (TDR, FDR, IR, tan delta, etc.) and material tests (E@B, OIT, etc.) are performed to find a correlation between the condition of the cables and the electrical test results. Finally, the cable management program is evaluated in the framework of PSR (SF3-4).
BE-83 | 83 | Switzerland | Belgium | 04. Concealed pipework | 64 | Ref. 4H: What is the reason for use of NUREG 1801 Rev1 as opposed to the newer version Rev2? |  | At the time the LTO Study Program was developed, only NUREG 1801 rev1 was available. For the use of rev2, see Question 33. | ref to BE-33
BE-84 | 84 | Netherlands | Belgium | 04. Concealed pipework | 65 | Could you please provide the operational parameters and pipe diameters? Or could you clarify if in your case it is not important for the ageing assessment? |  | The pipe diameters are not relevant in the definition of our programs.
BE-85 | 85 | United Kingdom | Belgium | 04. Concealed pipework | 68 | Section 4.A.1.2.2 on fuel transfer pipes highlights external inspections undertaken as part of excavation activities. Are these inspections opportunistic, in conjunction with other activities, or is the sole purpose of the excavations for inspection purposes? The same comment applies to Section 4.A.1.2.3 and 4.A.1.2.4. |  | When excavation works are carried out in the framework of another maintenance plan or project we use the opportunity to inspect the (otherwise inaccessible) pipes. There are no buried fuel pipes at the Tihange nuclear power plant.
BE-86 | 86 | Slovenia | Belgium | 04. Concealed pipework | 70 | Section 4.A.1.2.2, page 81: Are the external inspections of buried fuel lines carried out periodically or just when other actions necessitate the excavation of buried pipes (i.e. opportunistically)? |  | Please refer to question 85. | ref to BE-85
BE-87 | 87 | Netherlands | Belgium | 04. Concealed pipework | 71 | How often are periodical testing, sampling and inspection activities performed for every pipework group? |  | Depending on the legal requierements, the period could range from once a month to once every ten years.
BE-88 | 88 | Concealed pipework expert group | Belgium | 04. Concealed pipework | 72 | 4.A.1.2.2 Fuel transfer pipes – “…the fuel transfer pipes and their connections are visually inspected during excavation works or opening of the trenches.” Please can you confirm whether the excavation and opening of trenches is part of a planned inspection program, or if it is carried out opportunistically as the trenches are open for other reasons? Same comment applies to fire water pipework inspections on page 82 and cooling water on page 84. |  | When excavation works are carried out in the framework of another maintenance plan, or project we use the opportunity to inspect the (otherwise inaccessible) pipes (see Question 85). | ref to BE-85
BE-89 | 89 | Switzerland | Belgium | 04. Concealed pipework | 77 | For the three types of pipework, visual inspection of the external surface is conducted during excavation. Have there been any such inspections to this date? If yes - what is the operating experience gained from those? |  | The LTO units have been subjected to inspections. For the non-LTO units, a comprehensive program is under construction. The tests and inspections already performed on buried pipes led to the replacement of the pipes for fire protection at the Tihange nuclear power plant. The same inspections at the Doel nuclear power plant led to the replacement of some part of the fire system. At both sites, the fuel pipe inspection program resulted in the replacement of some parts of the system. Resulting from Operating Experience, ENGIE Electrabel now uses GRE pipes for buried water pipes and Inox or double-wall pipes for fuel systems. In case of replacement by steel piping, cathodic protection is applied.
BE-90 | 90 | Germany | Belgium | 04. Concealed pipework | 79 | It is epxlained that fuel transfer pipes are checked for internal corrosion and fouling through fuel analysis and periodic inspections. Under the headline of periodic testing, next to functional tests of the diesel engines, monitoring of the fuel circuit through a "Health Reporting process" is mentioned. What kind of tests are performed in this process? How are these actions integrated into the AMP? |  | Periodic sampling provides assurance that fuel oil contaminants are below unacceptable levels. The plants subject the fuel to chemical tests to monitor the absence of material depositions, water, corrosion products, particulate contamination concentrations, etc. Morever, periodic cleaning of tank allows removal of sediments. During the diesel test, the absence of leakage is checked and the correct replenishment of the diesel's fuel tank is performed. All this is monitored by the System Engineer, who’s in charge of the diesel.
BE-91 | 91 | United Kingdom | Belgium | 04. Concealed pipework | 81 | Section 4.A.1.2.2 on fuel transfer pipes highlights periodic testing of the diesel engines as a way of confirming the suitability of the fuel pipework. What frequency of diesel engine testing is undertaken (e.g. monthly, bi-monthly, quarterly etc.)? In terms of the monitoring undertaken, what "main parameters" are monitored by Operations? |  | In accordance to the technical specifications, each diesel is started monthly. The tests are defined to verify the capability of the diesel to realize its function (time to start and connect, power, stability, loss of charge, etc.). According technical specifications, periodical specific long-term test (24h running) and a periodical complete loss of electrical power on the safety train are performed. During these tests, other parameters are monitored to verify the good health of the diesel and of its auxiliary equipment (exhaust temperature, etc.) including the diesel fuel system (pumps, flow, filling of the daily tank, pressure).
BE-92 | 92 | Concealed pipework expert group | Belgium | 04. Concealed pipework | 81 | The "corrective actions" section talks about improvements to carbon steel fuel pipework. What is the extent of the application of these techniques? Are they just to short sections around the failure or are more extensive repairs undertaken? How much single wall carbon steel fuel pipework remains? |  | The carbon steel fuel pipework was replaced. : - At the Doel nuclear power plant, only part of the system (the concealed part) was replaced., - At the Tihange nuclear power plant, almost the entire system was replaced.
BE-93 | 93 | Germany | Belgium | 04. Concealed pipework | 81 | Similar as for the fuel transfer pipes, for the fire water system, under the headline of periodic flushing and testing, monitoring of the fire water system through a "Health Reporting process" is mentioned. What kind of tests are performed in this process? How are these actions integrated into the AMP? |  | All units are subjected to a legally obliged test program to verify the availability of the fire extinguishing system. This program includes: test of pumps, flow, pressure drop in pressurizer tanks, comprehensive test of hydrants, etc. All these tests are monitored by the System Engineer in charge of the fire system. All these ageing related tests are included in the Ageing Summaries (for non-LTO units) and AMPs (for LTO units).
BE-94 | 94 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 04. Concealed pipework | 81 | Does the fact that the fire water circuit in Tihange is more prone to corrosion due to different purposes than in Doel lead to a different and more detailed way of controlling the condition of the fire water circuit at Tihange? What do these special controls consist of? |  | The characteristics of the river water used at the Tihange nuclear power plant are different compared to the water used at the Doel nuclear power plant. Due to these differences, the environnemental conditions are also different leading to slight differences in the Ageing Summaries and then specific control for each sites.
BE-95 | 95 | Poland | Belgium | 04. Concealed pipework | 81 | 1. How big is the number of local repairs in NPP pipes and pipelines? 2. What kind of alloy is used in NPP pipes and pipelines (quantitative)? |  | 1. The number of repairs remains limited and the main repairs are detailled withing the NAR 2. The materials of the concealed piping are provided in the table on page 79 of the Belgian NAR.
BE-96 | 96 | Germany | Belgium | 04. Concealed pipework | 81 | On the one hand periodic flushing of the fire water system appears to be a method to prevent fouling. On the other hand frequent use of the fire water circuit for other purposes in Tihange is considered a reason to be more prone to corrosion and in Doel 1&2 parts of the circuit were even replaced after excessive use. That appears contradictory. Could Belgium discuss its decission for flushing the fire water system to prevent fouling by accepting the disadvantages of corrosion? |  | Periodic flushing allows us to clean the pipes. In order to limit corrosion : - At the Tihange nuclear power plant, the fire pipes are now filled with treated water for normal use (equipment testing). In case of a real fire, water from the river can be used, but the pipes will be cleaned afterwards. - At the Doel nuclear power plant, town water or treated water is used.
BE-97 | 97 | Germany | Belgium | 04. Concealed pipework | 82 | Also for cooling water to safety-related SSC, under the headline of periodic testing and chemical analysis, monitoring of the cooling water system through a "Health Reporting process" is mentioned. Besides a MIC program is mentioned for Tihange. What kind of tests are performed in these processes? How are these actions integrated into the AMP? |  | For cooling water to safety-related SSC, at Tihange, the system concerned by buried piping contains river water. For that reason, a biocide is injected on a regular basis to prevent fouling. In addition, a MIC program using non-destructive techniques (e.g. UT) is applied to measure the pipe thickness, which can result in a replacement project depending on the results. For cooling water to safety-related SSC, at Doel 12 unit the system concerned by buried piping contains only town water which circulates in a closed loop. Thanks to the good quality of this water, no MIC is expected at Doel 1-2. For the both sites, a periodic performance test of the heat exchangers in the circuit indicates the degree of fouling.
BE-98 | 98 | Concealed pipework expert group | Belgium | 04. Concealed pipework | 82 | Please can you provide some detail of the ongoing strategy to manage the integrity of the glass-reinforced epoxy fire water pipework installed at Tihange 2 and 3 between 2012-2016, please include any inspection requirements that have been identified. |  | ENGIE Electrabel conducts visual inspection on the exterior surface of the piping whenever the external surface is made accessible. When significant indications are observed, ENGIE Electrabel carry out a Shore Hardness D measurement following the test method described in ASTM D2240.
BE-99 | 99 | Concealed pipework expert group | Belgium | 04. Concealed pipework | 83 | The integrity management of pipework associated with the BR2 research reactor appear previously to be based upon responding to leaks, rather than a pro-active approach based upon risk and the relevant ageing mechanisms. I note that the regulator’s assessment identifies a number of areas for improvements within an action plan. Please can you provide some detail on the progress that has been made against the action plan? |  | The Belgian Safety Authority requests the licensees to take the necessary actions to fill the gaps identified, either during their own self-assessments or by the Safety Authority. Since the publication of the NAR, an action plan has been established by the licensee SCK CEN, proposed to and accepted by the Belgian Safety Authority (through some minor amendments). The deadlines have been discussed and accepted by the Belgian Safety Authority. These deadlines are in line with the PSR implementation phase extended to 2019. So, all gaps have been adressed and will be fulfilled by 2019.
BE-100 | 100 | EC | Belgium | 04. Concealed pipework | 83 | BR2: What is the material and design for the city water piping, feed water line for fire fighting and feed line for cooling water from the lagoon (carbon steel with protective coating on outer surface?) ? |  | City water piping is constructed in carbon steel and HDPE (recent renovations). Firefighting water piping is constructed in galvanised carbon steel. Lagoon feedwater is constructed in HDPE. All systems are low pressure-low temperature systems.
BE-101 | 101 | Germany | Belgium | 04. Concealed pipework | 83 | The transfer piping for pool water is placed in a concrete cellar and was so far considered as concealed piping. Due to a "design change" it is no longer considered as concealed. What has really changed for this piping? |  | The cellar is readily accessible for inspection of the piping in the new design. The piping is now fully accessible for inspection. Previously, the piping was buried in the soil. The material has been modified from carbon steel with ebonite protection coating to stainless steel.
BE-102 | 102 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 83 | Q3 : How often is the structural integrity of RPV’s assessed based on the periodic results of the surveillance program ? |  | The structural integrity of the RPV is assessed based on the (upper bound) trend curve of RTNDT vs. fluence. The results of the surveillance program are only used to confirm the conservativeness of the trend curve but are not used directly in the structural integrity analysis. The evaluation was performed at each surveillance capsule withdrawal (schedule is unit-specific).
BE-103 | 103 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 84 | Q5 : A vast R&D program has been carried out in Belgium on the surveillance program. A reconstitution technique to obtain new Charpy-V specimens by welding extension pieces to the broken half-Charpy-V specimen was developed as well as techniques on miniature specimens. Are those techniques used for Belgian reactors ? |  | Yes, these techniques are used routinely in the "enhanced surveillance" approach, in particular to perform fracture toughness tests on reconstituted pre-cracked Charpy-size specimens tested in three-point bending (in view of Master Curve T0 evaluation)
BE-104 | 104 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 84 | Q6 : What is the consistency of those techniques against the samples used for the surveillance program by comparing the results obtained by the different methods ? |  | The reconstitution process was extensively qualified in the 1980s-1990s, including through participation to international programs (e.g. RESQUE). There is no difference between the Charpy transition curves obtained from original or reconstituted specimens as long as some rules of good practice are respected. Miniature specimens are mainly used for tensile testing to obtain tensile data in an extended temperature range.
BE-105 | 105 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 88 | Q7 : Another way to mitigate the risk of irradiation embrittlement is to make use of neutron absorber rods made with Hafnium, for example. Do you make use of such neutron absorber rods made with Hafnium in Belgian reactors to decrease the neutron flux ? |  | No
BE-106 | 106 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 89 | Q9 : Are loads due to seism taken into account ? |  | They were taken into account at the design stage and in any re-evaluation according to the requirements of the ASME Code.
BE-107 | 107 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 90 | Q11 : At certain parts, the usage factor used to evaluate the risk of low cycle fatigue is close to 1, such as at the RPV studs. Is a non-destructive examination performed on certain parts of the RPV (studs, upper head penetrations) in order to check the absence of flaw which could be caused by low cycle fatigue, under the defence-in-depth approach ? |  | The RPV studs are periodically inspected as part of the in-service inspection program required by the ASME Code. For the upper head penetration, there is an enhanced inspection program for those units that still have penetrations in alloy 600, due to the risk of PWSCC.
BE-108 | 108 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 95 | Q13 : The degradation mechanisms caused by PWSCC is mentioned concerning the effect on BMI nozzles and upper head penetration. Are there other parts of RPV which can be concerned by PWSCC than BMI nozzles and upper head penetrations, such as reactor vessel radial keys, claddings, repaired parts with alloy 182? |  | There are dissimilar metal welds in nickel-based alloy between the RPV nozzles and the safe-ends at the Tihange 2&3 and the Doel 3&4 nuclear power plants. These locations are submitted to an enhanced inspection program.
BE-109 | 109 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 95 | Q16 : Why do the licensees not consider the criteria of RCC-M code on thermal ageing of low alloy steel, in terms of RTNDT shift, in case of a detected flaw ? |  | The applicable code in Belgium is the ASME Code, which does not have thermal ageing criteria. Furthermore, investigations performed on the thermal ageing of low-alloy steel at RPV operating temperature have not shown any evidence of a significant thermal ageing effect.
BE-110 | 110 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 95 | Q18 : Certain parts of the BR2 research reactor are made of stainless steel (top and bottom covers of the pressure vessel) and others made of aluminium alloy (shells). How galvanic corrosion is mitigated between aluminium and stainless steel parts ? Are there any specific arrangements of ISI for this damage ? |  | NA
BE-111 | 111 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 95 | - Is water chemistry monitoring part of the AMP? |  | Yes it is integrated in the AMP and in the operational procedures. The water chemistry monitoring program in all Belgian units is in line with EPRI recommendations.
BE-112 | 112 | EC | Belgium | 05. Reactor Pressure Vessels | 95 | It is mentioned "In this respect, it must be mentioned that hydrogen flakes are not an ageing mechanism but fabrication phenomena". Comment: That is true, but there is not significant experimental data on the possible evolution of hydrogen flakes with time or irradiation. This is one of the reasons to require performing regular re-inspections of reactor pressure vessel. |  | When the decision was made to restart the two units, it was agreed to install an inspection program for both RPVs to be executed during future scheduled overhauls. The inspections that have been conducted since then, have shown and confirmed that the hydrogen flakes have not changed. Hence, it can be concluded, that their non-evolutive behavior has been demonstrated by the safety cases as well as successive inspections.
BE-113 | 113 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 95 | - Page 97: ASME BPVC requirements are applied for in-service inspection of RPV. Is EQB qualified per ASME requirements? |  | The qualification process of the in-service inspections techniques used in Belgium is not based on the ASME VIII methodology but on the European methodology developed by the ENIQ network (European Network for Inspection & Qualification). The qualification is managed by the Electrabel Qualification Body (EQB) and submitted to approval of the Authorized Inspection Agency (AIA) and Authorized Nuclear Agency (ANA). EQB operates in conformity with the quality assurance rules requested on international stage for such an organization but does not come within the framework of an external accreditation system. EQB operates in conformity with the confidentiality and independence rules recognized on international stage for such an organization. It renders its decisions completely independently from its ordering parties and from any commercial consideration.
BE-114 | 114 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 95 | - Page 98: Is atmospheric corrosion evaluated and/or monitored on the outside surfaces of dissimilar metals welds? |  | There is no known issue of atmospheric corrosion in the reactor building . In addition, the nickel-based dissimilar metal welds are not susceptible to atmospheric corrosion.
BE-115 | 115 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 95 | - Page 98: What are the operating conditions and which parts of the RPV have operating temperatures higher than 300oC that could be affected by thermal aging? |  | The outlet nozzles are exposed to higher temperatures (maximum 329°C at Tihange 3 and Doel 4) and the RPV heads can also be exposed to temperatures > 300°C. There is no evidence of thermal ageing of low alloy steels at such temperatures and no requirements to consider thermal ageing in the ASME Code.
BE-116 | 116 | Slovenia | Belgium | 05. Reactor Pressure Vessels | 95 | Reactor pressure vessels, surveillance programs (page 99): Is the ex-vessel dosimetry used to validate the information on RPV irradiation embrittlement gather from surveillance capsules? |  | Yes, at Doel 1&2, the external dosimetry is part of the AMP for the LTO period to validate the fluence analyses since all surveillance capsules have been withdrawn.
BE-117 | 117 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 95 | - Page 99: Are the surveillance specimens manufactured at the time of RPV manufacturing? If not, how is qualification ensured? |  | They were manufactured at the time of RPV manufacturing and have been taken in overlength of the core shells or in a representative weld coupon (welded using the same procedure and products as the RPV welds).
BE-118 | 118 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 97 | - Page 99: What regions of RPV metal do the specimens cover (base metal, weld metal, HAZ, etc.)? |  | Base metal of the two core shells (except at Tihange 2 and Doel 3: only the core shell with the most sensitive composition), weld and HAZ (and a correlation monitor at Doel 1&2 and Tihange 1),
BE-119 | 119 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 97 | Q1 : Page 100 of the NAR, there is a vast amount of internal operating experience in Belgium since a total of 35 surveillance capsules out of the 36 initially present in the seven Belgian reactors have been withdrawn and tested. Our understanding is that it remains a single capsule for the last years of service for all the reactors. Could you explain on which elements is based the representativeness of this single capsule, knowing that its aim shall be to provide the RTNDT shift for the last years of service life of all Belgian reactors ? |  | Each RPV has its own surveillance program. Since all the original capsules have been withdrawn and evaluated (except for the one remaining at Tihange 1), we have experimental results for fluences well above those corresponding to 40 years of operation (in most cases up to 60 years equivalent or more). The last few years, two spare capsules were introduced at Tihange 2&3 and Tihange 3&4 in case of potential extended operation of these units. Please note also that each RPV surveillance program is designed specific for a given RPV. It contains specimens of the components of this specific RPV, taken during fabrication, and cannot be transposed to another RPV. In Belgium ENGIE Electrabel nevertheless compare systematically the results of Tihange 2 and Doel 3 on the one hand, and Tihange 3 and Doel 4 on the other hand, because these RPVs were manufactured by the same suppliers and with very similar materials, which gives an additional confidence in the results (an anomalous result would stand out more clearly). This is also the case for Doel 1 and 2. From a regulatory point of view, the surveillance program is evaluated for a given unit based on the capsules for this unit. For all Belgian units we have surveillance results corresponding to more of 40 years of operation for the vessel (in most cases up to 60-80 years).
BE-120 | 120 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 98 | Q2 : Page 100 of the NAR, the irradiation embrittlement effect is predicted in terms of RTNDT shift by conducting a testing program (Charpy-V and tensile specimens) on surveillance capsules. Is the RTNDT shift periodically calculated considering the last test results from the surveillance program ? |  | Yes, each time a surveillance capsule is withdrawn and tested the results are compared to the predictive trend curve (RTNDT vs. fluence) to confirm that this trend curve is still conservative.
BE-121 | 121 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 98 | - Page 100: How many capsules each RPV has at the beginning of life? |  | - Doel 1&2: six - Tihange 1: eight - Tihange 2&3 and Doel 3&4: four (+ two spares introduced a few years ago)
BE-122 | 122 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 99 | Q8 : Transients – Page 101, the PTS transient taken into account to define the RTNDT limit values for the acceptability of the risk of vessel failure is characterized by an initial rapid cooldown initiated for example by a safety injection following a small break loss of coolant accident. Could you provide the characteristics (pression, temperature) of this PTS event which helped defining the RTNDT limit values of 132°C for base materials and axial welds and 149°C for circumferential welds ? |  | The PTS criterion of the 10 CFR50.61 is not based on a deterministic analysis of a specific transient but results from a probabilistic analysis. No PTS analysis is required as long as RTNDT < 132°C for forgings and < 149°C for welds.
BE-123 | 123 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 99 | Q10 : Strain Ageing and thermal ageing - Page 101, in irradiated condition, the RTNDT is defined as the initial value plus the shift under irradiation measured by the shift of the Charpy-V curves at the 41J level. In fracture mechanical evaluation, is the shift of RTNDT due to strain ageing taken into account as well as the shift of RTNDT under irradiation? |  | The ASME Code and U.S. rules applied in Belgium do not require considering effects of thermal ageing or strain ageing.
BE-124 | 124 | Slovenia | Belgium | 05. Reactor Pressure Vessels | 99 | Hydrogen flaking (page 102): Could you please explain how the RSE -M trend curve change/influenced on the pT operating curves. |  | The hydrogen flaking issue led to consider an increased embrittlement, i.e. a higher RTNDT shift to consider in the determination of the new pT operating curves. The use of the more recent RSE-M trend curve instead of the previously used FIS formula does not have a significant impact in the fluence range of interest
BE-125 | 125 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 100 | Q4 : Page 102, the structural integrity is checked in presence of the postulated reference crack. What are the dimensions of the postulated reference crack ? |  | The dimensions correspond to the ones of the ASME Appendix G: For section thicknesses of 4 in. to 12 in. (100 mm to 300 mm), the postulated defects have a depth of one-fourth of the section thickness and a length of 1.5 times the section thickness.
BE-126 | 126 | Slovenia | Belgium | 05. Reactor Pressure Vessels | 100 | Low leakage core loading patterns (page 103): When are the low leakage core loading patterns introduced for Doel and Tihange units and how much is projected fluences consequently lower than those originally specified? |  | Low leakage core loading patterns were introduced at variable dates depending on the units , generally around the first decennial revision. The comparison with the original fluence estimates is not relevant (especially for the oldest units) considering the limited reliability of fluence analysis techniques at the time of design of these units. The fluence reduction compared to a standard loading pattern can be estimated as of the order of 15%.
BE-127 | 127 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 100 | - Page 103: Low-cycle fatigue. Does the assessment take into account identified underclad defects? |  | There are no identified underclad defects in the core shells of the belgian RPVs. Low-cycle fatigue crack propagation is considered for all indications detected in in-service inspections, according to ASME Code requirrements.
BE-128 | 128 | EC | Belgium | 05. Reactor Pressure Vessels | 101 | It is mentioned "Low leakage core loading patterns are used in all units in order to limit the fluence on the vessel wall as much as possible considering the other constraints on the loading pattern." Comment: Really low leakage core strategy is used to enhance fuel economy. As secondary, one of the benefits of low leakage core is a reduction of the neutron flux on the vessel wall. |  | Thanks for the comment.
BE-129 | 129 | Germany | Belgium | 05. Reactor Pressure Vessels | 101 | The influence of the invironment on fatigue usage factors (CUF) is considered for the units in LTO (Doel-1, -2, Tihange-1) according to the U.S. approach. As mentioned earlier, the highest CUF in the RPV are reached in the bolts and the junction between the upper head flange and the dome. Yet, this junction is not considered when concluding that there is practically no impact of the environment on the CUF in all parts of the vessel. Could this be explained? |  | The junction between upper head flange and dome is protected by a stainless steel cladding and is not exposed to the primary environment. In general for clad components the LWR environment effect on their fatigue life was addressed by demonstrating that the fatigue life of the cladding is longer than 50 years and hence there is no environmental effect on the underlying base material. The bolts and nuts are only exposed to air environment.
BE-130 | 130 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 102 | Q12 : Page 106, UT inspection of the RPV beltline were performed on the seven Belgian reactors from 2012, in order to detect underclad defects. Were the UT qualified to detect underclad defects and what were the performances compared to the largest possible underclad defects (12.5 mm deep semi-elliptical defect) ? |  | Yes, the UT was qualified and detection of a 5mm deep flaw was guaranteed
BE-131 | 131 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 05. Reactor Pressure Vessels | 102 | The situation of the primary water stress corrosion cracking of the BMI penetrations of Tihange 1 is deemed acceptable for 3 years. What are the specific adaptions planned to be implemented into the AMP as a consequence? |  | A re-inspection is already planned.
BE-132 | 132 | Germany | Belgium | 05. Reactor Pressure Vessels | 103 | Several indications were found during inspections of the Bottom Mounted Instrumentation (BMI) nozzles in Doel-1 made of Alloy 600. These indications were justified for at least ten years of operation. Were these indications likely to be due to PWSCC? If yes, how could these indications be justified for such a long period? |  | They are considered to most likely being scratches from fabrication. When they are justified by analysis this is based on the local stress state (including residual stresses) and the recognized disposition curves for PWSCC crack growth.
BE-133 | 133 | Germany | Belgium | 05. Reactor Pressure Vessels | 103 | The RPV upper head of Doel-1 was repaired 2005 due to PWSCC of penetrations made of Alloy 600 and their welds. New cracks and an evolution of existing cracks were found since 2012. How could new inspections using the most advanced inspection techniques demonstrate the safety of the RPV after new repairs planned for 2018 will have been performed? |  | The inspection techniques are qualified and will continue to be applied after the repair
BE-134 | 134 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 05. Reactor Pressure Vessels | 103 | Page 113 of the report describes what is being referred to as “French illness”, the appearance of cracks and leaks on reactor pressure vessel heads. It is mentioned that Belgian plants were also affected by these material defects and reparatory measures were taken consequently. It is stated that the RPV head of Doel 1 was repaired in 2005 and planned to be repaired again in 2018 as new cracks and an evolution of existing cracks have been detected in some penetrations since 2012. In contrast, the RPVs of Tihange 3 and Doel 4 were replaced preventively even if no cracking has been detected, international experience shows that there is a possibility that these heads could also experience cracking in the coming years. 1. When exactly is the RPV of Doel 1 scheduled for reparation this year? 2. Why is the RPV of Doel 1, where existing cracks have further evolved since 2012, not replaced - as has been done with Tihange 3 and Doel 4? According to the report the nuclear power plants Doel 1&2 as well as Tihange 3 and Doel 4 are all in the high susceptibility category. |  | The foundation of the LTO of Doel 1&2 is the summary report dated April 2015, which has been approved by the FANC and is available to the general public online. This report indicates that the decision to replace the RPV heads at Doel 1&2 will be assessed in line with an extensive inspection program rolled out before service life is extended. This inspection program, which uses cutting-edge measurement technologies, has since demonstrated that safety is guaranteed by performing repairs using a technique that has been applied successfully on several RPV heads around the world. This procedure is subject to a safety study, assessed and approved by international experts and Bel V. The Doel 1 repair will be foreseen during the scheduled outage of May-October 2018 in agreement with the FANC and BEL V.
BE-135 | 135 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 104 | Q14 : Page 119, the phosphorus contents of the materials in the Belgian units are generally low. What is the phosphorus content range for the different components which compose the Belgian RPV? |  | The phosphorous content of the Belgian RPV materials is below 0.015% for base materials (below 0.012% in most cases) and slightly higher (up to 0.015-0.017%) for the welds.
BE-136 | 136 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 105 | Q15 : Page 119, regarding the RPV beltline region, the surveillance capsule specimens are exposed to the same temperature as vessel wall and thermal ageing contribution is included in the post-irradiation testing results. What about the effect of thermal ageing on other components than RPV beltline region and specially what is the impact of a flaw outside the beltline region ? |  | The ASME Code does not consider any thermal ageing effect on low-alloy steels at RPV operating temperatures.
BE-137 | 137 | United Kingdom | Belgium | 05. Reactor Pressure Vessels | 106 | "Section 5.A.1.2.8 Thermal ageing of low alloy steel - There is no acceptance criteria for thermal ageing, as it is not mentioned in the ASME code. Are you developing an acceptance criteria for thermal ageing?" |  | No. There is no scientific evidence of significant thermal ageing on low-alloy RPV steel at RPV operating temperature.
BE-138 | 138 | Slovenia | Belgium | 05. Reactor Pressure Vessels | 111 | Safety injection water preheating (page 122): What is the temperature of the preheating water and how is boron concentration managed at that temperature? |  | The SI water is preheated to 45°C in Doel 3 and 35°C in Doel 1-2 and the boron concentration is kept between 2400 and 2600 ppm. Besides that, the temperature has no influence on the boron concentration management as long as it is high enough to ensure that all the boric acid is in solution.
BE-139 | 139 | RPV expert group | Belgium | 05. Reactor Pressure Vessels | 112 | Q17 : Page 122, the remaining flakes were analyzed in detail using advanced finite element and fracture mechanics techniques to justify that they respected the ASME XI criteria. In the fracture mechanics techniques, did hot as well as cold transients studied, especially because some flakes are located deeper in the vessel wall ? |  | Yes, all types of transients of the design files have been considered.
BE-140 | 140 | Finland | Belgium | 05. Reactor Pressure Vessels | 113 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? |  | We are not sure whether we've understood the question correctly. The main safety and operational challenges associated with the RPV AMPs are related to the potential presence of flaws (either pre-existing or appearing by PWSCC of Nickel-based materials) and are addressed by in-service inspections (as required by ASME Code or according to enhanced programs for sensitive locations). We do not see any impact of safe shutdown conditions on the AMPs. Please clarify the question.
BE-141 | 141 | EC | Belgium | 05. Reactor Pressure Vessels | 113 | It is mentioned "The quality of the vessel wall welds will be better than those of the shroud". Comment: It would be better to say that the quality of the vessel wall welds is expected to be better than that of the shroud. |  | Thanks for the comment. This proposition will be evaluated in case of revision of the National Report
BE-142 | 142 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 119 | In accordance with Technical Specification for chapter 7.1.1, can you describe the main concrete structural elements and add principles drawing? |  | The information is not made public but is available at the FANC as part of the licensee contribution to the National Assessment Report.
BE-143 | 143 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 119 | Does the report include the concrete structures inside the containment, the roof, the concrete foundation or only the walls? |  | The licensee contribution to the National Assessment Report is available at the FANC and includes the walls, the roofs and the concrete foundation. It does not include the internal structures inside the containment. However, reference to page 119 is not clear.
BE-144 | 144 | Germany | Belgium | 07. Concrete containment structures | 120 | Nothing is indicated in the chapter on concrete containment strucutres with regard to the inaccessible areas. How the ageing management programs are applied for these areas? What the procedures are used to evaluate the ageing phenomena in inaccessible areas? |  | Inaccessible areas are the outer surface of the secondary concrete containment walls under the ground and the bottom surface of the raft foundation. Surveillance of these areas is done by checking the leak tightness of the structures.
BE-145 | 145 | Netherlands | Belgium | 07. Concrete containment structures | 122 | Settlements: are there only guides for settlements and settlement differences or are there also guides for (tolerances of) angular distortion between components. |  | The concrete double containment of the reactor building has such a rigidity that distortion between components is not to be considered.
BE-146 | 146 | EC | Belgium | 07. Concrete containment structures | 122 | The report indicates that the containment metal liner is inspected only every ten year. However, operating experience show cases of corrosion or damage to containment liners that led to loss of containment leak tightness between two pressure tests. Therefore, inspecting the liner only every ten years seems not enough and it is suggested to perform at least an intermediate visual inspection of the liner. |  | As required by ASME code, the thorough inspection of the full liner is completed in ten years. Inspectors are present during every outage, and potential leak tightness might be observed during these outages.
BE-147 | 147 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 123 | 7.A.1.1.2 (Table 7A-1) Have ILRT been performed only for Doel 3 ? How are the tendons tested in Tiihange 1 ? |  | The table could be clarified. The ILRT are performed on Doel 3, Doel 4, Tihange 1, Tihange 2 and Tihange 3. The test of the tendons is performed every six months (operational test of extensometers).
BE-148 | 148 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 132 | 7.A.1.1.2 (Table 7A-1) What justifies the 10-year time interval of liner inspection and of ILRT ? How did the 5 year lift-of testing period be based on intensive theoretical and experimantal work (described in p.138) ? |  | See chapter 7.A.1.3.1 Frequency of inspections
BE-149 | 149 | Switzerland | Belgium | 07. Concrete containment structures | 137 | Are there permanent monitoring systems installed for the surveillance of the containment and, if yes, how is the experience with these systems (e.g. long-term behavior) ? |  | The monitoring is not permanent. However, the extensometers for surveillance of the post-tensioning are permanently installed. Experience shows that they are globally reliable. The technology has evolved, and ENGIE Electrabel has launched the enhancing of the old surveillance systems.
BE-150 | 150 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 137 | 7.A.1.2.2 A detailed description of ageing mechanisms can be found in IAEA documents. Do you think that this general is sufficient and no possible any additional mechanisms ? |  | Ageing mechanisme are based on the combination of environment & material, in our case we use GALL for the units of Doel 12 and Tihange 1. AMPs are developped to manage the ageing mechanisme. Additional mechanisms can be described in the relevant AMPs developed by the Licensees, and additional (specific) AMPs can be defined by the licensees (please refer to question 27). | ref to BE-27
BE-151 | 151 | Switzerland | Belgium | 07. Concrete containment structures | 137 | How are acceptance criteria for the inspected concrete structures defined? Which are exemplary acceptance criteria? Are there target condition levels defined? |  | See chapter 7.A.1.2.3 Acceptance criteria
BE-152 | 152 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 137 | 7.A.1.2.3 It is important to state that the final decision about the acceptability of observed defects is the responsibility of the engineer in charge. Do I understand well, that there is no clear quantitative criterion of defects ( for example: crack size) if it fullfill their function ? |  | The decision of the engineer in charge takes into account the quantitative criteria of defects expressed in chapter '7.A.1.2.3 Acceptance criteria' (for example cracks in ACI349.3R). The ageing program is also evaluated by the FANC and meets the regulatory requirements.
BE-153 | 153 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 137 | In accordance with Technical Specification for chapter 7.1.2, can you describe the establishment of acceptance criteria related to ageing mechanisms? If possible refere to "Key standards and guidance used to prepare the SSC specific AMP, including a list of the main documents", "Key design, manufacturing and operations documents used to prepare the SSC specific AMP", "R&D programmes, by describing the objectives, contents and results of programmes managed by: o Licensees; Industry or other relevant bodies" and "Internal and external operating experience, by describing why and how these experiences have been taken (or not) into account". |  | See chapter 7.A.1.2.3 Acceptance criteria
BE-154 | 154 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 139 | What are the acceptance criteria listed in relevant AMPs for this TPR? |  | See chapter 7.A.1.2.3 Acceptance criteria
BE-155 | 155 | Czech Republic | Belgium | 07. Concrete containment structures | 139 | "To: Chapter 7.A.1.2.3 Acceptance criteria, internal steel liner: Which non-destructive examination methods do you use for inspection of hermetic steel liner? Have you found corrosion on the back of the lining? If so, what is the acceptance criterion for remaining liner thickness? |  | See chapter 7.A.1.2.3 Acceptance criteria. The back of the lining is not inspected. Being protected by concrete, corrosion is not suspected. No acceptance criterion has been set up for this case.
BE-156 | 156 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 139 | 7.A.1.2.3 Do you have experiments for the concrete deformation related to pre-stressing steel relaxation ? Do you use the results of tendon tests of other units for validation of theoretical results of deformations ? |  | Such experiments are not possible due to the system of grouted tendons (instead of unbonded tendons) itself.
BE-157 | 157 | United Kingdom | Belgium | 07. Concrete containment structures | 139 | "7.A.1.2.4 Key standards, guidance, design, manufacturing and operations documents. There is currently one R&D program linked to the ageing of the concrete structures. The aim of this program, performed at the SCK•CEN, is to study the extent of accelerated carbonation in concrete due to micro cracks. The program was started in 2015 and extends to 2020. Please provide further details of this research work to clarify (i) whether carbonation is considered to be a major ageing mechanism that could undermine lifecycle requirements (ii) whether the primary driver is due to concerns with the original structural concrete and (iii) discuss the preferred techniques to mitigate carbonation effects. " |  | The R&D program is still ongoing and has not yet advanced sufficiently to provide the desired details. Nevertheless, the following considerations can be given: (i) carbonation is considered as a major ageing mechanism in cracked concrete exposed to external weather conditions. (ii) the primary driver for the R&D program was linked to possible new NPP to be operated by Engie. This research can also be applied to existing reinforced concrete, but the program is not directly linked to concerns with the original structural concrete of a specific plant. (iii) the purpose of the research is not to mitigate carbonation effects but to understand the micro-scaled processes of propagation of carbonation.
BE-158 | 158 | Switzerland | Belgium | 07. Concrete containment structures | 140 | Are there specific testing and inspection requirements for safety related anchorage elements (e.g. pull-out tests with acceptance criteria)? |  | Anchorage elements are not in the scope of this chapter. However, no specific testing requirements have been set up for these elements.
BE-159 | 159 | Switzerland | Belgium | 07. Concrete containment structures | 142 | How are the results of the tests on the witness beams transferred or compared to the assessment of the pre-stressing in the containment? Which are the acceptance criteria? |  | See chapter 7.A.1.2.3 Acceptance criteria: This test does not aim at assessing the pre-stressing in the containment.
BE-160 | 160 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 142 | 7.A.1.3.2 How the effectiveness of the coating and treatments are inspected ? Do the cracks under the coating are examined ? |  | Only visual inspections are performed. The coating of the liner is qualified for LOCA. Potential cracks not visible under the coating are not examined.
BE-161 | 161 | Czech Republic | Belgium | 07. Concrete containment structures | 143 | To: “7.A.1.3.3 Secondary containment inspection program – key features“, Visual inspections Please, could you provide us with any further details about specific software which has been developer for recording of detected defects and their comparing? We are interested in system of recording, possibility of saving photos, way of recording multiple defects (cracks) in one place, way of working with data and their annual comparison and so on. |  | The specific software SIMEO© is used for these inspections.
BE-162 | 162 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 143 | 7.A.1.3.3 What data are in the database of visual inspection ? What is the form of documentation of visual inspection ? Is a specific hardware used for visual inspection ? |  | The specific software SIMEO© is used for these inspections.
BE-163 | 163 | United Kingdom | Belgium | 07. Concrete containment structures | 143 | 7.A.1.3.4 Primary containment surveillance – main results. This section discusses the presence of existing blistering zones that were scrutinized during the 2014 inspection campaign. The cause of the blistering is attributed to out of plumb alignment defects durign the original construction. It is not clear whether these zones of bulging are large / small etc. Please provide further information to demnostarte the scope and scale of these defects. |  | Maximum out of plumb 0.14m. Largest concerned surface 4.31 m². This defect has been analyzed and justified.
BE-164 | 164 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 143 | 7.A.1.4.1 How the effectiveness of the coating and treatments are inspected ? Do the cracks under the coating are examined ? |  | Only visual inspections are performed. The coating of the liner is qualified for LOCA. Potential cracks not visible under the coating are not examined.
BE-165 | 165 | United Kingdom | Belgium | 07. Concrete containment structures | 144 | Section 7.A.2 provides information on the evaluation performed for the proper functioning of the existing concrete deformation sensors. This discussion would benefit from further information. Please provide additional details to explain the strategy for maintaining sufficient coverage of functioning instruments. |  | In anticipation of the newly issued AMP 311, new surveillance systems have been put in place to avoid possible future obsolescence of the existing instruments.
BE-166 | 166 | Czech Republic | Belgium | 07. Concrete containment structures | 144 | To: 7.A.2 Licensee’s Experience of the Application of AMPs, Internal steel liner blistering follow-up – 2014 What is your experience with photogrammetric techniques? What is the sensitivity of this technology? How do you differentiate between places weaken by corrosion and blistering zones?" |  | The 3D photogrammetric topometry has allowed to demonstrate that the existing blistering zone has not changed in time and therefore is considered as a construction default without further evolution.
BE-167 | 167 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 145 | 7.A.3.2 What have to be changed in the aging management process due to the recent events? |  | In view of the recent events, ENGIE Electrabel acknowledges the need to improve the effectiveness of its concrete ageing management program. This improvement has already been launched in the frame work of the continuous improvement program to integrate this feedback. Some of the actions foreseen after the concrete degration found in 2017 in an auxiliary building at Doel 3 deal with ifurther clarifying the roles and responsibilities within the organisation for the monitoring and repair of concrete structures, improving the quality of the monitoring procedures and reports, improving the follow-up and prioritization of repairs during outages as a result of inspection results, improving the internal knowledge on concrete ageing phenomena. See chapter ‘2.A.4 Review and Update of the Overall Ageing Management Program’ of the National Assessment Report. This chapter explains in which way ENGIE Electrabel continuously reviews and updates its overall Ageing Management Program according to the ‘PLAN-DO-CHECK-ACT’ cycle. Chapter ‘2.A.5.4 Enhanced Ownership and Integration by ENGIE Electrabel since 2017’ details how ENGIE Electrabel reorganized its Maintenance & Engineering Department to improve the effectiveness of the Ageing Management Program.
BE-168 | 168 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 145 | 7.A.2 Are the licencee satisfied with existing concrete deformation follow-up systems ? Why they installed a new system when the existing systems are still to be used until the end of the plants' operational lifetime ? |  | In anticipation of the newly issued AMP 311, new surveillance systems have been put in place to avoid possible future obsolescence of the existing instruments.
BE-169 | 169 | EC | Belgium | 07. Concrete containment structures | 146 | The report does not clearly mention what international operating experience of interest for the ageing of containment concrete structures of Doel and Tihange was considered. Please clarify whether relevant international operating experience has been identified and whether it led to some learnings or actions for Doel and Tihange. |  | See chapter 7.A.1.2.4 Key standards, guidance, design, manufacturing and operations documents
BE-170 | 170 | Slovenia | Belgium | 07. Concrete containment structures | 146 | Regulator’s assessment and conclusions on ageing management of containment concrete structure for NPP (Page 151, 152): Has the regulator (FANC) been carrying out any special inspections dedicated to ageing management of concrete structures focusing also on concrete containments? There is stated in the report, that this area will receive even more attention in the future. What kind of regulatory actions will be performed, e. g. more inspections, programs implementation assessment, etc.? Does FANC uses also TSO support in this area? |  | The Belgian Safety Authority (FANC & Bel V) have carried out specific inspections to evaluate the recent events related to concrete degradation. As an example a thematic FANC inspection, supported by its TSO Bel V, on the monitoring program of concrete structures at Doel has been carried out in 2018 to evaluate the lessons learned from recent events.
BE-171 | 171 | Switzerland | Belgium | 07. Concrete containment structures | 146 | Which are the reasons for the failure of the preventive and remedial actions concerning the required reparation of the concrete structure of Thiange 2? |  | A Root Cause Analysis was made and discussed with the FANC. The necessary measures have been taken.
BE-172 | 172 | Germany | Belgium | 07. Concrete containment structures | 147 | It is stated that operating procedures of licensee to manage the ageing mechanisms and to monitor the ageing of the 07. Concrete containment structures are adequate. In the report is also added: “The need for reparation of the containment concrete structure of Tihange-2 underlined the failure of the preventive and remedial actions for this type of component, as existing at that time, and the need for improvement of the ageing management of concrete structures. Although some measures were taken for improving the ageing management of concrete structures, some recent events at Doel NPP still show that this topic need further attention. Attention should be put on fully implementing the ageing management on safety important concrete structures of NPPs.” In sub-chapter 7.A.4 ”Action Plan” the following is given: “Although some recent events highlight the necessity to extend and deepen the ageing management program of concrete structures, the Safety Authority acknowledges that the ongoing actions should answer these concerns. In consequence, no other actions than ensuring complete implementations on the field of the ageing management program of concrete structure are identified by the Safety Authority.” Can Belgium explain in more detail the degradation of the containment concrete structure of Tihange-2 and the degradation observed at Doel NPP? What should be implemented in AMP and why were the existing AMPs not able to pre-vent the “recent events” at Tihange-2 and Doel NPPs”? |  | In October 2017, during the planned outage for refuelling of the Doel 3 reactor, extensive damage to the concrete ceiling and walls of rooms in the Bunker building was detected during a routine inspection. The bunker building houses 2nd level emergency systems (such as emergency pomps, emergency diesel generators,….) which are needed in case of certain external hazards (aircraft crash, earthquake,…) . Due to the extensive damage to the concrete ceiling of this bunkered building, the protection against external hazards (aircraft crash, earthquake) could no longer be ensured. Therefore the repairs of this concrete building need to take place before the reactor unit can be restarted. Current estimates foresee that these repairs (including the installation of an additional roof layer) will take unto the summer of 2018. The damage was located in 3 rooms under the top roof of the bunker building which contain the outlet nozzles of the steam generator safety valves. Steam releases through these valves, in combination with inadequate maintenance and repair in the past, are the cause of the extended concrete damage. In view of the recent events, ENGIE Electrabel acknowledges the need to improve the effectiveness of its concrete ageing management program. This improvement has already been launched in the frame work of the ontinuous improvement program to integrate this feedback. Some of the actions foreseen after the concrete degration found in 2017 in an auxiliary building at Doel 3 deal with ifurther clarifying the roles and responsibilities within the organisation for the monitoring and repair of concrete structures, improving the quality of the monitoring procedures and reports, improving the follow-up and prioritization of repairs during outages as a result of inspection results, improving the internal knowledge on concrete ageing phenomena. See chapter ‘2.A.4 Review and Update of the Overall Ageing Management Program’ of the National Assessment Report. This chapter explains in which way ENGIE Electrabel continuously reviews and updates its overall Ageing Management Program according to the ‘PLAN-DO-CHECK-ACT’ cycle. Chapter ‘2.A.5.4 Enhanced Ownership and Integration by ENGIE Electrabel since 2017’ details how ENGIE Electrabel reorganized its Maintenance & Engineering Department to improve the effectiveness of the Ageing Management Program.
BE-173 | 173 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 147 | 7.A.3.2 What type of preventive and correction actions have been undertaken ? |  | In view of the recent events, ENGIE Electrabel acknowledges the need to improve the effectiveness of its concrete ageing management program. This improvement has already been launched in the frame work of the ontinuous improvement program to integrate this feedback. Some of the actions foreseen after the concrete degration found in 2017 in an auxiliary building at Doel 3 deal with ifurther clarifying the roles and responsibilities within the organisation for the monitoring and repair of concrete structures, improving the quality of the monitoring procedures and reports, improving the follow-up and prioritization of repairs during outages as a result of inspection results, improving the internal knowledge on concrete ageing phenomena. See chapter ‘2.A.4 Review and Update of the Overall Ageing Management Program’ of the National Assessment Report. This chapter explains in which way ENGIE Electrabel continuously reviews and updates its overall Ageing Management Program according to the ‘PLAN-DO-CHECK-ACT’ cycle. Chapter ‘2.A.5.4 Enhanced Ownership and Integration by ENGIE Electrabel since 2017’ details how ENGIE Electrabel reorganized its Maintenance & Engineering Department to improve the effectiveness of the Ageing Management Program.
BE-174 | 174 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 148 | 7.A.3.3 How does the Safety Authority intend to support the improvement of AM of concrete structures ? |  | Several actions have been taken. The first one is the sensibilisation to this issue of experts from the Belgian Safety Authority, for the daily follow-up of the licensee's activities. In addition, the expert team in charge of the concrete structures assessment has been reinforced. Finally, specific controls and inspections have been carried out and some more are planned to support the improvement of AM of concrete structures.
BE-175 | 175 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 149 | 7.A.4 What do the Safety Authority think, is essential to examining the aging of concrete structures? Does the aging of concrete structures affect the lifetime of the power plant? |  | Obviously. The containment must fulfill its safety function. If this is not the case, wathever may be the origin of the loss of the function (whether originating from an ageing effect or an external event), the reactor must be shut down, possibly definitevely.
BE-176 | 176 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 07. Concrete containment structures | 150 | In total, the safety situation concerning the concrete containment structures is still considered sufficient, even though we only recently had to experience several incidents, most notably at Tihange 2. Given this background, can it be considered right that “no other actions than ensuring a complete implementation on the field of the ageing management program of concrete structure are identified by the Safety Authority”? |  | The Belgian Safety Authority has taken the adequate position. Taking into account that the OEF from the events affecting concrete containment structures has been integrated in the improvements of the ageing management program of concrete structures, no other actions is necessary.
BE-177 | 177 | Concrete containment PCPV expert group | Belgium | 07. Concrete containment structures | 150 | In accordance with Technical Specification for chapter 7.1.1, can you describe the main functions of the structures and add principles drawing? |  | The concrete structure provides the support for the steel containment shell. The latter provides the containment function for the reactor, which is periodically tested according to the license prescriptions. The concrete structure of the reactor building also supports the reactor pool. For security reasons, no drawings can be made public.
BE-178 | 178 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 09. Overall assessment and general conclusions | 151 | As mentioned in the report, there are still serious deficits in the field of monitoring of the ageing of some components and an insufficiency of remedial actions. Related to the restoration of public trust and in order to improve the sense of security: How should the deficits in the monitoring process be remedied? Might common, Europe-wide standards including reciprocal inspection be part of a future strategy? |  | This question is considered out of scope of the TPR on Ageing Management. Again, the Belgian Safety Authority does not feel that the TPR is the adequate forum to reply to questions on the need of common, Europe-wide standards including reciprocal inspection. This is basically a political question that should be addressed to the adequate political authorities, such as the federal government of Belgium. The Belgian Safety Authority already is committed to transposing appropriate international and European guidelines (such as the WENRA reference levels) in the national regulatory framework. In addition, on a volontory basis cross inspections are being organized on a bilateral level between the Dutch, French and German safety authorities to enhance inspection methods.
BE-179 | 179 | Germany | Belgium | 09. Overall assessment and general conclusions | 151 | It is stated that the Safety Authority plans to continousely enhance the follow-up of ageing management until the final shut-down and decomissioning of the nuclear facilities. What are the addtionial measures to enhance oversight with respect to ageing management for Belgium nuclear power plants and research reactors? |  | Currently several measures are considered within the Belgian Safety Authority. Improving the awareness of the technical experts and inspectors on the topic of ageing management is obviously a measure to enhance its oversight. This goes hand in hand with the further development of the expertise in this field within the Belgian Safety Authority. More practically the inspection plans have been updated in order to cover all the regulations, such that specific attention will be emphasized on ageing management. Reinforcing the review and assessments of the safety factor 4 ("Ageing Management") of the future Periodic Safety Reviews is also considered.
BE-180 | 180 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 09. Overall assessment and general conclusions | 151 | The Executive Summary (pp. ii-iii) as well as the final chapter on Overall Assessment and General Conclusions (pp. 159-161) both conclude that the overall ageing management program by ENGIE Electrabel is in line with international standards. However, they further point out that the program’s effective implementation can be improved. The report acknowledges that the licensee has taken some necessary steps in this direction whose effectiveness will have to be judged on the long-term. 1. What concrete steps will the Belgian Safety Authority take to judge the effectiveness of tools developed by the licensee recently? 2. Given the sensitive security matter at hand, why does the Belgian Safety Authority intend to judge the effectiveness only on the long term rather than in the short- and mid-term? |  | The development and the implementation of the tools will be obviously evaluated on short, mid and long-term. The thematic inspections on ageing management in each nuclear plants are planned periodically in conformity with the official inspection plans. These inspections aim at reviewing all the modifications and improvements brought to the ageing management program. The actual results and activities related to ageing management (for example maintenance activities, periodic in-service-inspections, replacement of older equipment) are also reviewed during the day-to-day inspection activities by Bel V. In addition the effectiveness of these improvements is also assessed within the Periodic Safety Reviews. For the units within LTO, SALTO audit missions from IAEA has been conducted on all three units. The follow-up SALTO mission in Doel 1 & 2 is already invited for 2019. In this framework, an independent assessment will be done by IAEA experts on the LTO activities related to ageing management.
BE-181 | 181 | Bulgaria | Belgium | 09. Overall assessment and general conclusions | 151 | Are the following IAEA reports and guides used too: 1. IAEA, Methodology for the Management of Ageing of Nuclear Power Plants Components Important to Safety, Technical Reports Series No. 338, IAEA, Vienna (1992) 2. IAEA, A system for the Feedback of Experience from Events in Nuclear Installations, Safety Guide No. NS-G-2.11, IAEA, Vienna (2006); |  | - IAEA, Methodology for the Management of Ageing of Nuclear Power Plants Components Important to Safety, Technical Reports Series No. 338, IAEA, Vienna (1992) : ENGIE Electrabel used the IAEA NSG 2.12. This more recent guideline used also the IAEA technical report serie 338 (see reference [I–2]) ; - IAEA, A system for the Feedback of Experience from Events in Nuclear Installations, Safety Guide No. NS-G-2.11, IAEA, Vienna (2006) :this document is not directly linked to ageing mangement program but moreless to "operating experience management system" that each program or process used. Pease find in chapter 2.A.2 the international reference that ENGIE Electrabel is following in the frame work of its ageing management program.
BE-182 | 182 | Bulgaria | Belgium | 07. Concrete containment structures | 151.152 | Concerning the lists of different civil structures ageing mechanisms, presented in the chapter “07. Concrete containment structures”: we could not find information on the common used methods for the concrete and civil structures ageing management condition monitoring. Did you use the compressive strength studies for concrete? Did you use half-cell potential measurement for reinforced steel bars? Would you please clarify which methods were used? |  | Several of the testing methods referred to in [2-Q] were used, depending on the issue and the extent of the ageing mechanism. The condition monitoring applied methodology is a progressive approach with 4 levels of analysis. The first level consists of visual inspections methods, the second level includes NDT techniques (hammering, grids for cracking follow-up,…), the third level introduces destructive testing (carbonation test, potential measurement of reinforcement, core samples), and the fourth level includes laboratory testing of the core samples. Compressive strength tests on samples has been performed for several units, mainly where potential ASR has been suspected. Potential measurement for detection of corroded steel reinforcement bars has also been conducted on the secondary containment of one unit.
BE-183 | 183 | Switzerland | Belgium | 07. Concrete containment structures | 152 | How are the structures and the structural elements assessed which are inaccessible for visual inspections (indirect / indicative methods)? |  | Inaccessible areas are the outer surface of the secondary concrete containment walls under the ground and the bottom surface of the raft foundation. Surveillance of these areas is done by checking the leak tightness of the structures.
BE-184 | 184 | Slovenia | Belgium | 07. Concrete containment structures | 152 | Processes and procedures for the identification of ageing mechanisms for the different materials and components of concrete structures (Page 140) and Monitoring, Testing, Sampling and Inspection Activities (Page 145) and Secondary containment inspection program – key features (Page 147): How often material tests have been performed for primary and secondary containment and what kind of requirements are written in the procedure for material testing of concrete structures, especially for containment? |  | Material (destructive) tests are performed on core samples of the secondary containment when deemed useful (after visual inspections has been performed). There is no regular time interval for these tests. The procedures for material testing are in accordance with the requirements of appropriate Belgian norms.
BE-185 | 185 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 07. Concrete containment structures | 152 | In consideration of the potentially immense danger for the public, the initiation of several more detailed inspections depending exclusively on the decision of the engineer in charge appears questionable (for instance 7.A.1.3.1 on p. 146, 7.A.1.3.3 on p. 147 or 7.A.1.4.2 on p. 150). The probability of mistakes or wrong decisions and, in consequence, of immense danger seems too high. Wouldn’t it be more effective and appropriate to delegate the decision for more detailed inspections to a group of engineers? |  | The wording engineer in charge has to be interpreted as "Engineer In Charge". This is a function assumed by a team and not by a single individual. In addition, organisational structures are implemented in such a way that important decisions are never taken by a single person. This is part of the nuclear quality management system.
BE-186 | 186 | EC | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 152 | 2.3.1: The scope of the AMP (NPPs): more supporting tools are available for the units that undergo LTO (i.e.: screening, ageing management programs, time limited ageing analysis and reliability centred maintenance). What is the current experience with these extra tools? How is the communication with the non-LTO units? This could be considered a good practice for the LTO units and an area for improvement of the non-LTO units as confirmed by the licensee on page 33 of the NAR. |  | ENGIE Electrabel only recently entered the LTO period. Therefore, extensive return on experience is not yet available. Communication between LTO and non-LTO units runs smoothly (it is the same team at site and at coporate level), but also between the R&D and Design engineers dealing with the ageing management program. Hence, there is good communication between all parties involved. Good practices learned with the new tools are shared and implemented in the framework of ENGIE Electrabel's continious improvement process for the non-LTO units. Finally, in the frame work of PSR project, ENGIE Electrabel is evaluating the applicability on Doel 3-4 & Tihange 2-3 NPPs of the ageing actions that were defined during the LTO study project of Tihange 1 and Doel 1&2.
BE-187 | 187 | United Kingdom | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 152 | "Starting in 2009, As the plants have entered LTO, ENGIE has applied additional ageing management tools as shown in Fig 2A-5. These have not been applied ot the newer units, but page 33 states that ENGIE plans to apply them. Please: 1 explain why it has been acceptable to not apply these tools to the newer plants. 2 provide details of the timescales to introduce them." |  | Ageing Management Program of the nuclear NPPs is in line with with the prevailing regulations and FANC requirements : - The Ageing Management Program (AMP) for nuclear power units Doel 1&2 and Tihange 1 has been addressed in the framework of the Long-Term Operation Study Program. The AMP for these LTO units is in line with the FANC’s Strategic Note and follows the methodologies specified in 10 CFR 54, NUREG-1800 Rev.1 and NUREG-1801 Rev.1. This approach and the resulting lifetime extension of the nuclear power units Doel 1&2 and Tihange 1 has been endorsed by the IAEA during a Safety Aspects of Long Term Operation (SALTO) mission. - The ageing of the other Belgian nuclear power units (Doel 3&4 and Tihange 2&3) has been evaluated in the framework of the PSR Program and is in line with the prevailing regulations and FANC requirements. The AMP for these units is updated as part of the continuous improvement process and will be re-evaluated during the next PSR.
BE-188 | 188 | United Kingdom | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 152 | §2.A.5.3 & §2.A.7.3 include improvements to ageing amangement that are being done by the licensee. What are the programmes for completion of these improvements? |  | All these arrangements or improvements are managed in the framework of ENGIE Electrabel's overall ageing management program.
BE-189 | 189 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 02. Overall Ageing Management Programme requirements and implementation | 154 | According to the report, for Tihange 1 and Doel 1&2, the LTO Ageing project upgraded the global AMP by means of a systematic and comprehensive process. This is currently not the case for Tihange 2&3 and for Doel 3&4. However, the report says that ENGIE Electrabel takes currently action for these units to move towards an ageing management program based on the program installed in the LTO units and on the most recent guidelines. In view of the potential risk resulting from nuclear power plants, what concrete action does ENGIE Eletrabel take for Tihange 2 to move towards an ageing management program based on the program installed in the LTO units and on the most recent guidelines? And when will the ageing management program for Tihange 2 be finalised? |  | See question 12. | ref to BE-12
BE-190 | 190 | Czech Republic | Belgium | 03. Electrical cables | 159 | (chapter 3.A.1.3) It is not mentioned if the monitoring of environmental parameters is regularly carried out. Could you please provide us some more information? |  | The sequence of the environmental parameters is described on page 54. Walk-downs are performed from once every year to once every four years.
BE-191 | 191 | Czech Republic | Belgium | 03. Electrical cables | 161 | "Adverse condition", monitoring parameters" (chapter 3.A.1.3 ) - (sorry - this is correction of previously send question) Parameters aren´t defined. It is not mentioned if the monitoring of environmental parameters is regularly carried out. Can you provide us some more information? |  | The sequence of the environmental parameters is described on page 54. Walk-downs are performed from once every year to once every four years.
BE-192 | 192 | Netherlands | Belgium | 07. Concrete containment structures | 161 | Could you elaborate on some highlights of the action plans for BR2 and the NPPs? Have these plans been established in cooperation between regulator and licensees? |  | The Belgian Safety Authority requests the licensees to take the necessary actions to fill the gaps identified, either during their own self-assessments or by the Safety Authority. Since the publication of the NAR, an action plan has been established by the licensee SCK CEN, proposed to and accepted by the Belgian Safety Authority (through some minor amendments). The deadlines have been discussed and accepted by the Belgian Safety Authority. These deadlines are in line with the PSR implementation phase extended to 2019. For the NPP licensee, the necessary actions to fill the gap was taken directly during the self-assessment phase of the NAR redaction.
BE-193 | 193 | Netherlands | Belgium | 04. Concealed pipework | 164 | Appendix A provides general information/definitions of different ageing mechanism for concealed pipework. It is not specific to Belgium NPPs and RRs, isn't it? Would you consider to omit it in updates of the NAR? Additionally, Appendix A also gives references, but these references are not on the reference list. If you are planning to keep Appendix A in the NAR, could you please provide references for Appendix A in the reference list? |  | he purpose of the scoping and screening of the ageing management program is first to identify all the possible ageing mechanisms that could affect the concealed pipeworks and then to screen out the ones that are not plausible. In this framework a complete list of the identified mechanisms has its place within the report. It is unclear for us what is the added value of the proposition to omit it in a prospective update of the NAR. Indeed the NAR presents a problem with the references considered in the appendix A, due to a concatenation problem during the finalization of the report. The references are the following for the appendix A: [4] IAEA – Safety Report Series N°82 (SRS N°82): Ageing Management for Nuclear Power Plants – International Generic Lessons Learned (IGALL) – International Atomic Energy Agency – Vienna – April 2015 [6] IAEA NE Series No. NP-T-3.20: Buried and Underground Piping and Tank Ageing Management for Nuclear Power Plants ZNO.10010705452 [8] Ageing S10B – Ageing Summary S10: Subterranean pipes, except for those belonging to the circulation water CW – CEC, part 1 (29/12/2009) ZNO.10010167017
BE-194 | 194 | Wilfried Oellers MdB Deutscher Bundestag Deutschland | Belgium | 01. General information | Appendix A | Anmerkungen: Die Europäische Atomgemeinschaft (EAG oder heute EURATOM) ist eine der ältesten europäischen Übereinkünfte, um das Leben in Europa, um die Lebenshaltung in den Mitgliedstaaten zu verbessern und zur Entwicklung der Beziehungen mit den anderen Ländern beizutragen. Dennoch gibt es in der europäischen Zusammenarbeit im Bereich von lebensbedrohlichen Gefährdungen weniger Schutz der Bevölkerung durch verbindliche und sanktionierbare europäische Regelungen als in deutlich überschaubareren Lebensbereichen, wie zum Beispiel bei den europäischen Regelungen zur einheitlichen Verwendung von Glühbirnen. Hier sehe ich eine starke Ungleichgewichtung, die im Sinne unserer europäischen Bürgerinnen und Bürger schnellstmöglich korrigiert werden muss. Fragen - Gegen die belgischen Hochrisikoreaktion Tihange und Doel gibt es erhebliche wissenschaftliche und behördliche Sicherheitsbedenken aus allen europäischen Anrainerstaaten, die bisher von der belgischen Regierung aus wirtschaftlichen Gesichtspunkten ignoriert wurden. Welche Pläne gibt es, Belgien dazu zu bewegen, künftig endlich die Sicherheitsinteressen, der Menschen trotz wirtschaftlicher Eigeninteressen zu beachten? - Gibt es Pläne eine europäische Atomaufsichtbehörde zu schaffen, die nicht nur beobachten und kommentieren darf, sondern bei Sicherheitsbedenken auch umfangreiche und wirksame Sanktionsbefugnisse gegenüber dem Verursacher hat und wenn nicht, warum gibt es keine solchen Pläne und welche konkreten Mitgliedsstaaten sträuben sich gegen eine solche Regelung? - Katastrophenschutz ist in der Regel eine nationalstaatliche Angelegenheit. Bei einem Supergau in einem Krisenreaktor, die ja regelmäßig bevorzugt in den Grenzregionen zu europäischen Partnerländern errichtet werden, kennt die Panik der betroffenen Bevölkerungen keine Grenzen. Fluchtbewegungen von hunderttausenden Menschen in Todesangst können unvermittelt auch die Behörden anderer Anrainerstaaten treffen. Hierauf sind die Katastrophenschutzpläne vieler Mitgliedsstaaten nicht in diesem Umfang ausgerichtet. Auf welche Weise soll in Zukunft die bestehende grenzübergreifende Zusammenarbeit im Bereich Katastrophenschutz verbessert werden, damit den europäischen Bürgerinnen und Bürger z.B. bei einem atomaren „Supergau“ auch grenzübergreifend bestmöglichst geholfen wird? |  | There is a misunderstanding here on the scope of the Topical Peer Review process. These questions, which already include misleading statements, do not address in any matter the Belgian National Report on Ageing Management and are considered out of scope of the TPR on Ageing Management. The Belgian Safety Authority does not feel that the TPR is the adequate forum to reply to such questions on emergency preparedness or the need of additional European supervision. These questions are of a political nature and should be addressed to the adequate political authorities, such as the federal government of Belgium.
BE-195 | 195 | Pascal Arimont / Sabine Verheyen / Rudolf Henke, Members of the European Parliament / Member of the German Bundestag, Belgium / Germany | Belgium | 05. Reactor Pressure Vessels | mehrere | The report states that in case of Doel 3 and Tihange 2 hydrogen flakes have been present inside the RPV shells since fabrication and inspection campaigns revealed no indication of flake growth. 1. What exactly is the Belgian Safety Authority going to do in order to inspect whether the flakes grow in future? 2. Given the fact that only comparable test setups can reveal any indication of flake growth, how will the Belgian Safety Authority ensure that comparable test setups are used when inspecting the flakes in future? |  | As explained in the Safety Case established by ENGIE Electrabel, there is scientific consensus on the fact that hydrogen flaking occurred during the construction of the forged pieces. The hydrogen flakes in the RPV of Doel 3 and Tihange 2 were not reported at the time of construction, but they have been identified and reported in 2012. Nevertheless, the forged pieces have been declared in conformity with the construction code after completion of the regulatory checks. When the decision was made to restart the two units, it was agreed to install an inspection program for both RPVs to be executed during future scheduled overhauls. The inspections that have been conducted since then, have shown and confirmed that the hydrogen flakes have not changed. In addition, it has to be noticed that: 1. ENGIE Electrabel has subjected the plants' RPVs to a full inspection one cycle after the restart. This inspection revealed no flakes growth and no new indications. Each three cycles, a new inspection (via UT) will be carried out to confirm the stability of the hydrogen flakes. 2. The UT inspection procedure is well described and the AIA has the duty (among others) to check that the inspections are caaried out in line with the qualified procedure. The fact that the procedure is followed ensures that the tests are compatible and comparable to each other.
BU-1 |  | Poland | Bulgaria | 01. General information | 8 | 1. What is the standard with acceptance criteria and methodology for non-destructive testing? | Website | According to the Inspection Procedure: In-service-inspection of base metal, cladding surfaces and welded joints of equipment and pipelines of WWER-1000 units at KNPP, as a main document with acceptance criteria is applied “НП-084-15. Federal Norms and Rules in the Area of Usage of Nuclear Energy." Unified Inspection Procedures for Base Materials, Weld Joints and Build-Ups in the Course of Operation of Equipment, Pipelines and Other Elements of Nuclear Power Plants, Rostehnadzor, Russia, 2015 The non-destructive testing (NDT) methodology is reflected in the NDT procedures, developed in accordance with the Russian standards and guides PNAE-G, as well as the international/European standards БДС EN ISO, approved by the Bulgarian Institute for Standardisation.
BU-2 |  | Poland | Bulgaria | 05. Reactor Pressure Vessels | 71 | 1. What is the methodology of taking a sample and carrying out the critical brittle temperature TK and test plane strain fracture toughness KIC without RPV damage? | Website | No samples are taken. The inspection is performed on surveillance specimen received with the delivery of the Reactors Pressure Vessels (RPV). Radiated surveillance specimen are placed in specially constructed containers (assemblies) mounted at the top end of the core baffle cooling channels. Measuring the critical brittle temperature TK - in line with the Methodology for determination the fracture toughness according to the results from the surveillance specimen tests for calculated strength and lifetime of the RPVs of VVER-1000 Reactors, РД ЭО 1.1.2.09.0789-2012. Testing the plane strain fracture toughness KIC - surveillance specimen with crack have not been tested sofar, but the activities are planned. A number of activities for conservative evaluation of KIC have been carried out according to the normative requirements adopted in Russia with a view to their forecasting up to 60 years of opearation.
BU-3 |  | United Kingdom | Bulgaria | 05. Reactor Pressure Vessels | General | General - Has international operating experience relating to heavy section forgings manufactured at Le Creusot forge been considered in relation the RPVs of Kozloduy NPP? | Website | The information received in 2015 on the deviation of the chemical composition (increased carbon concentration) of the steel at the bottom and the reactor pressure vessel cover at Flamanville-3 nuclear power plant, along with the WENRA workshop materials 'Activities in WENRA countries on positive macro-segregation issues', held in October 2017, have been taken into account. As reflected in section 5.1.2.9 of the national report, international operating experience related to heavy section forgings, RPVs in particular, was considered in 2013, in relation with the indications, registered in the Belgian reactors (Doel-3 and Tihang-2). In accordance with WENRA's recommendations to the nuclear safety authorities, the Nuclear Regulatory Agency and Kozloduy NPP have verified the manufacturer data, which also includes information on the chemical composition and mechanical properties of the base metal and the welded joints of the RPVs, as well as the inspections of the metal of the RPVs. According to the information from the review carried out in 2013, as well as the documents for extension of the lifetime of Units 5 and 6 (2012-2017), the heavy section forgings of the RPV, steam generators and pressurisers at Kozloduy NPP have been made of other types of steel, there are no deviations in the chemical composition of the metal. The production technology differs from the one that had been used in the Le Creusot plant and it prevents any carbon segregation.
BU-4 |  | United Kingdom | Bulgaria | 05. Reactor Pressure Vessels | 72 | " Section 5.1.2.1. Page 72. First paragraph. This section usefully identifies several types of corrosion as mechanisms requiring management. The final paragraph of Annex 1, page 1/4 identifies that the reactor coolant contains boric acid. There is international operating experience of RPV degradation due to boric acid corrosion. Is this risk specifically accounted for in the AMPs applied for the RPVs of Kozloduy NPP? " | Website | In the RPV's Ageing Management Program, it has been taken into account that the boron acid is a potential degradation mechanism for carbon and low alloyed steels upon contact with the external side of the RPV and the reactor head, during operation of the reactor plant, and it is dependent on the concentration of the boric acid. This could be due to leakage from the flange joints of the Control Rod System's nozzles (CRS) and the TK (temperature control) of the reactor head. The In-service Inspection Procedure provides for inspection of all components and surfaces exposed to a potential risk of boric acid exposure. The RPVs internal surface is completely clad with a two-layer austenitic stainless steel lining that protects the base metal and welded joints from corrosion development. According to the results of the ISI of the metal on the internal surface of the RPV during the years of operation, provided that the primary circuit water chemistry limits were obeyed, degradation mechanisms due to presence of boric acid in the coolant solution have not been identified.
BU-5 |  | Finland | Bulgaria | 03. Electrical cables | 42-44 | Cable deposits do not seem to be used to survey the qualified condition or cables. Is it considered to use cable deposits and testing of their samples in order to survey that the cables are in qualified condition? | Website | Cable deposits have not been used at Kozloduy NPP until now. A re-qualification of control and power cables for MILD, HELB and LOCA conditions was carried out for the purposes of extending the lifetime of units 5 and 6. As cables specimen, sections cut from decommissioned real ex-operational cables were used and left in the cable tracks along with the working cables. At present, the use of cable deposits is not planned.
BU-6 |  | Finland | Bulgaria | 05. Reactor Pressure Vessels | § 5 | To provide more specific description of the RPV surveillance related to irradiation embrittlement is recommended. | Website | The program includes the following activities for the monitoring/ oversight of the reactor pressure vessel: 1. Verification of the neutron-physical characteristics of the WWER-1000 reactor after each outage; 2. Validation of the neutron fluence of the RPVs of Units 5 and 6 by means of measured activity of ex-vessel detectors installed in the air cavity behind the vessels and comparison of the numerical and measured data on the activity of detectors; 3. Modernisation of the surveillance specimen sets from the unit 5's RPV in order to ensure 60 years of operation of the reactor plant. Equipping surveillance specimen from 1M and 2M assemblies from Unit 5 for accelerated irradiation in flat containers in the standard places for installation in the core baffle. 4. Preparation of surveillance specimen with cracks from sets 2L, 3L from Unit 5 and sets 1L, 2L, 3L from Unit 6 for performing tests to obtain crack resistance characteristics of the RPV's material, in order to increase the representativeness of the estimated curves on predicting the properties of the RPV's metal up to 60 years of opeartion. 5. Removing the modernised Units 5 and 6 assemblies of the new type, loaded in the cooling channels of the core baffle to accelerate the accumulation of neutron fluence. After their test, information on the condition of the RPV metal after exposure to the design fluence will be obtained. 6. Determination of the terms for modernisation of the irradiation sets 4L, 5L from Unit 5 and 4L, 5L and 6L from Unit 6 in flat container assemblies and loading for additional irradiation in accordance with the operational life of up to 60 years. 7. Conduct nanostructure examinations of surveillance specimens from the reference, irradiated and thermal sets to determine the characteristics of nano-dimensional imperfections that have impact on the mechanical properties of the RPV material after prolonged irradiation and exposure to operating temperatures.
BU-7 |  | United Kingdom | Bulgaria | 07. Concrete containment structures | General | There is no discussion on irradiation effect on the reinforced concrete secondary containment. How are these effects assessed and the long term integrity of the structure validated? Please provide more information on the ageing mechanisms and strategy for irradiation of the concrete containment. | Website | Radiation exposure has been taken into account in the assessment of ageing mechanisms on the Containments in the Kozloduy NPP. It is a fact that with regards to the reinforced concrete containments, the radiation ageing is not a significant factor, since the accumulated neutron fluence values are many times lower than the limit values. Changes in the properties of the concrete begin to occur with accumulation of integral neutron fluence of over 1х10^19 n/cm2. The calculated accumulated fluence in the metal of the support frame of the RPV of units 5 and 6, for 60 years of operation is less than or equal to 6,88х10^18 n/cm2. Considering that the calculations were made under conservative conditions and the fact that the value of the neutron fluence in the concrete of the Containment (which is more than 15 m away from the reactor shaft) will be much lower than the predicted value in the supporting frame of the vessel, it can be concluded that the value of the neutron fluence impacting the civil structure towards the end of the extended operating life of Units 5 and 6 will be less than 6,88х10^18 n/cm2 and it is not justified to expect worsening of the strength and deformation characteristics of the concrete of the Containment due to the effects of ionizing radiation. This finding is also supported by the regulatory document NUREG-1557, where, on page B-34, it is stated that "radiation exposure has a negligible effect on the reinforced concrete structures of Containments and Reactor Buildings and its influence can be neglected" (written on page B-34 of NUREG-1557).
BU-8 |  | Switzerland | Bulgaria | 03. Electrical cables | 12 | Textline18: Is there an AMP for electronic devices (capacitor, relais, modules, drives)? | Website | Separately developed Ageing Management Programmes (AMPs) for electronic devices at Kozloduy NPP are not available. Lifetime properties management of capacitors, relays, modules, etc. is conducted by applying a Maintenance and Repair (M&R) system, routine tests after maintenance, functional checks and operational control at work. To ensure the operability of the equipment, the equipment replacement takes place (before the expiration of the specified lifetime). Replacements of equipment are based on the calculation of the operational lifetime under the Arrhenius law using the dependence of the operating temperature ageing indicator and the failure and defect analysis of technical equipment, devices, units and modules of the electrical and I&C equipment. Furthermore, the defective unit or device is immediately replaced by a new one, of the same kind, from the spare parts and tools stock (SPS). It is impossible and not necessary to assess and control the degree of degradation due to the ageing of many thousands of individual components in the NPP. For this reason, Kozloduy NPP sends defective modules / units to the manufacturers, for analysis.
BU-9 |  | Switzerland | Bulgaria | 03. Electrical cables | 21 | Textline7: How is the presence or absence of liquid phase coolant in the RPV monitored? | Website | The reactor coolant level control system (RCLCS) consists of four level control channels. The measurement in each channel is realized using KNITU-5 reactor internal detectors, in which additional three-level temperature measuring devices are mounted at three levels along the height. Measurement is based on the principle of the difference in heat transfer in liquid and gaseous media. - measuring point 1 - under the RPV head; - measuring point 2 - at the level of the upper generant at the RPV inlet nozzles openings - measuring point 3 - at the level of lower generant at the RPV inlet nozzles openings These detectors are replaced once every 4 years during the core reloading.
BU-10 |  | Switzerland | Bulgaria | 03. Electrical cables | 21 | Textline20: What means ‘containment pre-stress control to visualize on-line data on the tendons pre-stress by measuring the relevant forces in six separate wires’? | Website | Тhe prestressing force in the monitored tendons of the concrete steel containment is measured in real time, by means of tensometric measuring equipment that scans a total of 60 measurement points. The sensors are located in 6 of the wires in the ten tendons, i.e., they are located in different wires of the cylindrical containment and the dome of the cylindrical part of the reactor building. The system consists of tensometric measuring equipment, sensors and a central data processing server, and applied specialized software to measure, record, store the information, analysing the condition of the containment of the airtight part of the reactor building.
BU-11 |  | Switzerland | Bulgaria | 03. Electrical cables | 22 | Textline18: What is the benefit of noise monitoring of the reactor internals trough neutron flux measurements? How is it done/filtered? | Website | Monitoring the fluctuations of the reactor internals at the core barrel is used for diagnostics during transients and accidents related to changes in the neutron flux density. The information is taken from the regular neutron flux control equipment. The modules of the neutron flux monitoring system (NFMS) perform accumulation, processing and storage of signals' data. The equipment does not register the physical displacement of the reactor internals. Calculations are performed. Data is processed using a mathematical model provided by the chief designer / Chief Design Engineer (confidential to the manufacturer) to diagnose, analyse the gradient of neutron flux change, and perform analytical comparative analysis with the data set in the models. Noises are also analysed, by which conclusions are made on vibrations, deviations from the normal conditions of the reactor internals during such transient modes. Filtering is by frequency.
BU-12 |  | Switzerland | Bulgaria | 03. Electrical cables | 41 | Textline13: What is the period/repetition time for the measurement of cables with the described methods (Rin, IC, tgd, PD)? | Website | The typical cable measurement period is 3 years, using methods (Rin, IC, tgd, PD). If an undesirable trend is found, the frequency of measurement is increased.
BU-13 |  | Switzerland | Bulgaria | 03. Electrical cables | 44 | Textline16: How (method) is air tightness of "ELOX" electrical penetrations measured? By local (difference) pressure measurement? | Website | Tightness and technical condition of airtight electrical cable penetrations (ECPs) is checked and recorded monthly and during outage by the reading on the pressure gauge mounted on each EPC (according to the requirements of EN 837-1 and EN 837-2) and it is controlled within the limits set by the manufacturer, under approved NPP procedures. Read is the absolute pressure in the penetration - Pn (according to the pressure gauge mounted on it) and the room temperature (taken down with portable mercury thermometer) at which the pressure is measured.
BU-14 |  | Czech Republic | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 9 | "An Equipment Ageing Management Plan was developed and put into effect in 2003." Is it one-time plan or is it living, periodically updated plan? | Website | The plan was developed once and it was in force until the Units 5 and 6 Lifetime Management Programme (the PROGRAMME) was launched.
BU-15 |  | Czech Republic | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 11 | "These SSCs have been assessed for their real condition and the residual lifetime." Does it mean that the residual lifetime is assessed for all SSCs in the scope of Ageing management? | Website | The residual lifetime is assessed for all SSCs within the scope of the Ageing Management Programme.
BU-16 |  | Czech Republic | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 12, 13 | "With the purpose of control and mitigation of the SSCs ageing effects, ageing management programmes are developed and implemented within the general PROGRAMME for the SSCs, as follows: • reactor pressure vessels; • steam generators; • primary circuit pipelines; • pressurizer; • reactor coolant pumps; • diesel generator station (DGS); • accumulator batteries; • unit transformers and house load transformers; • reactor internals (RI); • main heat-exchange equipment; • buried pipework from the service water system (QF); • hydraulic shock absorbers; • cables and cable facilities; • civil structures of Kozloduy NPP; • units 5 and 6 containments; • hydraulic engineering facilities for service water supply (HEF);" This list of AMPs is not clear for me. Does it mean that on Kozloduy NPP there is no ageing management programme for managment of flow accelerated corrosion in secondary feedwater pipelines and steam pipelines? | Website | At Kozloduy NPP, the current ageing management programmes are component-oriented rather than as per established degradation mechanisms. Each ageing management programme for the respective component concerned describes the mechanisms of degradation in place and all necessary actions related to their management. Corrosion management, accelerated by the flow of secondary circuit feedwater pipelines and steam pipelines, is carried out with the aid of procedures in the water chemistry programme, and the monitoring of the effects of ageing is carried out by the applying the procedures for NDS and in-service inspections.
BU-17 |  | Finland | Bulgaria | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Website | The main challenges related to the safe operation of the reactor plant are compliance with operating limits. In this respect, the operators' practices directly affect the operating parameters of the reactor equipment and have a significant role in reducing the degradation of the metal of the equipment, as the mitigating actions described in the RPV AMP.
BU-18 |  | Czech Republic | Bulgaria | 03. Electrical cables | 37 - 39 | to chapter 3.1.1. From the document it is not clear what kind of cables are included in AMP. Authors speak only about LOCA/HELB cables. Requested information about HV cables, cables in trenches and NIS cables is missing. Can you please give us clarification? | Website | The cables included in the AMP are those from the main and auxiliary systems necessary for the safe shutdown of Kozloduy NPP Units 5 and 6 and those important for electricity generation, namely: • cables supplying power for qualified equipment in the containment; • cables supplying power for qualified equipment outside the containment; • 6kV cables for qualified equipment; • cables from process systems that are important for the electricity generation (these are 6 kV cable, interconnections between the units and balance of plant equipment in the composition of long cable lines laid in ditches and technological tunnels the replacement of which would involve large material resources).
BU-19 |  | Czech Republic | Bulgaria | 03. Electrical cables | whole chapter 3 | Document does not contain many details that give overview about the whole AMP. Who is cable producer? How many types? It seems, that only LOCA cables are included in AMP. Can you please provide us with more details? | Website | The cables included in the AMP are those from the main and auxiliary systems necessary for the safe shutdown of Kozloduy NPP Units 5 and 6 and those important for electricity generation, namely: • cables supplying power for qualified equipment in the containment; • cables supplying power for qualified equipment outside the containment; • 6kV cables for qualified equipment; • cables from process systems that are important for the electricity generation (these are 6 kV cable, interconnections between the units and balance of plant equipment in the composition of long cable lines laid in ditches and technological tunnels the replacement of which would involve large material resources). Cable types and manufacturers: 1. Cables supplying power for qualified equipment in the containment: КПоСГ, КПоБОВ, КПоЭСВ, КПЭТИ, КПЭТИ-FRHF, КПоПЭнг-HF, МСТП, С5XFOE-R, JS5XFOE-R. Manufacturers: - Russia. Czech Republic 2. Cables supplying power for qualified equipment outside the containment: СВТ, САВТУ, Olflex classic 110 CY, Silflex SiHF, J-H (ST) H, NHXHX, NHXCHX, N2XCH, КВВГЭ-HFLS. Manufacturers - Bulgaria, Germany, Russia; 3. Cable types 6 kV: САВБТ, САХЕмеТ, NA2XSY, ПвСГ, АLKATEL. Manufacturers - Bulgaria, Germany, Russia, France
BU-20 |  | Czech Republic | Bulgaria | 04. Concealed pipework | 58 | Can you please specify the causes of the dynamic load? Is this a frequent load? | Website | Continuous monitoring of the environmental parameters in the premises of Units 5 and 6 is carried out by means of the regular sensors of the information systems. As additional (mobile) monitoring of the environmental parameters, sensors (loggers) for temperature and humidity are installed in the hot spots. Data about radiation conditions are taken from the regular devices of the centralized radiation monitoring information and measuring system.
BU-21 |  | Czech Republic | Bulgaria | 03. Electrical cables | 47 | "..monitors the parameters of the environment in the premises through the information systems sensors." Is it a stable system or is it variable and can be installed where requested? | Website | The cause of the dynamic load on the buried pipelines is the seismic impact. According to the conclusion on the technical condition and the residual lifetime of the underground service water pipelines of t of Units 5 and 6 of Kozloduy NPP, the analysis of the results shows that due to the low pressure of the transported fluid (0,2 - 0,6 МРа), main contribution to the formation of internal forces in the pipeline elements is the seismic load. This approach is embraced in the regulatory documents: НП-031-01Design standards, Earthquake-resistant nuclear power plants, 2001; NUREG-0800 Standard Review Plan, 3.7.3 Seismic Subsystem Analysis. Seismic Category I Buried Piping, Conduits, and Tunnels; NUREG/ CR-6876 BNL-NUREG-74000-2005 Risk-Informed Assessment of Degraded Buried Piping Systems in Nuclear Power Plants; ГОСТ 32388-2013 Process pipelines, Norms and methods of strength, vibration and seismic impacts calculation. (“For pipelines in continuous contact with soil in all dimensions and directions (buried pipelines) the seismic loading is presented as an axial relative deformation in the pipeline induced by the spread seismic waves through the soil layer in which the pipelines are laid. According to these criteria, it can be talked about seismic loads that could lead to local deformations.
BU-22 |  | Netherlands | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2.5/p17 | R&D: how are developments in R&D worldwide fed back into the AMP? | email | The feedback from R & D at world level is achieved through the exchange of operating experience. After an initial review and assessment of the applicability under certain criteria, the information is analysed and evaluated. The corrective measures proposed are assessed by the Operating Experience Council. The approved corrective actions are carried out in accordance with the procedure established at Kozloduy NPP.
BU-23 |  | Netherlands | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2.6/p18 | In what AM-relevant international groups does the operator and the regulator participate? | email | Kozloduy NPP have representatives in the IGALL International Project and the End-Of-Life Working Group (EOLWG) in the Nuclear Community. Bulgaridn Nuclear Regulatory Agency have representatives in WENRA Reactor Harmonization Working Group (RHWG) – developed in 2014 WENRA Safety Reference Levels for Existing Reactors (Issue I: Ageing Management) and in 2016 Ageing Management Technical Specification for the National Assessment Reports
BU-24 |  | Netherlands | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2.6/p18 | Does Kozloduj also learn from other types of reactors than the VVER1000? | email | Yes, at Kozloduy NPP, information is also reviewed for other types of reactors, different from WWER-1000. It is implemented through the Operating Experience Feedback System for use and dissemination of operating experience. After an initial review and assessment of the applicability according to certain criteria, the information is subject to evaluation and analysis, subsequently corrective measures are drawn up, or it is brought to the awareness the personnel through an informational bulletin.
BU-25 |  | Netherlands | Bulgaria | 03. Electrical cables | 3.1.2. / p.42 | The ageing mechanisms for the SSCs cable-structures, -penetrations, and -connections are well described. What are the established acceptance criteria for these SSCs (cf. Techn.Spec. 3.1.2)? | email | Cable-bearing structures (cable routes, supports, curves, covers, guard tubes) according to the design for cable structures outside the containment, shall be made of steel sheet elements with a nominal thickness of not less than 1.5 mm, galvanized. For the cable structures inside the containment, stainless steel is used. Condition is controlled by walkdowns and visual inspection. In the case of comments established on the condition of the supporting structures (e.g. breaking of integrity, occurrence of corrosion processes), repair or replacement of supporting structures is undertaken. The new cable structures are built according to standards, the corrosion resistance is classified according to standards (IEC EN 61537, Class 6 and 7) with a zinc layer thickness of at least 60-70μm according to the requirements (ISO 1461), which according to the corrosivity categories corresponds to C1 and C2, in line with an average annual zinc covering degradation (ISO 12944), respectively <0.1 μm / year and 0.1 to 0.7 μm / year, depending on the typical environment of the buildings and premises of the NPP. The cable structures inside the containment are made of stainless steel (ISO 61537 - Classes 9C and 9D). Electrical penetrations They are classified according to standard requirements at the design stage. (e.g. IEEE 323-1983 equipment, class 1E). The standard (ГОСТ 23286-78) determines the magnitude of test voltages and insulation resistance between the individual wires and the ground screen and housing, the test time and the acceptance criteria. The operating conditions are defined by the manufacturer, including both sides of the penetration for both normal operation and emergency conditions. For electric airtight penetrations the visual and measurement control is performed: • check of the condition of the anticorrosive coating, the lacquer coating at the welding areas and the weld joints, the presence of a protective head gaskets on both sides, the presence of caps on the free cable terminals; • the tightness and the technical condition of the airtight electric cable penetrations (ECP) is checked and recorded monthly, and during outage according to the indication of the pressure gauge mounted on each ECP (according to the requirements of EN 837-1 and EN 837-2) and is controlled within the limits set by the manufacturer in line with the approved NPP procedures. Read is the absolute pressure in the penetration - Pn (according to the pressure gauge mounted on it) and the room temperature (taken down with portable mercury thermometer) at which the pressure is measured; • Preventively after outage the cable connections to the airtight penetrations are controlled with a thermal imaging camera, • Check of the insulation resistance of the cable lines along with the penetration against the the housing. Criteria and thresholds are ≥0.5MΩ for type BT and ≥5MΩ for MTT type ECP. Regarding the ageing mechanisms of cable connectors, heads, sleeves, cable terminals , we would like to point out that the acceptance criteria values for electrical conductivity are the same as the ones for the pertaining cables. They are compliant with the specification of the manufacturers of passive components . Isolation resistance of cables is measured along with the one connectors, heads, connections. According to the annual schedule with thermal imaging camera, the cable connections and the contact surfaces are preventively inspected.
BU-26 |  | Netherlands | Bulgaria | 03. Electrical cables | 3.1.2 / p.44 | Would it be possible to provide the acceptability criteria for this "Procedure on P&C Cable Testing", or provide a reference to this document? | email | Success criteria are given in the Procedure for Power and Control Cables Testing, 30.ЕЧ.RZA.ИИ.016. The cable line test is considered successful in the absence of an insulation breakdown and if the values ​​of the measured values ​​are within the limits according to Tables 1, 2 and 3. Insulation resistance of cables 0,4 kV (Table 1) Purpose Rinsul.[MΩ] Testing voltage Regulatory Documents Power cables ≥0,5 =2500 V НИЭО item 28.1 Control cables for voltage up to 1 kV ≥1 =1000 V НИЕМС table 3.23 Control cables for voltage up to 60 V ≥0,5 =500 V НИЕМС table 3.23 Referance values for testing of power cables according to ГОСТ 340-53 (Table 2) Parameter Nominal voltage of the cable [kV] - Up to 3 6 10 20 35 DC testing voltage 6Unom 6Unom 6Unom 5Unom 5Unom Electrical leak current [µA/km] 150 140 230 400 650 AC testing voltage [kV] 7,5 14 23 40 65 Insulation resistance [MΩ/km] 50 100 100 100 100 Duration of application of the test voltage according to ГОСТ (Table 3) After installation 10 minutes In operation 5 minutes
BU-27 |  | Netherlands | Bulgaria | 03. Electrical cables | 3.2 / p.49 | Did the 2015/2016 survey confirm the trends of changes in the measured parameters in the 2006-2016 period? (in other words: have the ageing phenomena proceeded as predicted, cf. the request in the Techn. Spec. of the TPR) | email | A pilot study of the condition of the cabling of units 5 and 6 and balance of plant equipment carried out in 2015/2016 includes a full set of measurements of 36 cables of 6 and 0.4 kV, and some of these 6 kV cables similar examinations were performed in 2008. A comparative analysis of the condition shows that the cables with long service life are in good technical condition and presence has been found of sections with initial form of structural changes. The cables are included in a long-term cable test schedule with a specified test volume and duration of the test.
BU-28 |  | Netherlands | Bulgaria | 04. Concealed pipework | 4.1.1.3 | It is mentioned that the grouping criteria for concealed pipework are selected according to Table 5 of Annex3 of IAEA SRS No82 (IGALL). However, Table 5 of the above mentioned document provides only definitions; and there are no grouping criteria to be found in Table 5. Could you please elaborate on what criteria were used for selecting and grouping concealed pipework? And what is the motivation for using these criteria for ageing management purposes? | email | Table 5, Annex 3 of the IAEA SRS No82 (IGALL) document provides definitions for buried and underground pipelines. According to WENRA requirements for National Reports, the Bulgarian National Report covers the concealed pipelines which belong to one group - component cooling water system pipelines which provide cooling of important to safety SSCs. Since the materials of which the pipelines are manufactured and the working media (service water) are one and the same, the working parameters and the depth of burying of the pipelines are quite similar, therefore there are two types of pipelines: buried - in direct contact with soil, and underground - in contact with air (some are inaccessible and the access to others is considerably limited). The reason for such division is the availability of degradation of the outer surface of the buried pipelines because of the presence of foreign materials in the backfill.
BU-29 |  | Netherlands | Bulgaria | 04. Concealed pipework | p.58 | It is mentioned that “All defects discovered … up to 2016 are in … buried pipelines…” Does it mean that no defects have been found in underground pipelines (p.56, 4.1.1.3)? | email | No defects have been found in the underground pipelines according to the grouping described in 4.1.1.3 and the information on the defects found in the buried pipelines presented in the text under Table 2 (4.1.2.1).
BU-30 |  | Netherlands | Bulgaria | 05. Reactor Pressure Vessels | Ch.5 | The information provided in this NAR in its chapter 5 on ageing management of reactor pressure vessels, is to a great extent qualitative. However in the Technical Specification for the NARs, the countries are requested to report in their NARs on the acceptance and action criteria for the various ageing phenomena. Apart from indicating those criteria, it is obvious that the NARs must discuss the compliance of the reactors with these criteria. Could you please provide this information? | email | There is a full compliance of the RPV condition of units 5 and 6 with the acceptability criteria set out in the RPV's AMP: 1. The mechanical properties of the base metal and the welded joints are in compliance with the forecast values of the mechanical properties and characteristics at the end of the extended operational life up to 60 years. 2. The actual value of the RPV metal's embrittlement critical temperature does not exceed the maximum permissible embrittlement temperature of the RPV's metal, determined by means of calculation of the brittle fracture toughness at the moment of expiration of the extended operational life. 3. The actual value of the fast neutron fluence of energy above 0.5 MeV on the RPV does not exceed the estimated value at the time of expiry of the the extended operational life. 4. The indications registered are in compliance with the requirements of the regulatory documents and the strength calculations made. 5. The number of fatigue cycles of the reactor plant during normal operation, abnormal operation conditions, design basis accident does not exceed the estimated forecast number specified in the AMP. 6. The geometric dimensions of the reactor pressure vessel elements determined by carrying out measurement control correspond to the requirements of the design documentation.
BU-31 |  | Netherlands | Bulgaria | 07. Concrete containment structures | 7.1.1 | Was the design changed after the replacement of the prestressing system in 2005? | email | Changes to the design have not been necessary as the new system has the same performance as the old system. The new system is more reliable, more convenient to control and maintain, as well as the fact that it results in insignificant relaxation (loss of strain) over time.
BU-32 |  | Netherlands | Bulgaria | 07. Concrete containment structures | 7.1.2 | For the acceptance criteria, a number of different codes are used, US NRC, BSS, Eurocode 7 . Are only these codes evaluated or do also the original design codes apply that have been used for design, manufacturing and construction? | email | Initially, the acceptance criteria (used for the design, manufacturing and construction of Kozloduy NPP 30 years ago) that bear relation to the ageing mechanisms of the Containment were preserved and complied with over the years and they were only added up and upgraded in the course of time according to the requirements of the new regulatory documents. It is therefore logical that the acceptance criteria for assessing the ageing mechanisms of the Kozloduy NPP are currently determined on the basis of modern regulatory documents (American NRC, European Eurocode, Russian Gosatomunzor Rosesii (NP-031-01), etc.) as they offer a deeper and more conservative assessment of the ageing mechanisms.
BU-33 |  | Netherlands | Bulgaria | 07. Concrete containment structures | 7.1.3 | NDT testing on the structure 'steel lining': what is the periodicity of this testing? 10-yearly like in many countries? | email | Yes, NDS of the steel lining of the containment is scheduled to be done every 10 years before the periodic safety review.
BU-34 |  | Netherlands | Bulgaria | 07. Concrete containment structures | 7.1.3 | How are the measurements used for trend-analysis? Is the trending used to improve the future measurement programmes? | email | The results of the measurements carried out at Kozloduy NPP are subjected to a subsequent analysis of the development trends. On the basis of the analyses carried out, recommendations are given for improvement of the future measurement programmes. The actual values ​​obtained in the measurements are compared to the design ones and previously measured values ​​in order to identify possible development trends on the grounds of which a realistic assessment of the possibility of degradation occurrence can be made. Based on the analysis of the results obtained, it is decided (if necessary) to increase the frequency of the measurements, to increase the scope of the measurements or to displace the measuring points. When making such decisions (if necessary), the necessary changes in the measurement programmes are made (improvements).
BU-35 |  | RPV expert group | Bulgaria | 05. Reactor Pressure Vessels | §5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | expert group 2 | The main challenges related to the safe operation of the reactor plant are compliance with operating limits. In this respect, the operators' practices directly affect the operating parameters of the reactor plant equipment and have a significant role in reducing the degradation of the metal of the equipment, in terms of mitigating actions described in the RPV AMP. Reduction in reactor heat-up and cool-down rate during startup/shutdown from/to parameters in order to reduce the fatigue stress of individual components.
BU-36 |  | Concrete containment PCPV expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 14 | 2.3.1.5.1. Do the predictive maintenance use the trending calculations of the data collection and records storage system ? | expert group 4 | Predictive maintenance of equipment at Kozloduy NPP is planned based on recommendations from trends analysis made through calculations of input data from the data collection and record keeping system. The analyses are based upon approved procedures and methodologies. The results are published in writing in the form of: analyses from the diagnostics of the technical condition of machines and equipment (vibration control, thermo-visual monitoring, control of a complex of valve characteristics, electric actuators and other types of diagnostic control); statistical analyses of faults and defects and trends in the technical characteristics of equipment and systems; summary reports on the results of non-destructive testing of base metal, welded joints and welded surfaces; analyses of corrosion test results of equipment and pipelines, analyses of monitoring of civil structures.
BU-37 |  | Concrete containment PCPV expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 11 | 2.3.1.2 What method was used to determine the effect of civil structures on the lifetime of power plant ? ("When screening the civil structures only those that could limit the operational lifetime of the power plant were selected.") | expert group 4 | The civil structures that have impact on the plant lifetime and have been selected for AMR are all civil SSCs, which are: : 1. safety-related and retain their functional characteristics during postulated initiating events; which ensure primary coolant integrity, capability of shutting down the reactor and maintaining it in a safe shutdown state, and its capacity to prevent emergencies or mitigating their consequences; 2. not safety-related, but their failure may impair the safety functions of other safety-related SSCs; 3. not safety-related, but are to perform their functions throughout the operating lifetime in the event of a failure of the Reactor Protection System and station blackout; 4. not safety-related, but are to perform their functions throughout the operating lifetime in compliance with the fire safety and environmental protection requirements; 5. BOP SSCs required for sustainable electricity generation throughout the period of extended operation.
BU-38 |  | Concrete containment PCPV expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 11 | 2.3.1.3. What are the 2 subgroups of civil structures ? What are the subgroups used for? | expert group 4 | The civil structures are divided into two subgroups according to their importance and operating conditions. The first group includes important civil structures specified in the List of safety-related SSCs subject to maintenance and repair at Units 5&6. The second group covers all other facilities. This division is for the purposes of prioritisation and conduct of maintenance and repair works.
BU-39 |  | Concrete containment PCPV expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 13-14 | 2.3.1.5.1. What is the form (paper or electronic) of the archived documentation ? Have the collected and archived data been checked that they are complet and up-to-date ? Was the system verified and validated ? | expert group 4 | Documentation is archived both as hard copies and electronic copies in a special data base. In compliance with the regulations established at Kozloduy NPP, archived documents are reviewed for completeness and validity. The current plant system for achieving documents and records is subject to review in compliance with the internal audit system established at Kozloduy NPP.
BU-40 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 88 | 7.1.1.1. Are all the outer concrete surfaces of the cylindrical walls protected by an epoxy anti-corrosion coating ? Is there any coating (protective layer) on the steel linear ? | expert group 4 | Up to elevation 45.00, the containment does not have external concrete surfaces exposed to the weather and it is surrounded by a reinforced concrete structure (concrete shield building). On the outside, the containment cylindrical part is made of sprayed concrete protected by epoxy anti-corrosion coating. Above elevation 45.00, the open part of the containment has additional protection of corrugated galvanised iron. The inner surface of the containment (its steel lining) is protected by epoxy primer and then painted with epoxy enamel.
BU-41 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 91 | 7.1.1.3 Do the special reports contain a comparison with the results of previous measurements? Are predictions of trends in the conclusions? | expert group 4 | Yes. The special reports/records on containment monitoring include a comparison with the results of previous measurements. The geodetic survey and containment monitoring performed on an annual basis also include all the results of all the previous measurements as well as their comparison.
BU-42 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 92 | 7.1.1.3 Are there any substantive changes that justify the quarterly release? | expert group 4 | There are no such significant changes. The main purpose of the Quarterly Report on containment monitoring using the Containment Cable Prestressing Computer Monitoring System (stipulated in the current plant procedures) is to obtain, analyse, and archive detailed information (of high frequency of recording) about the actual tendon prestressing forces during various periods of time in order to obtain development trends.
BU-43 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 89 | 7.1.1.1 What was the reason that the dome received treatments with materials that prevent moisture entry into the reinforced concrete in 2014 ? | expert group 4 | The main reason for treatment of the Units 5&6 domes in the period 2013-2014 was the presence of microcracks and conditions for vegetation growth in the deformation joints of the dome which were detected during routine visual inspections.
BU-44 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 96 | 7.1.2.2. Are the derived acceptence criteria from Table 6, exact quantitative ones ? | expert group 4 | The acceptance criteria shown in Table 6 are quality criteria for expert assessment of detected defects (current condition) mainly based on visual inspections. Those criteria concern only defects/degradation mechanisms for which more accurate quantity criteria could hardly be established, such as: concrete erosion and cavity formation, shrinkage , etc.
BU-45 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 95 | 7.1.2.2 Do you have acceptence criteria for leakage (integral and local leak tightness tests) ? Is the leakage of emergency make up tank permitted ? Is the emergency make up tank leakage measured on-line ? | expert group 4 | It is a basic rule that such leaks are not permitted. The Emergency Feedwater Tank (room ГА-201) is lined with a layer of 6mm thick steel sheets (Вст3сп5) and second layer of stainless steel sheets (08Х18Н10Т steel), leakage monitoring between the two layers being performed during plant walkdowns through inspection and measurement of the leakage flow rate. When leakage is detected, remedial actions shall be taken.
BU-46 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 90 | 7.1.1.3 The planning, organisation and implementation of condition monitoring activities for the airtight structures, foundation block and auxiliary facility, together with the interpretation of results have been regulated. Is the periodicality of monitoring depend on the measured value, to the trend of the values ? | expert group 4 | Yes. The frequency of the performed monitoring of the condition of airtight structures, foundation block and concrete shield building depends on the measured values and is connected to the trend in the development of values. For that purpose, all results of the performed monitoring are subject to a follow-up analysis of the trends of development, and the obtained results are used for future improvements (if required) of the monitoring programmes, which can be related to: change in the monitoring frequency, increase in the measurement scope, relocation of the measurement zones, etc.
BU-47 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 90 | 7.1.1.3 Who and what determines the need of extraordinary visual inspections ? | expert group 4 | The additional visual inspection of the containment is obligatory performed after significant calamities and industrial accidents, which have influenced the building and facilities such as.: fires, floods, earthquakes, etc. Additional visual inspection is also performed in case of a report from the corresponding administrative unit or other authorized bodies for non-conformities or phenomena occurred between the planned periodic inspections of the facility structure. The scope and volume of the additional visual inspection are established.
BU-48 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 90 | 7.1.1.3 How happens the documentation of visual inspection ? What is the method and form of the documentation ? (handwritten note or photo or film, or digital recording with the time and position stamp …) | expert group 4 | The visual inspection is performed in compliance with the plant requirements. The containment monitoring results are documented in special reports and, if required, they also contain pictures.
BU-49 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 95 | 7.1.2.2 How to determine the significance of the ageing mechanisms ? Are the values of criteria sufficient to categorizes the defects ? It means for example: there are 2 criterion values for the average measured force in the tendons, one is the criterion of the significant defects and the other one of deviation ? | expert group 4 | The criteria for determination of the significance of the identified defects/ deviations (as given in Table 6) are quality criteria for expert assessment on the basis of mainly visual inspections, and they apply only to ageing mechanisms which have not been listed in Table 6 and for which it is very difficult to identify the accurate qualitative assessment criteria such as: concrete erosion and cavity formation,shrinkage/cracking , etc.) (this is indicated in the last record in item 7.1.2.2). Therefore, there are no two values of a criterion for assessment of the average measured force in the prestressing tendons ; for its assessment, only criteria indicated below are valid (in the first paragraph), below Table 6.
BU-50 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 95 | 7.1.2.2 Is there a predefined quantitative or qualitative features for definition for the categorization of all type of defects ? | expert group 4 | Yes, there is. Degradation mechanisms (defects, deviations) for which it is difficult to define precise quantitative evaluation criteria (for example, concrete erosion and cavity formation,shrinkage , etc.) are evaluated/categorized according to the quality characteristics given in Table 6. The remaining degradation mechanisms (defects, deviations) are evaluated/categorized according to the quality characteristics given in Table 6.
BU-51 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 95 | 7.1.2.2 Have no acceptance criteria been established for the leak tests (Containment Structure Leak Tests, Integral and Local tests) ? | expert group 4 | Yes, there is. The acceptance criteria for leak tests of the containment are described in details in procedure for leak tests of the containment as follows: - containment tests at the stage of reactor closure are considered successful if there are no air leaks in the seals and connections of the leaktight circuit at pressure - 400 mm H2O, the pressure drop rate is <2 mm H2O/h; - containment leak tests at overpressure of 0.7 kgf/cm2 are considered successful if there are no air leaks in seals and connections of the leaktight circuit, the obtained data for the air parameters are sufficient to define the containment leak value and interpolated pressure value for the containment at calculated pressure of 4 kgf/cm2 are not higher than 0.3 % of its value for a 24-hour period. The local tests are : - tests of the airlocks are performed at overpressure of 0.3 kgf/cm2, as the acceptance criteria is leakage <0.835 l/h - testing of the transport hatch is performed at overpressure of 0.6 kgf/cm2, the acceptance criteria is leakage <0.835 l/h.
BU-52 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 96 | 7.1.2.2 How the places have been defined where the alkali silicon reaction, ettringite formation are measured for the acceptence criteria ? | expert group 4 | The locations where ASR and DEF are measured in accordance with approved programmes. The studies are performed according to the requirements of the BDS EN 196-2:2013 Cement testing methods. Part 2: Chemical analysis of cement, ASTMC 856 „Standard Practice for Petrographic Examination of Hardened Concrete” and AASHTO T299 „Standard Method of Test for rapid Identification of Alkali-Silica Reaction Production Concrete.”
BU-53 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 96 | 7.1.3 Do you have a predifined test program for monitoring, testing and sampling ? | expert group 4 | No, we do not. Due to the specific nature of these activities (determination of the location and scope of sampling), similar programmes are prepared for every specific case immediately before performance of the study, based on the previous expert analysis of the results of the previous measurements.
BU-54 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 97 | 7.1.3 How often do you take a concrete sample? What determines where and when? | expert group 4 | Sampling from the containment concrete of Units 5&6 is stipulated in the plant documentation and is performed every 10 years. The key factors for sampling point location are: the most stressed locations determined based on expert analyses and the available checking calculations; locations where defects were visually detected; locations allowing comparison with previous samples. The results are updated and corrective actions taken including also a change in the sampling frequency, if required.
BU-55 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 98 | 7.1.4 Did you already need to perform preventive/corrective actions regarding concrete structures ? If yes, please give examples of urgent, necessary and recomended actions. | expert group 4 | Yes, there are already similar needs for taking corrective actions in terms of concrete structures of the containment and Reactor Building, but these were a tertiary priority (recommended actions), as well as secondary actions (required actions with an option for their postponing until the next outage). For example: -rehabilitation of the waterproofing coating of the protective concrete and the drainage of the domes of the containment of Units 5&6 with modern building materials which provide better protection against the ingress of moisture into the reinforced concrete; - restoration of the damaged varnish paint coating and the plaster of the Reactor Building structures as well as the self-dissipative flooring.
BU-56 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 98 | 7.2 Is it true that the examples listed in section 7.2 for improving metal structures and coatings belongs to the the second priority actions ? | expert group 4 | It is true that the listed activities/actions (Page 98) for improvement of the condition of metal structures and corrosion-resistant coatings are activities of primary priority (urgently required for performance of maintenance works). The examples listed in item 7.2 refer to structures of various significance. They are activities/actions of a secondary priority (required actions with option for postponing) as well as a tertiary priority (recommended actions). When determining the deadlines for the outages, high-priority structures are the ones from the List of safety-related SSCs subject to maintenance and repair at Units 5&6.
BU-57 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 101 | 7.2 Are you planning any preventive/corrective maintenance to eliminate the corrosion problem you have discovered (reinforcement concrete)? | expert group 4 | No need of such a preventive maintenance was identified. Concrete resistance a bit lower than the reference one was only detected at two locations, the values indicating just a possibility for occurrence of surface corrosion on rebar pieces, not that such occurrence was detected (no values below the established criteria have been measured). Based on the expert analyses conducted, the relevant locations will be monitored.
BU-58 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 102 | 7.3 Were there any suggestion of the review procccess to change the frequency or the content of periodic observations, assessment and maintenance of the structures during the extended lifetime ? | expert group 4 | Upon completion of the AMR, there were no such recommendations/suggestions concerning the containment in particular, but there were such recommendations/suggestions for the Reactor Building, e.g.: it was recommended to monitor more often the condition of the concrete in the compartments of the concrete shield building of the Reactor Buildings at Unit 5&6 through non-destructive tests, measurement of electrical potential between the reinforcement and concrete, and measurement of the carbonization depth in the concrete) - once every 5 years. This was covered by the update of the Ageing Management Programmes.
BU-59 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 97 | Please expain in more detail "instrumentation testing to take a picture of the rebars in typical cross sections and elements of the bearing reinforcement concrete structure of the buildings" | expert group 4 | Pictures of the position and diameter of rebar pieces (longitudinal and transverse) in concrete cross-sections are taken in accordance with the requirements of BS 1881-204:1988 „Testing concrete. Recommendations on the use of electromagnetic covermeters.” The thickness of the protective layer as well as the position and diameter of rebar pieces in structural elements is measured using a dedicated device like Ferroscan PS200 manufactured by Hilti.
BU-60 |  | Concrete containment PCPV expert group | Bulgaria | 07. Concrete containment structures | 101 | There is a long list of repairs and refuirbishment undertaken at KNPP following inspections in 2008. Were any changes in the ageing management system identified to ensure that the structure does not degrade to a condition where this level of repair and replacement is needed ? | expert group 4 | The specific maintenance activities performed after 2008 were actions of secondary priority (required actions with option to postpone until the first outage) as well as of tertiary priority (recommendations). Based on the expert analyses, it was identified that they do not require changes in the existing Ageing Management Programmes.
BU-61 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 52 | The only system described in the report is the CCWS. Why are other systems (e.g fuel lines, fire systems, other water supplies) excluded? This is inconsistent with other VVERs | expert group 5 | The Ageing Management System at Kozloduy NPP covers the safety-related concealed pipelines. The Ageing Management Programme for concealed pipework includes only the service water system used for the cooling of essential loads. The other concealed pipelines, such as fire system, emergency and alternative make-up system of spray pools, are not included in the ageing management programme due to the performed modernization and their replacement with HDPE pipes. The concealed pipework for fuel supply has been decommissioned.
BU-62 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 61 | You give a uniform corrosion rate and yet some pipework has clearly failed due to pitting or another such mechanism. How do you calculate the non-uniform corrosion rate or lifetime for other failure mechanisms and how does this compare to the current service life? | expert group 5 | Based on the results of the recent studies (visual inspection of the external surfaces, remote visual inspection of the internal surface and thickness measurements) of the concealed pipework, it can be seen that the main mechanisms of degradation are general corrosion and pitting corrosion. No other mechanisms were identified, which does not require calculation of corrosion rate for other degradation mechanisms. The thickness measurements results show that in some sections (mainly in the areas surrounding the pressurizers at the entry to the Reactor Building, and in the individual monitoring shafts) there are pipes installed with a thickness higher than the design thickness (nominal) with a higher margin. The average corrosion rate was determined upon destructive and non-destructive analyses to determine the thickness of the walls of the different sections of the concealed pipework (with different diameters, thickens and operating parameters) after excavation, cutting out of the defective sections in the shafts and concrete tunnels. Thus, in the calculations for lifetime extensionfor of this type of pipes, the average corrosion thinning of up to 1.2mm by the end of the operating lifetime (60 years) was considered; uneven corrosion distribution rate was not considered.
BU-63 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 55 | It is stated that system components are grouped according to their degradation level. The degradation levels should be elaborated. | expert group 5 | Incorrect translation in section 4.1.1.1 (page 55), which changes the meaning of the text. The correct translation is: "•identifying system components with some level of degradation requiring repair or replacement, and further analysis taking into account a number of acceptance criteria." as opposed to the incorrect "• grouping of system components according to their degradation level, requirements for repair or replacement and analysing by considering a number of acceptance criteria."
BU-64 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 61 | It is stated that at the end of the extended operational life shows that the corrosion thinning of all pipelines will be 1,2 mm. How long an operational life of CCWS underground pipelines have been extended? | expert group 5 | The operating lifetime was extended by 2051.
BU-65 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 67 | Please give more informations about the regulator's assessment and conclusion on ageing management of the concelead pipework (Section 04.3 of WENRA TS): in particular, describe the regulator's experience from inspection conducted on the activities carried out by the licensee and give a judgement about hte adequacy of the licensee's SSC specific ageing management programme. | expert group 5 | During the implementation of the Kozloduy NPP Units 5 and 6 Lifetime Extension Project (LEP) the regulator carried out periodic inspections of the Component Cooling Water System (CCWS) buried pipelines aging and the progress in implementation of the measures, related to the specific assessment and analysis for confirmation of the preliminary residual resource of these pipelines. The most important activities carried out by Kozloduy NPP are: verification of calculations, quantitative assessment of the residual life of buried pipelines and specific assessment and replacement of compromised pipeline sections. The regulatory body has carried out a thematic inspectionс in order to verify the compliance with regulatory requirements of the activities during operation, maintenance and aging management of the of the systems, strictures and components (SSC) of the Kozloduy NPP Units 5 and 6 Component Cooling Water System (CCWS), element of which are buried pipelines. The status, organization, requirements and control of the operation and maintenance activities have been checked. Working and reporting documents defining the operating requirements; the technical support of the system; maintaining the water chemistry control, conducting the functional tests; schedules, instructions, programs, procedures, protocols, prescriptions and reports on the implementation of the LEP measures have also been checked. The implementation of technical solutions and measures related to the investigation of buried pipelines by magnetic methods and modification and replacement of elements of the system were considered. The main conclusions are that the operation and maintenance of the hidden pipelines were carried out in compliance with the legislative requirements and according up to date internal documents, the dominant aging mechanisms are properly defined, effective methods for monitoring and slowdown of the ageing process of the pipelines were developed and used. The effectiveness of AMP implementation is confirmed by the results of the visual inspections and the non-destructive testing of wall thicknesses of buried pipelines, which confirm that by the end of the extended operational life of Kozloduy NPP buried pipelines will retain their geometric characteristics within the required standard limits.
BU-66 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 53 | What is the basis for distinguisihing of closed and open cooling circuit. The US practice adopted by Czech NPPs uses the term "closed" cooling circuit for circuits not connected with atmosphere (e.g. circuits between diesel engines and water/air cooler). The other option is a "open" cooling circuit, which can be once-through or recirculating. heat sink for recirculating open cooling circuit can be spray pond (e.g. ESW of VVER1000) or natural-draft or fan cooling towers. | expert group 5 | The pipelines are recirculation type functioning in an open cooling circuit with the spray pools.
BU-67 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 55 | The pH of service water is unusally high for un-treated water. What treatment is used for ESW. What alkalizing agent is used? | expert group 5 | The essential loads service water system is treated through automatic dosing of reagents such as dispersing agents, inhibitors, and biocides. The aim is to minimize the corrosion process and deposition of biofouling, sludge, and other corrosion products on the inner surfaces of the pipework and heat exchanging surface. рН=7.8-9.0 is required.
BU-68 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 53 | Excavated material (I suppose soil) is used as the backfill. This is kind of unususal setup. The most common setup includes sand bed, sand backfill close to pipe, gravel backfill ouside the sand and soil as an outmost layer. The very common root cause of degradation of buried piping is using of too little of sand and soil containing stones and debris during commissioning. Debris consequently scratches coal tar protection layer allowing contact of water from soil with bare steel piping followed with CUI (corrosion under insulation). Is the setup described in the report correct? | expert group 5 | In accordance with the design, a supper-thick three-layer protective tape, "Sil-B (green colour)," is used and it is tightly glued to the outer surface of the pipework. The new (repaired) coating when recovering the external insulation of the pipes consists of insulation tape “ID-16038” and epoxy primer“ID-45747”. The pipes are laid on a sand bed and covered with a tight sand backfill consisting of a mixture of sand and loess (there is no gravel). The insulation damage was caused by the foreign materials in the backfill. Upon repair of the insulation, sieved sand is backfilled to cover the pipework followed by a layer of coarse aggregate and a part of the excavated material is used to completely cover the excavation.
BU-69 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 55 | The (most) critical sections are both sections with intensive turbulent flow (elbows, Tees) and stagnant flow sections. What intensive degradation mechanism is expected for these areas? | expert group 5 | The turbulent flaw effects on the discharge pipelines with flow pressure of 0.46 MPa are insignificant. Erosion-corrosion wear can be indicated as a potential ageing mechanism but not flow accelerated corrosion, i.e.gradual removal of the metal corrosion products with liquid circulation. The results of ultrasonic thickness measurement does not show significant thinning of the walls of fittings (elbows, Tees). In the stagnant flow sections a local corrosion is expected (spots, pitting), which is confirmed by the assessment results.
BU-70 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 56 | The grouping criteria are selected according to tab. 5 at Annex 3. There is only one anxex in the Bulgarian report. There are no criteria for pipeline grouping described in IGALL AMP125. Please provide basis for criteria selection. | expert group 5 | Table 5, Annex 3 of the IAEA SRS No82 (IGALL) document provides definitions for buried and underground pipelines. According to WENRA requirements for National Reports, the Bulgarian National Report covers the concealed pipelines which belong to one group - component cooling water system pipelines which provide cooling of important to safety SSCs. Since the materials of which the pipelines are manufactured and the working media (service water) are one and the same, the working parameters and the depth of burying of the pipelines are quite similar, therefore there are two types of pipelines: buried - in direct contact with soil, and underground - in contact with air (some are inaccessible and the access to others is considerably limited).
BU-71 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 58 | What is technical basis for including of FAC (or erosion-corrosion) between actual ageing mechanisms? FAC is not possible in oxygen containing water line such is ESW. Usual concentration of oxygen in aerated water such is water from spray pond is about 10 ppm. 10 ppb of oxygen is dosed to condensate water in fossil power plants to effectively mitigate FAC. Also experience from Kozloduy cited in the report confirms no FAC at ESW lines. | expert group 5 | It is indicated in the text that the potential ageing mechanisms are given in Table 2. The erosion-corrosion wear is considered, i.e. gradual removal of the metal corrosion products with liquid circulation due to the presence of mechanical impurities (the spray pools are exposed to weather). The flow accelerated corrosion does not occur in this type of pipelines. The erosion-corrosion wear as a potential ageing mechanism is also considered in the documents for lifetime extension of this type of pipelines. The degradation mechanisms identified by now are general and local corrosion, as indicated in the text below the table.
BU-72 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 59 | Please describe magnetometric testing of coating. No open literature is available on the method. Is it the CIPS, ACVG, Current Attenuation Survey or DCVG or some other similar method? | expert group 5 | The metal magnetic diagnostics (based on the metal magnetic memory method) requires the use of metal magnetic memory device to define the stress concentration. The devices allow to record the changes in the magnetic field of the Earth caused by the change of tube metal permeability in the stress concentration areas, when the operator is moving along the axis of the buried pipework. Classification of magnetic anomalies is performed based on the criteria used in the MMM method and related standards used for the inspection. References (can be found on the Internet): РД 102-008-2002. Procedure for condition monitoring of the pipelines according to the contact free magnetic memory method, GOST (R) ISO 24497-1-2009. Non-destructive testing. Metal magnetic memory method. Part 1. Terms and definitions. GOST (R) ISO 24497-1-2009. Non-destructive testing. Metal magnetic memory method. Part 2. General requirements
BU-73 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 61 | What method is used for evaluation of pipe ovality? | expert group 5 | The verification for ovalization and static resistance of the cross-section is carried out for a section of a gravity pipeline Ø1220х8, since this pipeline is buried at the deepest level and has the highest ratio of cross-section diameter to thickness. The calculations were made according to NUREG/ CR-6876 BNL-NUREG-74000-2005 Risk-Informed Assessment of Degraded Buried Piping Systems in Nuclear Power Plants and American Lifelines Alliance, ASCE Guidelines for Design of Buried Steel Pipe, 2001 (with addenda through February 2005).
BU-74 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 61 | Finite Element Method requires very accurate inputs aka wall thicknesses to get benefit over code calculations. How do you get them without an excavation? | expert group 5 | The actual characteristics of buried pipelines are defined on the based of the field and laboratory studies. Upon analysis of all the results of destructive and non-destructive testing of the thickness of the pipelines and the assessment of their reliability and feasibility, the average estimated corrosion thinning for all pipelines extrapolated to the end of the period of extended operation, by 2051, was accepted to equal 1.2 mm. The finite element models of the analysed sections were constructed taking into account the actual geometry, estimated wall thickness, and design characteristics of the material.
BU-75 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 61 | The calculated corrosion wear 0,6 mm/30 yrs applies for uniform corrosion. Do you have any criteria or results for CUI? | expert group 5 | In the sections where no damages to the external insulation have been found, the insulation has a good adhesion to the pipework metal. In fact, when removed, no traces of external corrosion are detected underneath. The number and location of the sections with damaged insulation are stochastic values and are not subject to specific quantitative assessment. А common criterion for minimal wall thickness was established and validated based on calculations.
BU-76 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 62 | What kind of portable device was used within an Nalco treatment period? What OpEx do you have with this device? | expert group 5 | We haven't had any OpEx when using the device for measurement of the corrosion activity of water; the device is a property of the company and was used during the contract performance.
BU-77 |  | Concealed pipework expert group | Bulgaria | 04. Concealed pipework | 63 | How does penetration testing address any of mentioned degradation mechanisms (uniform corrosion, pitting, CUI or even FAC)? The ageing effect of any of these degradation mechanisms is not a crack. | expert group 5 | In the text it is said that the penetration testing (PT) is performed on the basis of the visual inspection results. This method is applied in the event of a crack detected on the external surface of the pipeline, in case of uncovered pipework, and upon repair of welded joints.
BU-78 |  | Concealed pipework expert group | Bulgaria | 03. Electrical cables | Chapter 3.1 | Is any software used for calculation of residual life time of cables? | expert group 5 | No software was used.
BU-79 |  | Concealed pipework expert group | Bulgaria | 03. Electrical cables | Chapters 3.2, 3.3 | Were some weaknesses of AMP program identified by the licensees and/or regulator? | expert group 5 | Low voltage I&C cables in the MILD environment were not included in the scope of the AMP due to their recent replacement. The activities for their inclusion in the scope of AMP are under way.
BU-80 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 9 | In the description of the Overall Ageing Management Programme is the Lifetime Management Programme (the PROGRAMME) mentioned. Please provide reference to this programme. | expert group 3 on other topics / expert group 1 | The programme identification number is 30.ОУ.00.АД.58.
BU-81 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 16 | From the description still remain unclear which (specific) key standards and guidance are used to asses ageing. Please specify more in detail. | expert group 3 on other topics / expert group 1 | The ageing management review was performed in compliance with the requirements of the Methodology for performance of a comprehensive study and assessment of the residual lifetime of the equipment and facilities at Units 5&6 of Kozloduy NPP. The requirements of the following TSDs are applied for the development of the Methodology: • Safe Use of Nuclear Energy Act, State Gazette (SG), issue 63, dated 28.06.2002. (SUNEA). • Regulation on Ensuring the Safety of Nuclear Power Plants; • Regulation on the Procedure for Issuing Licences and Permits for Safe Use of Nuclear Energy, dated 4.05.2004; • Regulation No.4, dated 21.05.2001 on investment projects scope and contents; • Regulation on the safe management of radioactive waste; • Regulation on Ensuring Safety of Spent Nuclear Fuel Management; • IAEA, Ageing Management for Nuclear Power Plants, Safety Standards Series Safety Guide No. NS-G-2.12, IAEA,Vienna (2009); • IAEA, Safe Long Term Operation of Nuclear Power Plants, Safety Reports Series No. 57, IAEA,Vienna (2008); • IAEA, Methodology for the Management of Ageing of Nuclear Power Plants Components Important to Safety, Technical Reports Series No. 338, IAEA, Vienna (1992); • IAEA, Data Collection and Record Keeping for the Management of Nuclear Power Plants Ageing, Safety Reports Series No. 50-P-3, IAEA, Vienna (1991); • IAEA, Equipment Qualification in Operational Nuclear Power Plants: Upgrading, Preserving and Reviewing, Safety Report Series No. 3, IAEA, Vienna (1998); • IAEA-EBP-SALTO‘ Final Report of the Programme on Safety Aspects of Long Term Operation of Water Moderated Reactors, Recommendations on the Scope and Content of Programmes for Safe Long Term Operation, Vienna, (2007); •Maintenance, Surveillance and In-service Inspection of Nuclear Power Plants, Safety Standards Series Safety Guide No. NS-G-2.6, IAEA, Vienna (2002); • IAEA, Periodic Safety Review of Nuclear Power Plants, Safety Standards Series No. SSG-25, IAEA, Vienna (2013) •General Provisions for Ensuring Safety of Nuclear Power Plants, ОПБ-88/97 – ПНАЕ Г-01-011-97. • Rules for arrangement and safe operation of nuclear installation equipment and pipelines, ПНАЭ Г-7-008-89; •Норми за изчисляване на якостта на оборудването и тръбопроводите на ядрени съоръжения (Standards for strength calculation of nuclear facility equipment and pipelines), ПНАЕ Г-7-002-86. • Equipment and pipelines of nuclear energy facilities. Welding and overlaying Basic Rules, ПНАЕ Г-7-009-89. • Equipment and pipelines of nuclear energy facilities. Welds and weld overlays. Inspection Rules, ПНАЕ Г-7-010-89. • Basic rules for lifetime extension of nuclear power plant unit, НП-017-2000. • Administrative technical specification of the Federal Department of Environmental, Technological and Nuclear Surveillance of state functions for licensing of activities in the field of nuclear energy use; Order of Ministry of National Resources and Natural Environment No.262, dated 16.10.2008; • Structure and content of the report on results from nuclear power plant unit comprehensive study for its lifetime extension, РБ-027-04; • Analysis of the NPP Unit Non-conformances with the requirements of current regulatory documents, РБ-028-04; • Structure and content of materials on justifying residual life to extend the nuclear power plant unit operation, РБ-029-04; • Analysis of operating experience for nuclear power plant unit lifetime extension, РБ-030-04; • recommendations for the content of the report on the comprehensive assessment of safety of the operating units of nuclear power plants (ОУОБ АС), РБ-001-05;
BU-82 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 16 | Please provide more details (references) to procedures/ instructions/ documents for the identification of ageing mechanisms, mentioned in the description. | expert group 3 on other topics / expert group 1 | The comprehensive study, conducted within the ageing management review, was performed in compliance with the requirements of the Methodology for performance of a comprehensive study and assessment of the residual lifetime of the equipment and facilities at Units 5&6 of Kozloduy NPP. There are references in the SSCs Ageing Management Programmes, to the specific documents about ageing mechanism identification. The technical condition of SSCs with the identification of prevailing and potential ageing mechanisms were identified during the comprehensive study;
BU-83 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 17 | Please provide more detailed information on how using of R&D programmes are organised in processes/ procedures of the overall AMP | expert group 3 on other topics / expert group 1 | In compliance with the current Kozloduy NPP system for incorporation of changes in current documentation, the information from implemented study and development programmes is incorporated into the processes/instructions of the overall AMP.
BU-84 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 17 | Please provide more detailed information on which R&D programmes/ projects licence holder is participating. | expert group 3 on other topics / expert group 1 | Kozloduy NPP experts take part in the IGALL project.
BU-85 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 32 | "In some cases, the experience from operation or research results raises the question of the timeliness of previous assessments, such as assessments of the life extension and qualification of installed equipment. After evaluating this information, Kozloduy NPP assigns performance of additional research and development activities." Could you please provide some example (s)? | expert group 3 on other topics / expert group 1 | The calculations for life extension are made with the help of modern methods, knowledge and new, up-to-date calculation models and software.
BU-86 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 34 - 35 | From the description remain unclear if regulatory does inspections on implementation of the overall AMP. If so, how often are inspections carried out? | expert group 3 on other topics / expert group 1 | The inspections for effectiveness and implementation of the overall AMP are carried out within the framework of the implementation of: the long-term (three-year) inspection program; during the periodic safety review - every 10 years; during the inspections of the readiness of the units for startup and operation, once per year after each annual outage, and resulting from updates of the overall AMP if needed. The frequency of inspections is determined in accordance with the long-term (three-year) inspection program, where the individual activities and specific programs that characterize the overall AMP are described and have to be covered within the three-year period. In general, during this period, there are two topical inspections annually covering the main elements of the overall Aging Management Program (AMP)
BU-87 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 32 - 35 | Do the regulatory identified any weaknesses during the assessment of the overall management programme? | expert group 3 on other topics / expert group 1 | No significant inconsistences that require substantial amendments were identified during the periodic regulatory review and assessment of the overall Aging Management Program (AMP).
BU-88 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 10 | Section 2.3.1.1. states that a special structural unit has been set-up within Kozloduy NPP PLC to develop and maintenance the Ageing Management Programme (AMP). Please explain the competency requirements and training provided (within respect to Ageing Management) for personnel in this unit responsible for the development of the AMPs. | expert group 3 on other topics / expert group 1 | The experts who belong to this specialized unit need to have master's degrees and qualification in energy, electrical engineering, electronics, instrumentation and control; and physical sciences. As a minimum, they need to have five-year experience in the plant operation or maintenance. Specialised training on life extension projects was delivered to experts by IAEA experts in connection with the conduct of Pre-SALTO Missions at the Plant.
BU-89 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 11 | Section 2.3.1.2. summarises the main groups of SSCs covered by the Ageing Management Programme. Please explain whether equipment provided to mitigate severe accidents is included within the ageing management programme. | expert group 3 on other topics / expert group 1 | The Ageing Management Programme covers equipment used for mitigation of severe accident consequences. Examples of such equipment are the passive autocatalytical recombiners and the containment filter venting system.
BU-90 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 11 | Section 2.3.1.2. states that SSC's required to deal with internal flooding are one of the groups of SSCs covered by the Ageing Management Programme. Please explain whether SSCs to prevent external flooding are included within the ageing management programme. | expert group 3 on other topics / expert group 1 | The paragraph tackles the issue of internal fire (translation error).
BU-91 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 12 | Section 2.3.1.4 lists the ageing management programmes (AMP) developed and implemented at Kozloduy NPP. This explains that the primary circuit pipework, vessels and RCPs are included within the AMP. Please clarify whether the emergency core cooling system is included within the programme. | expert group 3 on other topics / expert group 1 | Both the passive and the active part of the Emergency Core Cooling System are within the scope of the Overall Programme.
BU-92 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 17 | Section 2.3.2.2 states that acceptance criteria are determined for each component or equipment of the same type (commodity group) and that these are related to the degradation mechanisms for the SSC. Please explain the relationship between these acceptance criteria and the reliability claims made in the station's safety analysis. | expert group 3 on other topics / expert group 1 | There is no such text in Section 2.3.2.2., the text coresponding to the question is given in Section 2.3.2.4. of the National Assessment Report. The referred paragraph states that the specified acceptance criteria refer to the identified ageing mechanisms of components or a group of same type components, and that they ensure the design functions performed by each of these components. If the question is in connection between the requirements for the SSCs reliability in the SAR “station’s safety analysis” and the specified acceptance criteria, we can say the following: The SAR covers the requirements for qualification and safety classification of all SSCs. Different requirements (standards, design codes, etc.) are used for the design, manufacture, maintenance and operation of SSCs depending on the specified SSC safety classes. It must be noted that all SSCs, classified as important to safety, are included in the scope of the AMP. Therefore, the requirements of the standards or codes used for the design, manufacturing, or maintenance of the SSCs of the respective safety class, were applied for the specification of the acceptance criteria for the identified degradation mechanisms.
BU-93 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 20 | Section 2.3.3.1 describes a large number of diagnostic systems deployed to monitor the performance of SSC's in service including the automatic Leak Before Break System (FLUS). Please explain how the data from the FLUS is reviewed and trended and the competency requirements for personnel undertaking these duties. | expert group 3 on other topics / expert group 1 | The digital values of each periodic measurement of a dew point, the mass flow rate and other measured parameters (pressure, temperature) are recorded and their compatibility - verified. Data are stored in a circular buffer (up to 500 measuring cycles). data of the last 500 measurements are stored and selected "trend data" of the last 1000 measurements which are either a maximum or a minimum of the dew point in selected ranges of positions along the monitored circle. The user is able to continue analysing in autonomous mode. The use can save the data either on a CD or other suitable device (USB memory stick). The normal functioning of the leak detection system is provided by: - the specialists of the respective laboratory, within the regular work time; - the operating personnel (Senior Reactor Operator, Plant Shift Supervisor) during the shift.
BU-94 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 24 | Section 2.3.3.2. states that the Technical Council is established to take decisions regarding the replacement or repair of components or to specify additional inspection activities. Please confirm the responsibilities of the Technical Council and its composition (including its ability to access independent technical advice). | expert group 3 on other topics / expert group 1 | The Expert Technical Councils are Consulting Body to Kozloduy NPP EAD Chief Executive Officer. One of the objectives of these Councils is to enhance the level of safety, reliability and efficiency of the nuclear power facility operation. They are convened to discuss technical and/or process issues, projects, analyses, suggestions and developments of specific subject-matters. Specialists of given division, performing plant operating activities and having respective competence, take part in the council. Expert Technical Councils develop decision drafts which are approved by the Chief Executive Officer.
BU-95 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation |  | Section 2.3.3.summerises the surveillance programmes in place to monitor integrity of containment structures. Please explain if the integrity of the spent fuel pool is monitored by these programmes. | expert group 3 on other topics / expert group 1 | The SNF Pool integrity monitoring is included into the Surveillance Programme. The SNF Pool integrity is controlled through the Leak Monitoring System. In case of leaks of the SNF Pool internal liner, actions are undertaken to remove the leaks according to a programme that is especially developed for the purpose.
BU-96 |  | General AMP expert group | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation |  | Section 2.3.4 explains the process by which remedial actions are implemented in response to findings from the licensee's monitoring, testing and sampling programme. The implementation of corrective actions (such as replacement or repair) of long life SSCs can involve significant technical challenges, lead times and costs. Please explain the process used to prioritise the implementation these longer term remedial actions to ensure timely action is take to arrest ageing and degradation effects. | expert group 3 on other topics / expert group 1 | Organisation and implementation of activities related to drafting proposals for implementation of programmes within the framework of the Company Planning System is implemented in compliance with the Administrative Procedure. Development of Kozloduy NPP EAD Business Programme”. The organisation of the activities connected with the maintenance of necessary stock of materials and spare parts is implemented according to the procedure for operational planning, regulated in the respective Company’s documents Decision-making process covers convening of Expert Technical Councils where given suggestions, statements and justifications are discussed by focusing on safety. Experts and specialists of respective plant operational divisions that have the authority of making suggestions take part in the council meetings. Suggestions are approved by the Chief Executive Officer.
BU-97 |  | Cables expert group | Bulgaria | 03. Electrical cables | 38/45 | What is the main source of information to select the cables important to safety that are subject to the AMP ? It appears that the operator does not have a cable data base to facilitate the aging assessment of cables. In which way is then the operating conditions ( e.g. factors like temperatures, humidity, radiation , vibrations, chemical, etc..) impact on specific cables determined? Such an impact is different in different areas of the plant and cannot be assessed on a" generic" basis. | expert group 3 | The operator has cable data bases developed for other projects, implemented in the Plant. All data for cable qualification and life are managed by the Information System for Organization of Operational Activity (IS OOA) and the electronic archive data base SmartDoc. Considering the operating conditions, those data are used for the comprehensive examination, actual condition assessment and ageing management of Units 5 and 6 cables. The impact of factors as temperature, humidity, radiation, etc., is specifically assessed for each cable type and specific compartment during qualification.Parameters of Units 5 and 6 compartments environment are continuously monitored by the regular sensors of the information systems. As additional (mobile) monitoring of the environmental parameters, sensors (loggers) for temperature and humidity are installed in the hot spots. Data about radiation conditions are taken from the regular devices of the centralized radiation monitoring information and measuring system.
BU-98 |  | Cables expert group | Bulgaria | 03. Electrical cables | 39/44 | Among the verification activities for determining the state of cables/degradation, is cable heating regularly assessed? How are the “hotspots” on the cables identified? Has the procedure for placing (deposition) of surveillance specimen in “hotspots” been implemented at NPP? | expert group 3 | No hotspots due to cable heating as a result of loading were detected during measuring the cable lines with a thermal imaging camera. Additional (mobile) logger sensors are installed in the hotspots, identified according to the environmental parameters. Placing of surveillance specimen in the hotspots is not envisaged.
BU-99 |  | Cables expert group | Bulgaria | 03. Electrical cables | 47 | Did you consider measures to reduce current load (e.g. using of cables with a large cross-section of a conductor or connection of a parallel cable) when replacing the power cables ? | expert group 3 | It is mandatory to follow an approved procedure for the replacement of power cables - conductor cross-section is recalculated by considering continuous loading current, thermal resistance of current in short connections, the length of the line, the method of laying and the surrounding environment of the cables. Measures to reduce the current capacity (e.g. connection of a parallel cable) are foreseen in the original design.
BU-100 |  | Cables expert group | Bulgaria | 03. Electrical cables | 41/42 | The measurements of insulation capacity (C) and dielectric loss angle tangent (tgδ) were performed on which voltage levels/insulation types. The partial discharge characteristics (PD) is performed for cables on which voltage levels? Do these measurements apply to power cables up to 1 kV? | expert group 3 | The following measurements are taken on the 6 kV cables: - resistance of cable line insulation (IR); - testing of cable line with cable reflectometer; - measurement of absorption coefficient and polarisation index (DAR, PI) - partial discharge characteristic measurement (PD); - measurement of tangent delta (dielectric loss angle) - tgδ) Core insulation of power cables of up to 1 kV (IR) and cable line insulation resistance are measured.
BU-101 |  | Cables expert group | Bulgaria | 03. Electrical cables | 42 | The degradation mechanisms for different types of cables are specified, but buried cables are not mentioned. Are the degradation mechanism of buried cables identified/considered? Also, are there junction boxes assessed for aging related degradation? | expert group 3 | The degradation mechanisms of buried cables have been specified/considered in the new revision of the Ageing Management Programme. Connection boxes are subject to assessment of degradation in compliance with our environment qualification programme. Connection boxes are replaced during modernisation and replacement of equipment and cables at Kozloduy NPP.
BU-102 |  | Cables expert group | Bulgaria | 03. Electrical cables | 43 | For cables in tunnels, ducts or conduits, are there special housekeeping activities for those locations defined and implemented | expert group 3 | Cable tunnels, half-floors, and shafts are inspected and housekeeping is maintained according to approved schedules, according to the Cable Inventory and Lighting Operating procedure, ID No.30.ЕЧ.KS.ИЕ.11/5, and Quality procedure. Procedure on Units 5 and 6 Equipment Housekeeping, 30.ОУ.ОК.ИК.12/5. The scope of monitoring during field walkdowns of cable trays covers the following: - - cleanness - lack of foreign materials, dust; - state - absence of: loose, hanging cables or bare wires, integrity of cable coating and cable trays, integrity and proper closing of cable covers and cable ducts, well closed and fixed connection boxes, sealed cable penetrations; - labelling - available cable labelling, labelling of connection boxes and cable trays.
BU-103 |  | Cables expert group | Bulgaria | 03. Electrical cables | 47 | Is an assessment of changes in average annual temperature ( environmental conditions) for the extended operation of cables being undertaken, and what is the periodicity? | expert group 3 | The primary factors that impact the equipment of the instrumentation and control systems (I&C Systems), the electric equipment and cabling in KNPP are: temperature, radiation, humidity (dampening) and mechanical damages. These stressors are never more significant in magnitude than the environmental ones, that will occur during the normal operation of the unit, the expected operating events including, and are called "Mild Environment" [IEEE323]. Even during the different seasons of the year. The humidity of the atmosphere in the NPP buildings is actually very low because of the available air-conditioning installations (air drying). Even in cases of high humidity concentration in the atmosphere, the effect (degradation) on electric and structural characteristics of polymers because the partial pressure is too low to make a considerable quantity of water to penetrate into the insulating material. Temperature as a relevant ageing factor is calculated with temperatures that are a little higher than the actual temperatures at the installation spot of respective equipment and this is verified by the continuous yearly monitoring. However, this can be neglected because of the almost constant or gradually changing temperature in the NPP rooms throughout the year. Therefore, the effect of moisture and temperature is considered only for the equipment outside the ventilated areas - that is why the equipment in these areas is in limited items.
BU-104 |  | Cables expert group | Bulgaria | 03. Electrical cables | 48/49 | For the period 1997. - 2005 no changes in the characteristics of cables were observed. What about the period since? What was the root cause for the presence of the moisture in the cable insulation? In 1996 a deterioration of the insulation of some cables was observed. what was the cause of the deterioration? | expert group 3 | In the period 1992-1995, during the operation of Units 5 and 6, some defects (insulation breakdowns) were found on the cable lines 6 and 0.4 kV, that provide power for the equipment in containment and in the 6 kV cable lines between Units 5 and 6 and the common plant facilities. Cable penetrations and cable heads were immediately inspected. Cable lines were tested and it was found that degradation of insulating qualities was due to penetration of moisture in cable penetrations and cable heads that were implemented according to the initial design. The following measures were taken on the basis of these conclusions: - 6 and 0.4 kV power and control tight penetrations were replaced in stages, priority was given in the replacement of the penetrations of the cable lines that supply power to the equipment that is important to safety and the normal operation. - the cable heads of the cable lines were replaced in stages. Subsequently, the insulation state of the 6 and 0.4kV cables was examined in the years 2005, 2009, 2015/16. It was found that the overall state of the 6 and 0.4 kV cable line insulation was good after the replacement of the sealed cable penetrations and cable heads.
BU-105 |  | EC | Bulgaria | 01. General information |  | A section with References is missing in the report. Please could you provide the references of the following documents: - the Licensee self-assessment and to the Council of Ministers' decree (page 5 of the NAR) - the Equipment Ageing Management Plan put into effect in 2003 and the Lifetime management programme put into force in 2007 (p9) - the Integrated Management System (p13) - the Ageing Management Review (AMR) and residual life assessment of the equipment and facilities of Units 5 and 6 (p27) - the Regulation for Ensuring the Safety of Nuclear Power Plants (p32) |  | - Ageing management self-assessment of NPP, related to EU Topical Peer Review, “Kozloduy” NPP Plc, 01December 2017г.; Decision №8 for adoption of a National Report of Bulgaria for an EU Topical Peer Review “Ageing management assessment of NPP”, Council of Ministers of Republic of Bulgaria, 11 January 2018 - Equipment Ageing Management Plan - 30.ОУ.00.АД.57 and Lifetime management programme - №30.ОУ.00.АД.58 - The integrated management system is described in Management System Manual - ДОД.УК.НК.01 - Ageing Management Review (AMR) and residual life assessment of the equipment and facilities of Units 5 and 6 of “Kozloduy” NPP Plc - РД АТЕ.116/02 0806 2012 - Regulation on ensuring the safety of nuclear power plants, Promulgated: State Gazette No.76 of 30 September 2016
BU-106 |  | EC | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 10 | The requirements to the process of screening of SSCs covered by the PROGRAMME have been developed on the basis of the IAEA recommendation to the NPP ageing management: Please indicate how often the screening results are verified and the reference to the document containing the mentioned requirements. |  | The requirements according to which the actual content of the list of SSC, included in the selection, are specified in Quality Procedure. Implementation of design modifications at Units 5 and 6," 30.ОУ.ОК.ИК.05. The methodology for identifying the scope of the SSCs for the purposes of ageing management is applied during design modification implementation (commissioning or decommissioning of equipment)
BU-107 |  | EC | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 10 | 2.3.1.3. Methods for SSCs grouping in the screening process: No method is described. Please describe the method and/or provide the reference to the used document. |  | Description of grouping for the process of SSCs selection is presented in the document Methodology for conduct of comprehensive examination and assessment of the residual lifetime of the equipment and facilities of Units 5&6 at Kozloduy NPP, РД АТЕ. 116/02.0806-2012.
BU-108 |  | EC | Bulgaria | 02. Overall Ageing Management Programme requirements and implementation | 28 | In 2016 a Pre-SALTO Peer Review Mission of Unit 5 was conducted by a team of IAEA experts: Could the report of this mission be made available? |  | Executive summary of the Mission report can be found here: https://www.iaea.org/sites/default/files/documents/review-missions/26_kozloduy_salto_executive_summary.pdf
BU-109 |  | EC | Bulgaria | 03. Electrical cables | 43 | What is the frequency of "periodic monitoring" for power cables? |  | Measurements of 6 kV power cables under the methods Rin, IC, tgd, PD are taken every 3 years and after every repair of a facility before energising. Measurements of 0,4 kV power cables are taken after each repair of the facility before energising.
BU-110 |  | EC | Bulgaria | 03. Electrical cables | 44 | What is the periodicity for measuring insulation resistance? |  | It is measured every year after each repair of the facility before energising.
BU-111 |  | EC | Bulgaria | 03. Electrical cables | generic 37-51 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found. |  | The cables under the Ageing Management Programme belong to the main and auxiliary systems that are important for the safe shutdown of Kozloduy NPP Units 5 and 6 and for energy production, namely: • cables for qualified equipment into the containment; • cables for qualified equipment outside the containment; • 6kV cables for qualified equipment; • cables for process systems important for the production of electricity (these are the 6 kV cables, connecting the units and common plant equipment, part of the equipment of long cable lines laid in excavations and process tunnels - the replacement of these parts requires significant material resources) Cable types and manufacturers: 1. Types of cables for qualified equipment into the containment: КПоСГ, КПоБОВ, КПоЭСВ, КПЭТИ, КПЭТИ-FRHF, КПоПЭнг-HF, МСТП, С5XFOE-R, JS5XFOE-R. Manufacturers - Russia and the Czech Republic 2. Types of cables for qualified equipment outside the containment: СВТ, САВТУ, Olflex classic 110 CY, Silflex SiHF, J-H (ST) H, NHXHX, NHXCHX, N2XCH, КВВГЭ-HFLS. Manufacturers - Bulgaria, Germany, Russia; 3. 6 kV cable types: САВБТ, САХЕмеТ, NA2XSY, ПвСГ, АLKATEL. Manufacturers - Bulgaria, Germany, Russia, France.
BU-112 |  | EC | Bulgaria | 03. Electrical cables | generic 37-51 | It is not clear whether cable deposits are used to follow-up ageing. Please clarify. |  | The cable "depots" at Kozloduy NPP has not been used so far. Control and power cables for MILD, HELB and LOCA conditions were re-qualified for the purposes of Units 5 and 6 life extension. Currently operating pieces of cables and decommissioned pieces left into the cable trays were used as samples. Currently, the use of cable "depots" is not planned.
BU-113 |  | EC | Bulgaria | 03. Electrical cables | generic 37-51 | The neutron flux instrumentation cables are not mentioned explicitly in the report. What are the AM practices for them? |  | The equipment, including the cables and detector units of the neutron flux monitoring system (NFMS) was commissioned in 2002 and 2003, after the modernisation of the existing complex. The residual life of the NFMS complex was assessed under the project for operating life extension which covered conduct of technical inspections of the state, measurements, tests, approval tests and analyses, and the coaxial cables up to the neutron flux detecting modules were also subject to that assessment. Detecting modules and coaxial cables were inspected and their insulation resistance - measured. The following recommendations for the LTO were given in result of that assessment: - To continue assessing and measuring the insulation resistance and/or reflectometering of measuring cables (coaxial cables) and detecting modules; - During the annual maintenance of the complex, attention needs to be focused on the technical state of modules and electric connections (circuit board contacts, terminal blocks, card slots, etc.), system components for relocation of the detector unit of the ionisation chambers. Neutron flux detector cables are coaxial of the КНМС2С type with mineral insulation - no ageing effects were detected on them.
BU-114 |  | EC | Bulgaria | 05. Reactor Pressure Vessels | Chapter 5.1.2.9, page 76 | In page 48 it is mentioned "due to the fact that the reactors of Units 5&6 at Kozloduy NPP are of a newer generation, and are manufactured according to a different technology, the occurrence of defects of hydrogen flocken type of base metal of reactor pressure vessels is impossible.". The sentence should be rewritten in the following way: "due to the fact that the reactors of Units 5&6 at Kozloduy NPP are of a newer generation, and are manufactured according to a different technology, the occurrence of defects of hydrogen flake type in the base metal of reactor pressure vessels is unlikely.". |  | Accepted.
BU-115 |  | EC | Bulgaria | 07. Concrete containment structures | 87 | The description of the containment structures important for the Chapter 7 is quite superficial and the diagram is very small and difficult to see. It would have been more appropriate to include a larger, better quality figure in an annex along with a more detailed description in Chapter 7. |  | Accepted.
BU-116 |  | EC | Bulgaria | 07. Concrete containment structures | 90 | Section 7.1.1.3 implies that ageing mechanisms of the concrete structures are identified only by observations and monitoring of their condition. There is no mention of the application of international standards, practices, guidance, own and international operating experience feedback and results of research. Section 2.3.2.3 does not provide much additional information. How is it ensured that exhaustive consideration of the applicable ageing mechanisms for each component is performed and that monitoring is adequate to detect new or unexpected degradations? |  | The comprehensive assessment reports analyse the studied and assessed ageing and degradation mechanisms at Kozloduy NPP to verify that these mechanisms comply with the requirements of IAEA SRS No. 82 Аgeing Мanagement for Nuclear Power Plants: International Generic Ageing Lessons Learned (IGALL). Russian and French organisational experience in NPP units life extension and the modern European standard systems (Eurocode) were applied in the selection of assessment points and instrument monitoring. The applicable ageing mechanisms were thoroughly considered for each component, and monitoring is sufficient to detect new or unexpected degradations.
BU-117 |  | EC | Bulgaria | 07. Concrete containment structures | 97 | With regard to the annual leak test of the containment structure, please can you provide information on the acceptance criteria for the test and whether any deterioration in the measured leakage has been experienced with ageing or if any remedial actions have been necessary. |  | Yes, there have. The acceptance criteria for containment leak tests are described in details in the containment leak test procedure as follows: - containment tests at the stage of reactor closure are considered successful if there are no air leaks in the seals and connections of the leak tight circuit at pressure - 400 mm H2O, the pressure drop rate is <2 mm H2O/h; - containment leak tests at overpressure of 0.7 kgf/cm2 are considered successful if there are no air leaks in seals and connections of the leak tight circuit components, and the obtained data for the air parameters are in a sufficient scope to define the containment leak value and the interpolated pressure value for the containment at calculated pressure of 4 kgf/cm2 is not higher than 0.3 % of its value for a 24-hour period. Currently there are no records for degradation of the measured containment leak in result of ageing, therefore there are no cases which required the implementation of any urgent corrective actions.
BU-118 |  | EC | Bulgaria | 07. Concrete containment structures | 97 | Starting on p97, there is a list of inspections and tests carried out 'in the course of specialised surveys (and/or upon identifying the necessity thereof)'. Please could you provide, for the different tests/inspections listed, more information on the frequency of the tests (if they are regular tests) or the triggers that identify the necessity to perform them. |  | The tests/inspections under question, carried out during the special reviews are conducted minimum once (1) in 10 (ten) years. Due to the specific character of the activities (identifying the location and scope of sampling), similar tests/examinations are conducted only according to Programmes, especially developed for each specific case immediately prior the conduct of the review. The determining factors for sampling location are: the most stressed locations, identified on the basis of expert evaluations; locations with defects detected during visual inspection; and locations used for comparison with previous samples. The results of the review are organised in a report which provides necessary prescriptions for greater frequency of conducted tests/inspections (if necessary).
BU-119 |  | EC | Bulgaria | 07. Concrete containment structures | 97 | US thickness measurement of the steel liner: Is this a periodic test? At which locations are the inspections made and how are they selected? |  | Ultrasonic measuring of the steel liner thickness is performed once in every 10 (ten) years. At least 20 (twenty) points, selected by an expert evaluation, are measured on the basis of currently available data and results of the previous review. The deciding factors for the selection of measurement locations are the following: the most stressed locations, identified on the basis of expert evaluations; locations with defects detected during visual inspection; and locations allowing comparison with previous samples.
BU-120 |  | EC | Bulgaria | 07. Concrete containment structures | 101/102 | It is mentioned that concrete resistivity measurements at Unit 5 were lower than the limit. Could you provide more information on the resulting preventive/remedial actions, e.g. increase of test frequency or repairs to the affected areas. When will the next resistivity measurements take place? |  | Concrete resistance, a bit lower than the boundary value, was measured only in 2 items, but their values indicated only prerequisites for the occurrence of surface corrosion in the reinforcement, not that such really occurred ( boundary values are the lowest). Processes will be monitored according to the AMP on SC and their progress trends watched.
BU-121 |  | EC | Bulgaria | 07. Concrete containment structures | 94-95 | Acceptance criteria: Little information is provided regarding acceptance criteria related to cracking of concrete. What are the acceptance criteria for cracks? Is a cracks map maintained and is the development of cracks followed. What are the related follow-up activities in case unacceptable cracks are detected? |  | Cracks are assessed according to the requirements of Eurocode 2 EN 1992-1-1. Crack mapping is maintained for structures with significant number of cracks - the map is updated and crack development - monitored (turbine foundation structure mapping). The maximum allowable width of the cracks is 0,4 mm. When cracks of widths equal or exceeding 0,4 mm are found, measures are undertaken to process the crack with elastic material (injection). The surfaces of the cracks which are of widths beyond 0,4 mm are treated with durable elastic compositions to prevent the damp air or aggressive gaseous media penetrate the cracks.
BU-122 |  | EC | Bulgaria | 07. Concrete containment structures | general | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | There are containment structure components that are not directly accessible for inspection. For instance, this is the concrete surface of the containment that is locked between the walls of the concrete shield building and the steel liner (from level 13.20 up to level 45.60). Alternative inspection methods are applied for similar "structure components" as follows: concrete is tested in the closest accessible point and the obtained results are used by applying the necessary uncertainty factor and conservatism.
CH-1 |  | Poland | Switzerland | 01. General information | 8 | Are there any prescribed ageing mechanism for electrical components similarly as for mechanical and civil engineering field? If so please give reference. |  | According to chapter 2.3 and 3.1 of the NAR the Part 1 fact sheets contain a list of the most important ageing mechanisms for electrical components. The licensees reports which were published according to chapter 1.2 of the NAR contain in chapter 3.1.2 a list of ageing mechanisms for electrical cables. The reports are available on ENSIs Webpage (keyword "Topical Peer Review").
CH-2 |  | Poland | Switzerland | 04. Concealed pipework | 36 | For Gosgen NPP (KKG) please specify the inspections that licensee and ENSI is performing to verify state of concealed pipework sections in the secondary and the primary service water systems. |  | The inspection program for the primary and secondary service water system for Gösgen NPP is based on SVTI specification NE-14 and guideline ENSI-B06. The licensee is responsible for carrying out the required inspections. The SVTI specification NE-14 and guideline ENSI-B06 define whether an inspection has to be supervised by the SVTI, which is the TSO authorized by ENSI. Findings have to be reported to ENSI and the TSO. Generally, ENSI is not present during the inspection but as a regulatory authority ENSI is allowed to be present at any inspection. Besides the SVTI NE-14 and ENSI-B06, there is no special regulatory guideline for concealed pipework. Therefore, there is no required inspection interval and no method defined. The inspection program for conceald pipework is part of the preventive maintenance of KKG. The interval for inspection is depending on several factors such as schedule of the train outage or the schedule for the long term maintenance. Concealed pipework have been inspected by: - Visual inspections of the inner surface by means of walkdowns (trained personnel walks through the pipework) of large diameter pipework during the outage. Walkdowns do not need a formal qualification according to guideline ENSI-B07 (Visual Testing). - Remote controlled visual inspections in the empty state of the system. - During maintenance work and revision of valves the pipework adjoined are inspected visually. - At pipework, which is fed by a service reservoir, the amount of water running through the pipework is measured monthly. Deviations from normal flowrates could indicate large leaks in the pipework. During functional tests, the amount of water running through is measured. Deviations from standard values could indicate large leaks in the pipework. These two methods are legitimate as small leaks do not endanger the functionality of the system in general.
CH-3 |  | Norway | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 6-12 | Can you please briefly describe the methodologies used in AMP for non-replaceable SSCs? |  | In general, the approach or methodology used in the management of ageing for non-replaceable is not different from that used for replaceable components except those components which will be replaced periodically. These components are usually not part of ageing management. As described in chapter 5 of the NAR the AMP for a non-replacable component like the RPV is more complex. In order to demonstrate the integrity of the RPV special inservice inspection and montoring programmes (e.g. for fatigue and neutron embrittlement) are necessary.
CH-4 |  | Bulgaria | Switzerland | 05. Reactor Pressure Vessels | p. 40 | “(2015?) However, in the RPV of unit 1 of Beznau Nuclear Power Plant (KKB), indications were detected that can probably be traced back to non-metallic inclusions from manufacture. The RPV integrity assessment, taking into consideration the ultrasonic testing indications, is not yet complete. KKB unit 1 has been shut down since the discovery of the indications.” When do you expect to have the results from the assessment? It is ‘case by case’ decision but could you give information regarding the formal actions in such cases? |  | Review of the safety case for Beznau Unit 1 by ENSI and its independent experts was completed early in 2018. It was concluded that the non-metallic inclusions do not have a negative impact on RPV integrity or radiation embrittlement. In general, whenever deviations from the specified/expected condition of SSCs are detected, the possible impact on safety and integrity must be fully assessed. This is always done on an individual basis for the case in question.
CH-5 |  | Bulgaria | Switzerland | 05. Reactor Pressure Vessels | p. 40 | “Periodic inspections SVTI as the authorised expert of ENSI, verifies the licensee in-service inspection programmes for the RPVs and the adherence to the defined inspection intervals and monitors the correct implementation of non-destructive testing.” What is the involvement of the Regulator? Does the licensee/SVTI submit the reports and the modification plans to the Regulator for information/approval? |  | During the annual refueling outages, ENSI will do inspections of selected NDT, which typically includes inspection of the execution of NDT based on NDT procedures and inspection of the evaluation of results. For NDT results that require further evaluation as to their acceptability (such as fracture mechanics assessments), ENSI will review the evaluation. SVTI submits a report on all non-destructive inspections that are subject to supervision by the authorised expert body to ENSI for information. The report contains the scope of the NDT, check against the requirements, and NDT results. Deviations from the scope of non-destructive inspections or inspection intervals specified in SVTI specification NE-14 require approval by ENSI.
CH-6 |  | Slovak Republic | Switzerland | 01. General information | Pages - general | Is there a licensee´s ageing management database in place? How is it structured? Does it include acceptance criteria and trending to decide on the required steps for corrective actions? |  | With regard to chapter 2.3 of the NAR there is no requirement for such a database neither given in the overall ageing management programme nor stipulated by the Swiss regulatory guide ENSI-B01. In general, information on acceptance criteria or trending is given in the fact sheets and/or other technical reports. According to chapter 2.3 of the NAR databases for ageing management related activities are used in the different departments of the Swiss NPP as appropriate. Depending on the NPP for mechanical components databases for managing FAC (including individual acceptance criteria and trending) , for in-service inspection and for ageing management exist (documentation of gap resolution and yearly review results). For electrical components the inspections are managed by the overall technical database. This database provides type and component specific information. In other NPPs the integrated operational management systems contain all aging management related information like component history and database for in-service inspection of SSCs including acceptance criteria.
CH-7 |  | United Kingdom | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 13 | Section 2.5 discusses harmonising the annual review of ageing management for the civil electrical and mechanical fields. An earlier section (2.4) refers to an annual safety report. Please outline the content of the annual review/safety report in terms of ageing management. |  | According to chapter 2.1 in the NAR the annual reporting includes a compilation of the newly created, updated or modified documents on ageing management (e.g. facts sheets, field-specific GSKL guides) presentation of the results of the fatigue monitoring, evaluation of the internal and external operating experience, presentation of new findings regarding the state-of-the-art of science and technology, as well as the evaluation of the effectiveness of the AMP on the basis of failure statistics and findings from maintenance.
CH-8 |  | Slovenia | Switzerland | 05. Reactor Pressure Vessels | 45 | Integrity of RPV (page 45): Could you please explain which computational analyses of the resistance to brittle fracture are used to confirmed the integrity of the RPVs. |  | Brittle fracture resistance have to be demonstrated by deterministic fracture mechanics approach. The methology isn't determined in detail by Swiss regulation, but it shall used a state of the art procedure. Recomendations by IAEA TECDOC-1627 should taken into account. KKB and KKG used the methology given in KTA 3201.2. Thermohydraulic analyses for different LOCA are performed by RELAP and KWU-MIX. Thermal, structural and fracture mechanics calculations were done by 3D elastic-plastic FEA. The positions for primary interest are nozzle corners and the area around the RPV core weld. Through- and undercladding cracks are in axial & circumferential orientation with different depths and an a/l-ratio of 1/6 have to postulated. The time histories of SIF are plotted as K-T-diagramm against the ASME KIc curve. The consideration of WPS effect is allowable. Before finishing 40 years of operation the PTS analyses need to be updated with respect to the expected end of plant life.
CH-9 |  | Slovenia | Switzerland | 05. Reactor Pressure Vessels | 46 | Cladding anomalies (page 46): Could you please clarify what anomalies are they and explain the licensees plan for their investigation. |  | In 2017, Gösgen NPP (KKG) carried out a series of investigations on the cladding anomaly. It was shown that the anomaly has not changed since its discovery by comparing inspection data from 2006 and 2017. In addition, a replica was taken and an ultrasonic inspection of the RPV base material in the area of the anomaly was performed. It has been shown that the cladding anomaly has no contact with the RPV base material and is very likely due to a welding defect during manufacture. Comparable investigations are planned for the cladding anomaly at Beznau NPP (KKB); no results are yet available.
CH-10 |  | Slovenia | Switzerland | 05. Reactor Pressure Vessels | 48 | Periodic inspection (page 48): Which ENSI specific inspections of selected non-destructive tests are carried out during annual outages? Is the program for inspection of vessel penetration part of AMP at the Swiss NPPs? Is the inspection of flux thimbles guide including? |  | Specific inspections are planned before each annual refueling outage based on the list of NDT planned for that year. Criteria for selecting the inspection topic are for example use of a newly qualified inspection technique or presence of previously detected accpetable flaws in a component. Inspection programs for vessel penetrations, including flux thimble guides are part of the AMP.
CH-11 |  | Slovenia | Switzerland | 04. Concealed pipework | 36 | Section 4.1.2, page 36: It is written that the operating experience for the concealed pipework of both service water systems at the Gösgen Nuclear Power Plant (KKG) is positive, based on the results of the inspections performed. There are no inspections/testing/methods for KKG mentioned in the Section 4.1.3. What were these inspections, what methods were used? |  | The inspection program for the primary and secondary service water system for Gösgen NPP is based on SVTI specification NE-14 and guideline ENSI-B06. The licensee is responsible for carrying out the required inspections. The SVTI specification NE-14 and guideline ENSI-B06 define whether an inspection has to be supervised by the SVTI, which is the TSO authorized by ENSI. Findings have to be reported to ENSI and the TSO. Generally, ENSI is not present during the inspection but as a regulatory authority ENSI is allowed to be present at any inspection. Besides the SVTI NE-14 and ENSI-B06, there is no special regulatory guideline for concealed pipework. Therefore, there is no required inspection interval and no method defined. The inspection program for conceald pipework is part of the preventive maintenance of KKG. The interval for inspection is depending on several factors such as schedule of the train outage or the schedule for the long term maintenance. Concealed pipework have been inspected by: - Visual inspections of the inner surface by means of walkdowns (trained personnel walks through the pipework) of large diameter pipework during the outage. Walkdowns do not need a formal qualification according to guideline ENSI-B07 (Visual Testing). - Remote controlled visual inspections in the empty state of the system. - During maintenance work and revision of valves the pipework adjoined are inspected visually. - At pipework, which is fed by a service reservoir, the amount of water running through the pipework is measured monthly. Deviations from normal flowrates could indicate large leaks in the pipework. During functional tests, the amount of water running through is measured. Deviations from standard values could indicate large leaks in the pipework. These two methods are legitimate as small leaks do not endanger the functionality of the system in general.
CH-12 |  | Slovenia | Switzerland | 04. Concealed pipework | 37 | Section 4.1.4, page 37: It is stated that a part of the buried pipeline in KKG was replaced. What was the reason? This is curious since (on the same page) the regulator states that »neither the background nor the effectiveness of already performed preventive and remedial actions on concealed pipework sections is presented in sufficient detail.« |  | The primary and secondary service water system in Gösgen NPP consist of different kinds of pipework. The type of pipework used is depending on the diameter. Concealed pipework with a diameter smaller 350 mm was built during erection time from low carbon steel without a coating of the inner surface. The outer surface was coated. Concealed pipework with a diameter between 350 and 600 mm consists of low carbon steel with an inner and outer coating. Concealed pipework with a diameter larger 600 mm consist either of cement pipework or of low carbon steel pipework having an inner and outer cement coating. The piping either is buried in soil (e.g. low carbon steel pipework having an inner and outer cement coating) or is within non-accessible channels (e.g. pipework with a diameter below 350 mm). In general, the experience with concealed pipework is positive. Visual inspections of the inner surface by means of walkdows within the piping of large diameter pipework showed no signs for degradation of the functionality of the pipework. The experience with the low carbon steel pipework having an inner coating is positive as well. The performed inspections show, that generally the inner coating is in good condition. In few cases, damages of the inner coating have been found. The corrosive medium (river water) caused in these cases corrosion of the low carbon steel. However, this type of piping is used in KKG in concealed areas as well as in accessible channels. In those pipings appeared neither leakages nor loss of piping wall thickness that endangered the functionality of the systems. However, due to the river water running through the system, corrosion is a relevant ageing mechanism for uncoated low carbon steel piping and coated low carbon steel piping, if the coating is damaged. Therefore, in the last 20 years the uncoated pipework made from low carbon steel in the concealed as well as in the accessible areas of the plant were replaced by austenitic pipework as part of the preventive maintenance. Up to now, KKG has 20 years of positive experience with austenitic pipework in service water systems (river water) for accessible as well as concealed pipework. In the concealed as well as in the accessible areas no leakages were detected at austenitic pipework. In two cases of concealed piping the low carbon steel piping was not replaced by an austenitic steel piping but equipped with a polymeric inlay. The inlay is made of Polyethylene and was mounted during an outage of the system. The method used allowed the mounting of an inlay in the existing low carbon steel pipework from the erection time.
CH-13 |  | United Kingdom | Switzerland | 07. Concrete containment structures | 51 | Section 7.1.1 states that the guidelines ENSI-G01 /31/ are used to specify the scope of all structures to be included into the AMP. Defining the correct scope of structures and the appropriate level of review is important to the overall efficiency of an AMP. Please provide more information on how these guidelines specify the different classifications of structures and the detail required to support AMP. |  | The guideline ENSI-G01 "Safety Classification" defines the classification of the structures. 2 nuclear building classes (BC I and II) are implemented, according to the relevance of the building for the nuclear safety and for radiation protection. Typical examples for BC I are the reactor building and emergency building and for BC II the turbine building and waste storage building . The requirements within the AMP are specified in the guideline ENSI-B01 "Aging Management". All building structures in BC I and II have to be inspected systematically, based on a principal interval of 10 years (main inspections) and 5 years (intermediate inspections). Reporting to the regulator is required in 5 year intervals for BC I and 10 year intervals for BC II buildings.
CH-14 |  | United Kingdom | Switzerland | 07. Concrete containment structures | 56 | 7.1.3 Monitoring, testing, sampling and inspection activities for concrete structures. Beznau Nuclear Power Plant (KKB) - As part of maintenance measures, the condition of the pre-stressing of the annular girder between the dome and the outer cylinder of the outer reactor building envelope building was assessed based on special inspections using drilled cores, tapering of the anchor heads and potential field measurements. Please provide more details of these activities and how the tecniques were safely implemented. |  | The annular girder is pre-stressed with 14 tendons, has a height of approximately 6 m and a thickness of 1.70 m. The anchor heads are arranged at 8 circumferential points. The anchor heads with the lowest measured potentials (and therefore the highest probability of corrosion) were exposed. The observed condition of the anchor heads confirmed the results of the potential field measurements and supported conclusions about the condition of the non-exposed steel parts. The condition is fine and no further measures are implemented.
CH-15 |  | Finland | Switzerland | 04. Concealed pipework | 37 | What are the corresponding safety and operation challenges, like maintaining safe shutdown condition, flooding risks, etc. connected to AMP? |  | In general, according to the current flooding analyses for the Swiss NPPs pipebreaks in the nuclear service water systems are not risk-dominant. The consequences of such pipebreaks are limited due to the fact that the special emergency systems in the Swiss NPPs are designed to take over heat removal in case of loss of the original service water systems. These special emergency systems are functional (well or hilltop reservoir as diverse heat sink) and spatial (situated in an seperate building) independent from the original service water systems. Further, taking into account that only limited pipework sections of the nuclear service water systems are not accessible and that these sections are burried in soil or are encased in concrete to a large extent outside the buildings the consequences of a pipebreak are further reduced.
CH-16 |  | Czech Republic | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 6 | "The licensees of Swiss nuclear power plants had already been required to introduce an AMP for safety-relevant SSCs by the former Swiss regulatory authority (now ENSI) at the end of 1991. Consequently, it was decided by the Group of Swiss nuclear power plant managers (GSKL) to charge a coordination team ‘Ageing Monitoring in Swiss Nuclear Power Plants’ with creating joint documents as a basis for preparing an AMP." It was an expert team? If yes, who were these experts, plant staff or external experts? |  | The coordination team as well as the expert teams consist of plant staff.
CH-17 |  | Czech Republic | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 6 | "Ageing management is implemented in the individual departments of the Swiss nuclear power plants. For this purpose, a GSKL expert team with the necessary technical competence was established for each department. Ageing management was divided into the electrical, civil and mechanical engineering fields. To clearly assign the technical responsibility, interfaces between the individual departments were defined in an additional GSKL document /25/." I understand that ageing management is multidisciplinary work so it is clear that the work is devided between several different departments. But who is the main responsible for development and implementation of overall AMP? |  | Overall plant level: The GSKL group and their subordinated expert teams prepare and review the existing national guidance on how to implement ageing management programms. In other words, the GSKL Group and their expert teams are responsible for the development and implementation of the "generic" overall AMP. Plant-specific level: The individual members of the GSKL group and their expert teams are responsible for the application of the overall AMP in their departments of their individual plants. The responsibilities and the process for the implementation of the overall AMP on the plant level is described in the plant's certified management system.
CH-18 |  | Czech Republic | Switzerland | 03. Electrical cables | 19 | What kind of optical cables installed on NPP do you use more commonly - those with glass or plastic core? |  | In the Swiss NPPs only optical fiber cables consisting of glass are used.
CH-19 |  | Czech Republic | Switzerland | 03. Electrical cables | 24 | p 24 last para ."…..systematic replacement of all medium voltage cables was decided upon and completed by 2011" Does somebody tested these removed cables? Just for information. |  | The replaced cables were not tested.
CH-20 |  | Finland | Switzerland | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? |  | Conditions for safe operation and safe shutdown are determined in the plant design documents. The AMP needs to make sure that the components and structures maintain their integrity and function. This is adressed through adequate selection of the scope of the AMP and the inspection and maintenance programs.
CH-21 |  | Czech Republic | Switzerland | 03. Electrical cables | 23, 26, 28 | "Liebstadt NPP p.26 ""…the relative elongation at break is used as a reference value for ageing…"" Muhlberg NPP, p.28…""….required minimum elongation at break 50 %"" Beznau NPP, p 23….""….is still above required 50 %""" Why one NPP (Liebstadt) uses another end point criterion? Relative change instead of absolute value. |  | All Swiss NPPs test EAB according to IEC62582-3 using minimum 50% elongation as an acceptance criteria.
CH-22 |  | United Kingdom | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 10 | The report mentions that the AMP includes specific technical documents including fact sheets, ageing catalogues and ageing dossiers. What is the purpose of each of these documents and what are their contents? |  | The AM-documentation for each of the engineering domains in the Swiss NPP consists of higher level and plant-specific documents. The higher level documents describe the physical ageing phenomena occurring in the nuclear power plants in general and present a procedure for the early detection and control of these phenomena. The ageing catalogues (including a generic list of potential degradation mechanismen) used in the mechanical and civil structure engineering domain as well as the fact sheets part 1 (including all potential ageing mechanisms) and part 2 (including possible diagnostics methods) used in the electrical engineering domain belongs to the higher level documentation. The fact sheets used in the mechanical and civil structure engineering domain as well as the fact sheets part 3 used in the electrical engineering domain belongs to the plant-specific documentation. In these documents the ageing mechanismen relevant for the different plant-specific mechanical components, electrical components and structural elements as well as the diagnostics methods used to detect degradation mechanismen are determined. The ageing dossiers will only be used in the electrical engineering domain for the ageing management of components classified 0E (safety related). In comparison to the content of the fact sheets (part 1 up to 3) for the ageing managment of electrical components classified 1E (safety relevant) the ageing dossiers include only the tests performed to detect the relevant ageing mechanismen based on the experience gained from the AM of 1E classified components. In summary, the scope of the AM documentation used in the electrical engineering domain depends on the safety classification of the components (graded approach).
CH-23 |  | United Kingdom | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 11 | Page 11 of the report provides information on the preventive maintenance including inspections by the licensee. This refers to a number of ENSI standards and states that the maintenance programmes must be defined in plant-specific documents, such as technical specifications. It is not clear how the fact sheets, ageing catalogues and ageing dossiers are used in the generation of plant-specific documents. Please explian the link between the specific technical documents in the AMP and the plant-specific documents which define the maintenance programmes etc. |  | For civil structures each fact sheet contains the inspections to be performed and the assessment of the condition of the individual structures derived from the inspections. There are no additional maintenance documents. In other words, all inspections carried out according to the AMP and the results are documented in the fact sheets. The results of inspections are analyzed and any required maintenance measures are initiated. For mechanical and electrical components the gaps identified by the AMP are closed by taking appropriate measures. This is documented in the fact sheets. The measures taken to close the gap are documented in the maintenance programme, e.g. by work instructions, NDE plans and system health reports.
CH-24 |  | United Kingdom | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 12 | The licensee reviews ageing management on an annual basis and submits its report to ENSI. What does ENSI do with this report? |  | According to chapter 2.6 of the NAR ENSI reviews this information (e.g. based on the reportable plant-specific events), approves the field-specific guides for further use and informs the licensees within the framework of the annual meeting between ENSI and the GSKL coordination team of the review results. Further more ENSI performs targeted inspections based on the information it received. The annual reporting is an important tool to demonstrate that ageing managment is a living tool in the Swiss NPP.
CH-25 |  | United Kingdom | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 14 | §2.6 on the regulatory oversight process appears to focus on review of the paperwork in the AMP. There is no indication in this section of the report on how ENSI satifies itself that ageing is being managed on the plant. What regulatory inspections does ENSI underake to reassure itself that the plant is not degrading due to ageing? |  | In general, the scope of regular based AM-focused inspections performed within ENSIs annual basic inspection programm is limited. As indicated in chapter 2.6 of the NAR ENSI prefer to fokus on targeted inspections based on the informations gained from the regulatory oversight process. Typically, most inspections of mechanical components are performed during the annual refuelling outages. Specific targets for these inspections are selected based on the inspection and maintenance programs. Inspection topics include non-destructive examinations of major components such as RPV welds, system walk-downs, replacement of components, etc. The inspection includes a review of the relevant procedures, the execution of the work, and the obtained results. A particular focus of inspections is placed on special measures defined on the basis of AMP findings, such as an extended scope of NDE due to (inter)national operating experience. The implementation of the ageing management program itself is reviewed through regular meetings with the licensee (which are not necessarily conducted in the form of a formal inspection) and through review of the annual reporting according to guideline ENSI-B02. ENSI is reviewing the updated fact sheets for civil structures, including randomly also the detail inspection reports of the testing institute. Main findings with a possible relevance to the structural safety of buildings are visually inspected by civil engineering specialists from ENSI to make an independent assessment. Recent examples of ENSI-inspections in Beznau NPP are possible AAR-damages at the weathered concrete containment, the shadow gaps with locally beginning of corrosion of reinforcement due to the carbonation of the concrete at different buildings, fire protection bulkheads, roof sealing membranes, inspection gallery in the foundation plate. ENSI inspects ageing management of electrical components as part of its annual inspection planning. In the case of a thematic inspection, the corresponding system (for example reactor protection system or well water pump) is also assessed with regard to aging (for example module boards) including the associated connections and wiring (visual inspection) and any abnormalities were noted and evaluated. The metrological tests (for example, Tan δ) and the trend monitoring are checked on the basis of the annual reporting for aging monitoring with regard to the basics and the latest findings, and the planned maintenance work is checked.
CH-26 |  | Germany | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 9 | On page 9 it is described how the Swiss licence holders defines the acceptance criteria while implementing the ageing manangement programme. Ususally, information from technical specificiations of the vendor will be taken into account, too. Can Switzerland describe how technical specifications from vendors (e.g. for cables or mechanical compents) are taken into account when defining the acceptance criteria? |  | For active mechanical components vendor information on performance parameters (flow rate, pressures, temperatures, closing times etc.) are usually taken into account. For passive components vendor information on materials and construction, e.g. wall thickness of components, are usually taken into account. Other relevant vendor information, e.g. life time of rubber elements or information on ageing issues as provided by the OEM, will be credited case by case. For electrical components vendor information like the qualified life under defined environmental conditions is used as an acceptance criteria.
CH-27 |  | Germany | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 13 | In the Swiss report it is stated that updates to the ageing management programme were due to changes in regulatory specifications or further developments of the state of the art of science and technology. Can Switzerland provide a few examples of recent modifications with respect to a progressed state of the art of science and technology? |  | There are only a few recent modifications of the Swiss overall AMP with respect to a progressed state of the art of science and technology, e.g.: - In the year of 2011 the GSKL catalogue of ageing mechanisms for mechanical equipment (KATAM) was fully reviewed and updated. As revealed by yearly checks performed by the GSKL expert team for mechanical components no further modifications to that document were necessary since then. - At NPP KKM, since 2000, in order to minimise stress corrosion cracking on internals, cladding and internal RPV welds, a switch to hydrogen water chemistry control (HWC) took place, which since 2005 has been supplemented by noble metal injection with platinum (OLNC™ process - Online Noble Chem). Within the scope of the research collaboration with NPP KKL and the Research Institute PSI, this is being further optimised. - Generic fact sheets of the cables (fact sheets part I and II) were complemented by the use of cable diagnostics (LIRA) and use of thermography.
CH-28 |  | Germany | Switzerland | 03. Electrical cables | 21, 25 | It is mentioned several times in the report that the environmental conditions are assessed and accounted for during the design stage (e.g. p. 21 for KKL). However there is no information on whether there is some process in place to regularly confirm that the actual environmental conditions (temperature, radiation) in the plant match those previous assumptions. Only KKG mentions some walkdowns on p. 25. Is there such a process in place? |  | In general, conservative environmental conditions are considered in the AMP for electrical components in the Swiss NPPs. Changing environmental conditions are reviewed regularly and where appropriate, are temporarily or long-term measured. The plant specific maintenance and ageing management procedures include the specific locations where the components are installed.
CH-29 |  | Germany | Switzerland | 03. Electrical cables | 23, 26, 28 | On p. 23, 26 and 28 KKB, KKL and KKM describe their cable deposits and how tests are conducted regularly on those cables. All plants described how the deposits were supplied with new cables in 1996 and 1999. Do those cables cover all cable types in use and were the cables not procured by new suplliers somehow pre-aged to account for the previous operating history of the cables in use? Also unlike KKL, KKB and KKM do not explicitly mention that the extracted samples are subjected to LOCA conditions. Does the usual testing process include LOCA tests for these plants (KKB and KKM)? |  | There are relevant 1E low tension and instrumentation cable samples in the deposits. The deposits are exposed to harsh environmental conditions which cause preaging. For cables which are used e.g. in the containment a LOCA test was made before the installation of the cables in all Swiss NPPs. A possible repetition of the LOCA test is considered in the context of cable life time extension .
CH-30 |  | Germany | Switzerland | 03. Electrical cables | 24 | KKG has no cable deposits on its own but takes credit from cable deposits in and periodical tests conducted on cables in the Neckarwestheim nuclear power plant (GKN). With the imminent nuclear phaseout in Germany these periodical test will soon no longer be conducted. What are the plans on cable deposits and destructive tests in KKG for the time period after GKN will be shut down? |  | KKG has its own cable deposit which contains cables for the purpose of accelerated aging. This cable depot has not yet been evaluated by tensile elongation tests. As a result, KKG will launch systematic tests and evaluations of its own cable depot and use synergies with other partner plants and / or clarify whether individual candidates could be taken over from the GKN depot.
CH-31 |  | Germany | Switzerland | 07. Concrete containment structures | 52 | Scope of AMP for concrete structures: In chapter 7.1.1 “Scope of ageing management programmes for concrete structures” it is indicated that the outer reactor building envelope is used to protect the inner structures against external effects, among others such as airplane crash. For above-ground outer concrete wall (outer cylinder) one of the requirements is defined as “Penetration protection against impact”. For the dome this requirement is not given. Why should only the cylindrical part of containment be protected against aircraft crash and not the dome? |  | The listing is incomplete. Of course "Penetration protection against impact" is required for the dome too.
CH-32 |  | Germany | Switzerland | 07. Concrete containment structures | 53 | In chapter 7.1.2 “Ageing assessment of concrete structures” is stated that “the occurrence of AAR on weathered concrete components in the presence of potentially reac-tive aggregates cannot be excluded. The risk for the building structure is low because the occurrence can be quickly detected and if necessary a repair is easily implemented.” This conclusion should be explained better, because the experience of NPP Seebrock in USA does not confirm this statement. At the time of discovering the AAR in Seebrock the concrete core samples demonstrated a substantial reduction in compressive strength compared to test cylinders cast during construction and a modulus of elasticity substantially lower than the expected value. Also the implementation of the repair measurements was not easy. How does Switzerland inspect AAR in concrete structures? Can Switzerland explain in more detail the conclusion, that AAR can be quickly detected and repairs can be easily implemented? |  | The statement is referring to possible occurence of AAR in Beznau NPP on the weathered concrete containment. These very small affected surfaces with the typical fine, net-like cracks are clearly localized, visible and accessible. Drill cores are made for further examinations in the laboratory, the determination of the residual swelling mass in a long term test to define the damage potential is currently being carried out. According to the drill cores the damage depth is low, in particular in relation to the overall thickness of the concrete containment.Therefore the effects and risks to the structural safety of the building structure is low and a possible repair can be easily implemented, e.g. (depending on the damage potential) only an applied coating to prevent the moisture entry could be a repair measure.
CH-33 |  | Germany | Switzerland | 07. Concrete containment structures | 60 | In chapter 7.3 “Regulators assessment and conclusions on ageing management programmes for concrete structures” is stated that “up until now, only one special test on an inaccessible structural component of the outer reactor building envelope in Beznau Nuclear Power Plant (KKB) has been performed, in which it was confirmed that the pre-stressing in the annular girder between the dome and the outer cylinder of the outer re-actor building envelope is sufficient.” On page 52 it was written that the tendons and the anchor heads are set in concrete and thus are inaccessible for non-destructive testing. On page 59 it was written that there is still no reliable experience for the condition assessment of inaccessible civil engineering structures. Which method was used for the special test performed at Beznau NPP? |  | The mentioned special test was not a non-destructive inspection. Based on previous potential field measurements, cores were drilled into the covering concrete in order to expose anchor heads of prestressing tendons for visual examination (corrosion spot check). After the inspection the surfaces have been reconstructed.
CH-34 |  | Germany | Switzerland | 09. Overall assessment and general conclusions | 66 | ENSI stated in the National Assessment Report that it will extend the focus of its regulatory efforts regarding ageing management in order to make sure that all safety-relevant concealed piping systems are included and are covered by suitable maintenance and inspection programmes. ENSI identified this topic as an area of improvement. Can Switzerland (ENSI) share its expectations for an improved ageing managment of concealed piping systems in more detail? |  | ENSI intends to perform a comprehensive inspection on this issue in the second half of 2018 in all Swiss NPPs. The expectation is, that the identified concealed pipework of the nuclear service water systems is adequately addressed in the corresponding system fact sheets. That means, potential degradation mechanisms are identified and test programmes are in place. If no specific AMP is implemented for these pipe sections the licensees have to be reasonably justified that the existing programmes for ageing management and maintenance for the accessible pipework of the nuclear service water systems are sufficient. Sufficiency has to be demonstrated based on the evaluation of the previous system operating history.
CH-35 |  | Germany | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 70 | On page 70 it is stated that no reliable inspection methods are available to monitor inaccesible or difficult to access structural components. On the other hand, ENSI plans to demand corresponding tests from the licensees. Can Switzerland explain in more detail the envisaged test for the above mentioned structures? Does ENSI require to perform such tests or develop the necessary techniques to performe such tests? |  | According to chapter 7.3 of the NAR the Swiss licensees have added Annex 4 to the GSKL civil engineering guide. Based on five application examples, the guide illustrates, how condition information can be collected for inaccessible components using indirect investigation methods. Examples for the monitoring of inaccessible or difficult to access structural components are: a) External concrete wall of reactor building, below ground, in groundwater, with external sealing The condition levels of concrete, reinforcement and sealing are determined with examinations of the concrete from the inner side of the concrete wall. Assessments: - Visual findings: Only few, small cracks, no efflorescences and no discolorations, no water, no humidity - Drill cores: All laboratory tests show that the concrete is in good condition and that no deviations from the design occur (e.g. compressive strength, density, humidity) - Settlements measurements show no relevant findings Conclusion: Concrete, reinforcement and sealing are in a good condition. The external sealing is effective, no external carbonation may be assumed. b) Concrete wall of fuel element storage pool, covered by a liner The condition levels of concrete and reinforcement are assessed in principle with the same indirect methods as described under a).
CH-36 |  | Germany | Switzerland | 04. Concealed pipework | 35 | KKB (Beznau) identified only a few meters of stainless steel piping of the essential service water system to be concealed, yet under dry atmosphere in the turbine building. The licensee excludes any relevant ageing. Has there been any inspection from the inside? |  | No inspections have been performed before the service water system at Beznau NPP was replaced partially in 2011/2012. From todays point of view no inspection of the 3m part of stainless pipe is planned neither from inside nor from outside. During planned maintenance work at the raw water pumps visual inspection of the accessible piping can be used as reference.
CH-37 |  | Germany | Switzerland | 04. Concealed pipework | 36 | KKG (Gösgen) identified sections of the primary and secondary service water systems that are either buried or inaccessible in ducts. The licensee considers the operating experience as positive, while he already replaced ferritic buried piping by austenitic stainless steel piping and coated some selected originally uncoated piping from the inside. This appears somehow contradictory. How is the current state of the concealed piping evaluated? |  | The primary and secondary service water system in Gösgen NPP consist of different kinds of pipework. The type of pipework used is depending on the diameter. Concealed pipework with a diameter smaller 350 mm was built during erection time from low carbon steel without a coating of the inner surface. The outer surface was coated. Concealed pipework with a diameter between 350 and 600 mm consists of low carbon steel with an inner and outer coating. Concealed pipework with a diameter larger 600 mm consist either of cement pipework or of low carbon steel pipework having an inner and outer cement coating. The piping either is buried in soil (e.g. low carbon steel pipework having an inner and outer cement coating) or is within non-accessible channels (e.g. pipework with a diameter below 350 mm). In general, the experience with concealed pipework is positive. Visual inspections of the inner surface by means of walkdows within the piping of large diameter pipework showed no signs for degradation of the functionality of the pipework. The experience with the low carbon steel pipework having an inner coating is positive as well. The performed inspections show, that generally the inner coating is in good condition. In few cases, damages of the inner coating have been found. The corrosive medium (river water) caused in these cases corrosion of the low carbon steel. However, this type of piping is used in KKG in concealed areas as well as in accessible channels. In those pipings appeared neither leakages nor loss of piping wall thickness that endangered the functionality of the systems. However, due to the river water running through the system, corrosion is a relevant ageing mechanism for uncoated low carbon steel piping and coated low carbon steel piping, if the coating is damaged. Therefore, in the last 20 years the uncoated pipework made from low carbon steel in the concealed as well as in the accessible areas of the plant were replaced by austenitic pipework as part of the preventive maintenance. Up to now, KKG has 20 years of positive experience with austenitic pipework in service water systems (river water) for accessible as well as concealed pipework. In the concealed as well as in the accessible areas no leakages were detected at austenitic pipework. In two cases of concealed piping the low carbon steel piping was not replaced by an austenitic steel piping but equipped with a polymeric inlay. The inlay is made of Polyethylene and was mounted during an outage of the system. The method used allowed the mounting of an inlay in the existing low carbon steel pipework from the erection time.
CH-38 |  | Germany | Switzerland | 05. Reactor Pressure Vessels | 44 | After detection of stress corrosion cracking at a feed water nozzle of the RPV of KKL (Leibstadt), a repair was undertaken with a ‘full structural weld overlay’. Is this weld also subject to a mechanical stress improvement? How is the follow-up inspection program of this weld? |  | KKL is currently in the process of qualifying a mechanical stress improvement procedure for its dissimilar metal welds. For the N5 nozzle with FSWOL no application is planned, other N5 yes. For the inspection of the full structural weld overlay, inspections with a qualified ultrasonic inspection technique are carried out at shortened inspection intervals.
CH-39 |  | Germany | Switzerland | 05. Reactor Pressure Vessels | 45 | In 1997, based on results from these monitoring measures, the RPV nozzles of KKM (Mühleberg) were modified by the installation of double thermosleeves. What was the effect of these double thermosleeves with respect to single thermosleeves on the fatigue of the nozzles? |  | Before 1997 the nozzle was exposed to HCF due to turbulent thermal mixing. Accurate estimations for the fatigue usage factor are difficult for this phenomenon. Investigations by NDT did and does not show indications. After installation of double thermosleeves the effects by turbulent mixing were reduced to a neglectible value. The annual increase of fatige usage factors, now caused primarily by LCF transients, are typically between 0.2 and 0.5 % only.
CH-40 |  | Germany | Switzerland | 05. Reactor Pressure Vessels | 46 | According to ENSI, cladding anomalies were not mentioned in the licensee reports while such anomalies were identified in the RPVs in Gösgen and Beznau Nuclear Power Plant (KKG and KKB). Apparently these anomalies were detected quite recently. What kind of inspections of the cladding are required and performed in the Swiss RPV? |  | The specification SVTI NE-14 requires a VT-3 cladding inspection every 10 years with additional VT-1 inspection of selected areas. The Swiss NPP implemented this requirement with their inspection programs, in particular the areas of the inlet and outlet nozzles or other known anomalies are selected for the VT-1 inspection.
CH-41 |  | Netherlands | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 2.6 | Could ENSI describe the main parts of its proactive inspections of the AM at NPPs? |  | In general, the scope of regular based AM-focused inspections performed within ENSIs annual basic inspection programm is limited. As indicated in chapter 2.6 of the NAR ENSI prefer to fokus on targeted inspections based on the informations gained from the regulatory oversight process. Typically, most inspections of mechanical components are performed during the annual refuelling outages. Specific targets for these inspections are selected based on the inspection and maintenance programs. Inspection topics include non-destructive examinations of major components such as RPV welds, system walk-downs, replacement of components, etc. The inspection includes a review of the relevant procedures, the execution of the work, and the obtained results. A particular focus of inspections is placed on special measures defined on the basis of AMP findings, such as an extended scope of NDE due to (inter)national operating experience. The implementation of the ageing management program itself is reviewed through regular meetings with the licensee (which are not necessarily conducted in the form of a formal inspection) and through review of the annual reporting according to guideline ENSI-B02. ENSI is reviewing the updated fact sheets for civil structures, including randomly also the detail inspection reports of the testing institute. Main findings with a possible relevance to the structural safety of buildings are visually inspected by civil engineering specialists from ENSI to make an independent assessment. Recent examples of ENSI-inspections in Beznau NPP are possible AAR-damages at the weathered concrete containment, the shadow gaps with locally beginning of corrosion of reinforcement due to the carbonation of the concrete at different buildings, fire protection bulkheads, roof sealing membranes, inspection gallery in the foundation plate. ENSI inspects ageing management of electrical components as part of its annual inspection planning. In the case of a thematic inspection, the corresponding system (for example reactor protection system or well water pump) is also assessed with regard to aging (for example module boards) including the associated connections and wiring (visual inspection) and any abnormalities were noted and evaluated. The metrological tests (for example, Tan δ) and the trend monitoring are checked on the basis of the annual reporting for aging monitoring with regard to the basics and the latest findings, and the planned maintenance work is checked.
CH-42 |  | Netherlands | Switzerland | 03. Electrical cables | 3.1.2 (general intro) / p.20 | The Technical Specification of the TPR also enquires about "acceptance criteria". For none of the NPPs it is described how acceptance criteria, if any exist, are incorporated in their "Fact Sheets". Please elaborate. |  | The acceptance criteria are established in the cable fact sheets part 3 (Examples for low voltage cables: Insulation resistance ≥ 1 MOHM according electrosuisse, Elongation at break e ≥ 50%; examples for medium voltage cables: Tan delta: values according to EPRI, Report 3002000557).
CH-43 |  | Netherlands | Switzerland | 03. Electrical cables | 3.1.2 (KKL) / p.22 | How is the regular feedback from experience (for identifying unexpected ageing) implemented in the NPP's AMP? |  | Details about monitoring of the international research programmes and evaluation of the operating experience can be found in chapter 2.3.2 of the NAR.
CH-44 |  | Netherlands | Switzerland | 03. Electrical cables | 3.2 (KKG) / p.31 | KKG has put in place nearly a complete new set of cables to be able to plan for LTO. For the old set (e.g. the discovered brittle control room cables, cf. 3.1.4 / p.29): has it been investigated whether or not the ageing has proceeded as predicted? |  | Cable ageing in the control room (especially ​​the cable sheathing at the connections are impacted) was more advanced than in other plant areas. This is true even though very moderate and constant environmental conditions (temperatures, humidity, light) are predominant in this area. This led to the conclusion that with a high probability the combination of stripping (which leaves the electrical insulator free) and continuous light UV irradiation by the fluorescent tubes are the main contributors to faster aging. KKG subsequently planned the testing / replacement of comparable cables and the replacement of the fluorescent tubes by LED lamps which have no UV in the spectrum.
CH-45 |  | Netherlands | Switzerland | 04. Concealed pipework | 4.3, p.37 | There is not enough information presented to provide a peer review of the concealed pipework AMP (chapter 4). This is also recognized by the regulator and mentioned as an area of improvement. Could this information be provided by responding to this comment in the peer review? |  | ENSI has recognized an area off improvement related to concealed pipework AMP. For this reason, an ENSI focus inspection in the Swiss power plants is already being planned. The following topics will be examined in more detail: Scope of concealed pipework to be considered in the AMPs; previous operating experience and identified flaws; inspections and maintenance activities carried out, maintenance measures planned for the future. ENSI will evaluate the findings of the focus inspection and will request further measures if necessary.
CH-46 |  | Netherlands | Switzerland | 07. Concrete containment structures | 7.1.1 | Does the ENSI-B01/10/ take into account LTO and beyond design lifetime of the concrete structures? Does the lifetime affect the (ISI) inspections and evaluations of concrete structures? |  | The guideline ENSI-B01 does not explicitely address the issue of long term operation. However, the AMP and the required periodic inspections/assessments within the AMP are implemented as a continuous process. In Switzerland the licences of the NPPs are not formally limited, there is no limited lifetime. Therefore as soon as significant aging effects will be observed, the licencees are required to develop measures (such as repair, reconstruction or shortening of inspection intervals) in order to keep the structures' condition within acceptable limits.
CH-47 |  | Netherlands | Switzerland | 07. Concrete containment structures | 7.3 | The assessment of the Concrete structures is based on the ENSI guideline ENSI-B01 from 2011. Will the guideline be evaluated because of the experience of the last years of use and are international experiences (OEF, GALL) also taken into account? |  | According to guideline ENSI-B01 the GSKL guide for civil engineering fact sheets has to be updated at least every ten years and has to consider the international state of the art in science and technology. The last update was in December 2015 and complies with the international standards. See also Section 2.1 and 2.2 of Swiss National Assessment Report.
CH-48 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | Have the Licensees verified that the identified degradation mechanisms are in agreement with international standards such as IGALL or GALL? |  | Guideline ENSI-B01, which specifies requirements for ageing management programs in Swiss nuclear installations, specifically refers to recommendations in the IAEA Safety Guide NS-G-2.12. The IGALL program is one of the important references for the implementation of ageing management in Swiss nuclear plants (see chapter 2 of NAR).
CH-49 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | What requirements applied for the qualification of the NDE-system and operators? |  | According to the applicable guideline ENSI-B07, comprehensive qualification is required for all NDT techniques applied to RPVs. This includes qualification of procedure, equipment and personnel. NDT labs have to be accredited according to EN ISO/IEC 17025. The qualification body must be an accredited inspection body type A according to EN ISO/IEC 17020 and be approved by ENSI.
CH-50 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | What are the requirements for the laboratories that perform the periodic non-destructive tests? |  | NDT labs have to be accredited according to EN ISO/IEC 17025. According to the applicable guideline ENSI-B07, comprehensive qualification is required for all NDT techniques applied to RPVs. This includes qualification of procedure, equipment and personnel. The qualification body must be an accredited inspection body type A according to EN ISO/IEC 17020 and be approved by ENSI.
CH-51 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | Regarding in-service inspection programs, how are the inspection intervals determined? |  | As long as there is no active ageing mechanism indentified, inspection intervals are applied as specified in SVTI specification NE-14, which is based on international Codes and Standards (in particular ASME XI). When evidence of potentially progressing damage is found, inspection intervals may be adjusted as necessary to ensure that existing flaws do not exceed the acceptability limits before the next inspection.
CH-52 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | When all sets of irradiated specimens are removed from a reactor, how is the fluence monitored? |  | Fluence monitors inside the surveilance capsules are used for calibration and validation of neutron transport theory models. After the calibration of the fluence modelling software, the prediction is done independened from the remaining specimen. (see question 1042). Gösgen NPP (KKG) use ex core measurements. The last set of irradiated specimen covers the complete expected end of life. | Ref to the line with the question in the source file which corresponds to CH-53
CH-53 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | Which methods are applied for the prediction of the vessel fluence? |  | The prediction of the vessel fluence is based on numerical modelling by (usually 2D) deterministic transport theory programmes according to the actual core loading. 3D flux distributions are obtained by combining results of two separate 2D-neutron transport calculations. Examples for such programmes are DORT/ANISN used by Beznau NPP (KKB) and CASCADE/PINPOW used by KKG. The calculated fluence is verified by analyzing neutron monitors after removal of the surveillance capsules. Future fluences are then predicted by extrapolation of existing results.
CH-54 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | Which methods are applied for the analysis of P-T limiting curves? |  | P-T-limits are established by postulating quarter-depth cracks at zones with highest embrittlement. Fracture mechanics analysis is done according to ASME BPVC, Section XI, App. A & G.
CH-55 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | The reactor vessel heads for Beznau 1 and 2 have been replaced but not for Gösgen NPP. For the manufacturing of the reactor vessel head to Gösgen what materials were used? |  | KKG is a 3-loop second generation PWR from Siemens-KWU. Materials of RPV Head are: Base material: 22NiMoCr3-7 (ASTM A 508 Class 2), Cladding: X5CrNiNb19-9, CRD flanges & upper ICM nozzles: X6CrNiNb18-10, CR- & ICM nozzles: St52.3, clad. X5CrNiNb19-9 or X6CrNiNb18-10, o-rings: Inconel 718 with silver coating, dissimilar welds CRD & ICM: Inconel 82/182, flange bolts & washer: 26NiCrMo14-6, flange nuts: 34CrNiMo6 other: BH 36 (ribs), St 37.2 (support ring), Stellit 21 (cladding of centring)
CH-56 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels | P47 | According to the report : "Neutron fluences are continuously monitored". How is the fluence monitored? Have ex-vessel dosimetry been installed? |  | The fluence is updated periodically, based on theoretical fluence calculations according to the actual loading of the core. Most of the Swiss NPPs are using neutron monitors inside the surveillance capsules. KKG is using excore detectors. Ex vessel dosimetry is installed in KKG, but not in the other Swiss NPPs.
CH-57 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | 5.1.2 Para 5.1.2 of [D3] states that “The guideline ENSI-B01 and the GSKL guide specify the requirements for the preparation of fact sheets for the RPVs”. It is needed to clarify what is this “fact sheets” and provide information on their structure and contents. |  | The fact sheet compiles a systematic analysis of all information relevant for ageing management of a system or component. This includes the scope of the ageing assessment (which parts of the system/component are included), evaluation of possible ageing mechanisms regarding their relevance for the individual parts, the relevant internal and external operating experience, review of the state of technology, references to maintenance and inspection programs, etc. ENSI intends to provide a description of the structure of the RPVs fact sheets used in the Swiss NPPs as an annex to the thematic presentations during the workshop.
CH-58 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | Is it possible to clarify which TLAAs are used for RPV safety substantiations? |  | The following TLAA will be performed for RPVs: - Fatigue assessments with repect to the RPV end of life - Calculation of expected end of life RTNDT - Pressurized thermal shock (PTS) analyses (PWR) - Leak-before-Break analyses (PWR)
CH-59 |  | RPV expert group | Switzerland | 05. Reactor Pressure Vessels |  | 5.3 Para 5.3 of [D3] states that cladding anomalies were identified in the RPVs in Gosgen and Beznau NPP. It can be referred to unexpected degradation and should be described in the NAR in more detail in para 5.1.3. Corresponding clarifications for the cladding anomalies should be provided as an answer. |  | In 2017, KKG carried out a series of investigations on the cladding anomaly. It was shown that the anomaly has not changed since its discovery by comparing inspection data from 2006 and 2017. In addition, a replica was taken and an ultrasonic inspection of the RDB base material in the area of the anomaly was performed. It has been shown that the cladding anomaly has no contact with the RPV base material and is very likely due to a welding defect during manufacture. Comparable investigations are planned for the cladding anomaly at KKB; no results are yet available.
CH-60 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 58 | With reference to Section 7.2 Licensees experience of the application of ageing management programmes for concrete structures, what external operating experience events involving ageing-related degradation of 07. Concrete containment structures have been evaluated for applicability to Swiss NPPs? |  | The Swiss licensees have formed and are operating a working platform for the experience exchange in respect of ageing management, ageing mechanisms and investigation methods. So far, no unexpected ageing effects have occurred on the civil engineering structures in the Swiss nuclear power plants. In addition to this exchange the licencees and the regulator benefit from the periodic reviews performed by WANO and by the IAEA.
CH-61 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 55 | With reference to Section 7.1.3 Monitoring, testing, sampling and inspection activities for concrete structures, what instrumentation is used in Swiss NPPs to monitor the long term performance of 07. Concrete containment structures? |  | In principle the AMP is carried out according to the guideline ENSI-B01 and as described in section 7.1.3, also for long term performance. Additional monitoring and permanent instrumentation is basically not planned and is limited to few locations (e.g. in Mühleberg NPP some permanent measurements of cracks and humidity in the reactor building).
CH-62 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 55 | Have there been any cases identified in which there are differences between the design assumptions and the actual operating conditions for parameters that may affect the performance of the 07. Concrete containment structures? |  | No. The loads, temperatures, pressures etc. have been kept well beyond design levels, so far.
CH-63 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 55 | Is leak rate testing used as part of the testing activities for the concrete structures of Swiss NPPs? |  | No. The concrete containments in the Swiss NPPs are secondary containments, which are not designed against internal overpressure.
CH-64 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 55 | What settlement monitoring activities are performed for the concrete structures of Swiss NPPs? |  | The monitoring of settlements in Swiss NPPs is not uniform and varies from plant to plant. Basically there is no permanent instrumentation and measurement present, the settlements are measured by conventional survey systems according to the inspection plan every 5 to 10 years. In Mühleberg NPP the measurements have been discontinued, because the last results showed, that the settlements have come to a complete stop.
CH-65 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 51 | Outer reactor building description - Could you please clarify where the concrete containment (for BWRs) is covered in your report? Is the concrete containment for BWRs a pre-stressed structure? |  | In chapter 7 "Concrete containment structures" there is no specific distinction with respect to the reactor types. The secondary containments in the Swiss NPPS are constructed in reinforced concrete, therefore the requirements on the structures (presented in chapter 7.1.1) do not significantly depend on the reactor type. The concrete containments in the Swiss BWRs are not prestressed structures.
CH-66 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 52-53 | Ageing assessment of concrete structures - Please clarify how loss of pre-stressed is captured in the ageing assessment? |  | Loss of prestress is not an issue in the concrete containments of the Swiss NPPs. There is one very limited exception, the ring girder between the dome and the cylindrical shell in Beznau NPP. There the prestressing tendons are grouted and therefore not accessible for inspections or retensioning. In one documented special inspection some selected anchor heads have been exposed for visual inspection (corrosion spot check), with positive inspection result.
CH-67 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 56 & 60 | Beznau Nuclear Power Plant - Please could you provide more information on how the level of pre-stressed (or the loss of pre-stress) in the annular girder is addressed by the AMP? |  | The level or loss of pre-stressing was not scope of the investigations at the anchor heads (see also question to this topic). The loss of pre-stressing because of relaxation, creep, shrinkage is considered in the design. The tendons are grouted and the loss of prestressing is not relevant for the ultimate resistance. The serviceability of the concrete containment plays a minor role, as the primary containments in the Swiss NPPs are steel shells which are designed to withstand the overpressure load cases and to fulfil the tightness requirements.
CH-68 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | Table 7.2 | Table 7.2 - The condition levels in table 7.2 seem to be qualitative levels, are these linked to quantitative values and numerical acceptance criteria? |  | Indeed it is not easy to define quantitative values for the condition assessment from predominantly visual inspections. However the detailed assessment criteria may be categorized as "semi-quantitative". They contain quantitative elements, some examples: for level 1 and 2: depth of carbonation significantly less than coverage depth of the reinforcing steel bars; for level 2: less than 10% of the surface with significant cracks.
CH-69 |  | Concrete containment PCPV expert group | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 9 | Monitoring of international research programmes - Please could you provide more information on the ultrasonic-guided wave technology in embedded concrete structures? |  | The technique has been succesfully applied in one Swiss Nuclear plant. After developing a system which was applicable for the local geometry a screening measurement could detect some areas of interest. Two of these areas were then observed by locally excavating inspection holes. The indication could be confirmed in good accuracy. In another Swiss plant a feasibility study revealed that the accuracy of this technique was found to be unsatisfactory in the case of the complex geometry to be examined. In the following the concrete covered steel structure was locally excavated to allow conventional NDE technique on the steel shell.
CH-70 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 55 | Monitoring, testing, sampling and inspection activities for concrete structures - The frequency of inspections is every 10 years. Are there any other inspections (of the civil engineering structures) or monitoring programmes that take place more frequently? Could you provide more information on how trending is used to provide confidence that from one inspection to the next the condition level will not substantially decrease? |  | In addition to the 10-yearly main inspections, intermediate inspections in the half-time between the main inspections are required by regulation, performed systematically and documented. Continuous maintenance and repair of the concrete structures are understood to be part of the daily business. Trending: As part of the scope of the main inspections, the experts are requested to assess the potential development/degradation of the inspected structures within the period until the subsequent inspection.
CH-71 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | 56 | Beznau Nuclear Power Plant - Please could you provide more information on the condition of the concrete, reinforcement, steel liner and its anchoring found during the Steam Generators and RPV head project? |  | The steam generators were replaced in 1993 (unit 1) and 1999 (unit 2). Only visual assessments of the exposed structural components were done. The RPV heads were replaced in 2015. The clippings in the containment were on the same place for both projects, therefore the broken out materials in 2015 did not originate from the construction period and no further examinations were carried out. Nevertheless the exposed structures (concrete, steel reeinforcement, liner including anchoring) of the original building were inspected and no damage was found.
CH-72 |  | Concrete containment PCPV expert group | Switzerland | 07. Concrete containment structures | All | Could you provide more information on the seals, gaskets, water stops and liner AMPs? |  | All these "non-concrete structural elements" are included in the inspection scope of the AMP. Aging mechanisms and assessment criteria are specified in the GSKL civil engineering guide. In the practical implementation seals and gaskets are replaced as soon as significant degradation is observed. Steel liners with safety functions are included in the AMP of mechanical equipment. Insufficient experience has been collected/reported so far on water stops (e.g. underground) which are not accessible for visual inspections.
CH-73 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 35 - 36 | Paragraph 4.1.2 doesn't describe the key standards, guidance and manifacturing documents used to prepare the ageing management. Please give information. |  | The key standards and guidelines relevant for the developement and implementation of the ageing management programme in the Swiss NPPs are described in chapter 2.1 and chapter 2.3 of the NAR. In general, the inspection program for the mechanical systems is based on SVTI specification NE-14 and guideline ENSI-B06. Besides the SVTI NE-14 and ENSI-B06, there is no special regulatory guideline for concealed pipework. Futhermore, the system-specific fact sheets used for the ageing-related assessments in the Swiss NPPs (except KKM) do not explicitely address ageing management of concealed pipework. Therefore ENSI has recognized an area of improvement related to concealed pipework.
CH-74 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 36 | Paragraph 4.1.3 gives information about the implemented monitoring, testing and inspection activities for Mühleberg Nuclear Power Plant (KKM). Give information about the monitoring, testing and inspection programs of the other NPPs. |  | The inspection program for the service water systems for the Swiss NPP is based on SVTI specification NE-14 and guideline ENSI-B06. The licensee is responsible for carrying out the required inspections. The SVTI specification NE-14 and guideline ENSI-B06 define whether an inspection has to be supervised by the SVTI, which is the TSO authorized by ENSI. Findings have to be reported to ENSI and the TSO. The inspection program for conceald pipework is part of the preventive maintenance of the Swiss NPP. The interval for inspection is depending on several factors such as schedule of the train outage or the schedule for the long term maintenance. Concealed pipework have been inspected by: - Visual inspections of the inner surface by means of walkdowns (trained personnel walks through the pipework) of large diameter pipework during the outage. Walkdowns do not need a formal qualification according to guideline ENSI-B07 (Visual Testing). - Remote controlled visual inspections in the empty state of the system. - During maintenance work and revision of valves the pipework adjoined are inspected visually. - At pipework, which is fed by a service reservoir, the amount of water running through the pipework is measured monthly. Deviations from normal flowrates could indicate large leaks in the pipework. During functional tests, the amount of water running through is measured. Deviations from standard values could indicate large leaks in the pipework. These two methods are legitimate as small leaks do not endanger the functionality of the system in general.
CH-75 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 37 - 38 | Paragraph 04.3 - Give information about the ENSI's experience from inspection and assessment as part of its regulatory activity about the ageing management of concealed pipework in the NPPs. Please give also information about the methods and the activities to be carried out by ENSI to extend "the focus of its regulatory efforts regarding ageing management ...(area of improvement)." |  | ENSI has recognized an area off improvement related to concealed pipework AMP. For this reason, an ENSI focus inspection in the Swiss power plants is already being planned. The following topics will be examined in more detail: Scope of concealed pipework to be considered in the AMPs; previous operating experience and identified flaws; inspections and maintenance activities carried out, maintenance measures planned for the future. ENSI will evaluate the findings of the focus inspection and will request further measures if necessary.
CH-76 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 36 | Section 4.1.3 – For Mühleberg Nuclear Power Plant (KKM), for ferritic pipework “The measured wall thicknesses are significantly above the calculated required wall thicknesses, so that the structural integrity of the service water system is ensured up to the time the system will be put out of operation. According to the licensee, this result also applies to the concealed pipework sections of the service water system, because these sections are of identical design and are exposed to the same conditions as the accessible pipe sections.” Please explain how the Licensee has gained confidence that the concealed sections of pipework are exposed to exactly the same external environmental conditions (e.g. temperature, humidity) as the exposed sections. |  | According to KKM the inner surfaces of both exposed and concealed pipings experience the same medium (river water) in identical condition. The condition assessment of the outer surface in the inaccessible section can be carried out by analogy to the similarly manufactured, wrapped and routed reactor cooling water line which runs parallel to the auxiliary cooling water line. Within the scope of a probe excavation, a section of the inaccessible reactor cooling water line was uncovered. Even after more than 40 years, no significant degradation of the outer surface including the wrapping could be detected.
CH-77 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 35 & 36 | In section 4.1.2, KKM identified that it had concealed pipework in the emergency cooling water and the essential service water systems. In section 4.1.3, KKM state that it has applied experience gained from inspecting buried sections of the main cooling water pipe that is buried and runs next to the service water pipe. Is the main cooling water pipe associated with the systems identified within section 4.1.2, or is it an additional system with concealed pipework? |  | The main cooling water system is an additional system. The system is not safety classified and is therefore not part of the existing AMP.
CH-78 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 35 & 36 | Gösgen Nuclear Power Plant (KKG) identified concealed pipework sections in the secondary and the primary service water systems, buried or located in inaccessible ducts. It also stated that “based on the results of the inspections performed, the licensee comes to the conclusion that the operating experience for the concealed pipework of both service water systems is positive.” Section 4.1.3 only includes an input from KKM; please can KKG provide some detail of their monitoring, testing, sampling and inspection activities for concealed pipework. |  | The primary and secondary service water system in Gösgen NPP consist of different kinds of pipework. The type of pipework used is depending on the diameter. Concealed pipework with a diameter smaller 350 mm was built during erection time from low carbon steel without a coating of the inner surface. The outer surface was coated. Concealed pipework with a diameter between 350 and 600 mm consists of low carbon steel with an inner and outer coating. Concealed pipework with a diameter larger 600 mm consist either of cement pipework or of low carbon steel pipework having an inner and outer cement coating. The piping either is buried in soil (e.g. low carbon steel pipework having an inner and outer cement coating) or is within non-accessible channels (e.g. pipework with a diameter below 350 mm). In general, the experience with concealed pipework is positive. Visual inspections of the inner surface by means of walkdows within the piping of large diameter pipework showed no signs for degradation of the functionality of the pipework. The experience with the low carbon steel pipework having an inner coating is positive as well. The performed inspections show, that generally the inner coating is in good condition. In few cases, damages of the inner coating have been found. The corrosive medium (river water) caused in these cases corrosion of the low carbon steel. However, this type of piping is used in KKG in concealed areas as well as in accessible channels. In those pipings appeared neither leakages nor loss of piping wall thickness that endangered the functionality of the systems. However, due to the river water running through the system, corrosion is a relevant ageing mechanism for uncoated low carbon steel piping and coated low carbon steel piping, if the coating is damaged. Therefore, in the last 20 years the uncoated pipework made from low carbon steel in the concealed as well as in the accessible areas of the plant were replaced by austenitic pipework as part of the preventive maintenance. Up to now, KKG has 20 years of positive experience with austenitic pipework in service water systems (river water) for accessible as well as concealed pipework. In the concealed as well as in the accessible areas no leakages were detected at austenitic pipework. In two cases of concealed piping the low carbon steel piping was not replaced by an austenitic steel piping but equipped with a polymeric inlay. The inlay is made of Polyethylene and was mounted during an outage of the system. The method used allowed the mounting of an inlay in the existing low carbon steel pipework from the erection time.
CH-79 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 37 | Section 4.1.4 – KKG has stated it had “already performed replacement of ferritic pipe sections with austenitic stainless steel where pipes are buried.” Does this mean that KKG has no buried ferritic steel pipework? Was the pipework renewed with stainless steel as a pro-active measure, or as a result of previous degradation or failure? Please can some detail be provided of the criteria considered when identifying pipework needing internal coatings? If it was not originally coated, why does it need coating now? |  | The primary and secondary service water system in Gösgen NPP consist of different kinds of pipework. The type of pipework used is depending on the diameter. Concealed pipework with a diameter smaller 350 mm was built during erection time from low carbon steel without a coating of the inner surface. The outer surface was coated. Concealed pipework with a diameter between 350 and 600 mm consists of low carbon steel with an inner and outer coating. Concealed pipework with a diameter larger 600 mm consist either of cement pipework or of low carbon steel pipework having an inner and outer cement coating. The piping either is buried in soil (e.g. low carbon steel pipework having an inner and outer cement coating) or is within non-accessible channels (e.g. pipework with a diameter below 350 mm). In general, the experience with concealed pipework is positive. Visual inspections of the inner surface by means of walkdows within the piping of large diameter pipework showed no signs for degradation of the functionality of the pipework. The experience with the low carbon steel pipework having an inner coating is positive as well. The performed inspections show, that generally the inner coating is in good condition. In few cases, damages of the inner coating have been found. The corrosive medium (river water) caused in these cases corrosion of the low carbon steel. However, this type of piping is used in KKG in concealed areas as well as in accessible channels. In those pipings appeared neither leakages nor loss of piping wall thickness that endangered the functionality of the systems. However, due to the river water running through the system, corrosion is a relevant ageing mechanism for uncoated low carbon steel piping and coated low carbon steel piping, if the coating is damaged. Therefore, in the last 20 years the uncoated pipework made from low carbon steel in the concealed as well as in the accessible areas of the plant were replaced by austenitic pipework as part of the preventive maintenance. Up to now, KKG has 20 years of positive experience with austenitic pipework in service water systems (river water) for accessible as well as concealed pipework. In the concealed as well as in the accessible areas no leakages were detected at austenitic pipework. In two cases of concealed piping the low carbon steel piping was not replaced by an austenitic steel piping but equipped with a polymeric inlay. The inlay is made of Polyethylene and was mounted during an outage of the system. The method used allowed the mounting of an inlay in the existing low carbon steel pipework from the erection time.
CH-80 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 36 | Section 4.1.3 – For Mühleberg Nuclear Power Plant (KKM), “For the plastic pipes of the emergency cooling water system, compliance with the required material properties is checked annually using retained samples from the manufacturing batch which were stored in the river water. It is therefore possible to detect ageing-induced changes in the material properties in a timely manner.” I consider that the retention of test samples subject to representative operating conditions for ongoing testing is an example of good practice. |  | Thank you for the comment
CH-81 |  | Concealed pipework expert group | Switzerland | 04. Concealed pipework | 37 | Section 4.3 – I support the AFI that was identified to extend the focus of regulatory efforts regarding ageing management in order to make sure that all safety-relevant concealed piping systems are included and are covered by suitable maintenance and inspection programmes. |  | Thank you for the comment
CH-82 |  | Cables expert group | Switzerland | 03. Electrical cables |  | Could you please provide (an) example(s) regarding the Fact sheet 3, to understand how it works for one cable type? |  | An example of the structure and content of a cable fact sheet will be presented at the workshop. In annex 4 of IAEA-TECDOC-1402 an example of the fact sheets used for electrical components in one of the Swiss NPPs is illustrated.
CH-83 |  | Cables expert group | Switzerland | 03. Electrical cables |  | Is there any continuous monitoring inside the containment in the Swiss NPP to detect hot spots? |  | Plant parameters such as radiation and temperature are continuously monitored and recorded in the Swiss NPPs. The measurement equipment is also placed at hot spots e.g. in the vicinity of the main steam lines.
CH-84 |  | Cables expert group | Switzerland | 03. Electrical cables |  | Are there any considerations regarding hot spots when the qualified lifetime is used as a basis of the maintenance? |  | In general, it is the sustained task of the ageing management to assure that the local environmental conditions (including “hot spots” for cables) are covered by the environmental conditions defined for the qualified life assessment.
CH-85 |  | Cables expert group | Switzerland | 03. Electrical cables | 17 | The NAR seems not to clarify the relation between the cable groups examples in WENRA specification and status on Swiss NPP (except group 4, neuron flux cables) . Could you please clarify |  | As indicated in chapter 3.1.1 of the NAR the different cable groups defined for the AMP in the Swiss NPPs roughly correspond to the grouping suggested in the WENRA specfication. According to this specification groups of cables similar to those defined in the specification can be included.
CH-86 |  | Cables expert group | Switzerland | 03. Electrical cables | 20 | Has the cables within the AMP process been analysed for the “water treeing formation" degradation mechanism? |  | Water treeing has been considered in the AMP of the Swiss NPPs as a cable degradation mechanism. According to part 1 and 2 of the cable fact sheets (see licensees reports published on ENSIs Webpage, key word "Topical Peer Review") this type of mechanism is of special importance for medium voltage cables. The medium voltage cables are mostly installed in dry environment. As part of the AMP the medium voltage cables are subject to tan delta measurements. Based on the results of those measurements there are no indications of water treeing.
CH-87 |  | Cables expert group | Switzerland | 03. Electrical cables | 20 | It is not fully clear from the NAR whether there are buried cables or those in trenches at Swiss NPP that fall under the AMP and were as such analysed. Please clarify. |  | This information about cable routing is collected in the fact sheets part 3. Most of the safety relevant cables in the Swiss NPP are laid dry. Otherwise they are qualified for wet conditions.
CH-88 |  | Cables expert group | Switzerland | 03. Electrical cables | 23 | The NAR report depicts the ageing management techniques: Visual inspection, electrical tests (IR, delta tg, TDR, LiRA), mechanical tests (EAB on cables in deposits), but does not specify which of those are applied to the cables that are subject to EQ vs. those that are NON-EQ . could you please clarify. |  | All safety relevant cables (classified 1E) are environmentally qualified and are subject to the AMP.
CH-89 |  | Cables expert group | Switzerland | 03. Electrical cables | 23 | In the NAR, except for Leibstadt NPP, is not clear whether all the Swiss NPP developed the environmental monitoring programs to control the degradation mechanisms (e.g. temperature, radiation, humidity) affecting cables. AS those activities are essential elements of the AMOP for cables, kindly clarify the actuals status. |  | Each Swiss NPP has an environmental monitoring programm to control the degredation mechanisms affecting cables. Actual measurements and evaluations (e.g. those derived from the cable deposits in the Swiss NPPs and from the VGB database which contains experimental data from different German cable deposits) are included in the cable fact sheets and are continously updated.
CH-90 |  | General AMP expert group | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | 21 | At page 21 it is mentioned that the process of ageing management is integrated into the certified management system of the Swiss nuclear power plants and divided by department. What indicators are used to assess the effectiveness of the process? |  | Trending and monitoring indicators are used to access the AMP effectiveness on a component and system level. As described in the NAR, indicators such as annual unplanned non-availability of safety-relevant systems or the number of operational incidents that can be traced back to ageing mechanisms are used for evaluating effectiveness. But there are no indicators in place to directly access the effectiveness of the AMP process itself.
CH-91 |  | General AMP expert group | Switzerland | 02. Overall Ageing Management Programme requirements and implementation | N/A | Comment: The description of the AMP for nuclear installations in Switzerland covers all elements required by Topical Peer Review 2017 - "Ageing Management Technical Specification for the Na-tional Assessment Reports" |  | Thank you for the comment.
CH-92 |  | EC | Switzerland | 01. General information | 6 | " The performed ageing-related assessments of safety -relevant SSCs are summarised in the plant-specific fact sheets. " Please could you indicate the number of facts sheets per plant, and give some details about their structure or provide an example fact sheet. How do they link with the TLAA / AMPs referred to in the IAEA reference documents? |  | According to chapter 2.3.1 of the NAR fact sheets in the civil engineering domain are created for either individual buildings or building parts, fact sheets in the electrical engineering domain are created for component groups and fact sheets in the mechanical engineering domain are created on a system or component basis. The number of the fact sheets differs from plant to plant. The number of fact sheets ranges in the civil engineering domain from 25 to 65, in the electrical engineering domain from 50 to 70 and in the mechanical engineering domain from 30 to 45. In Annex A of IAEA-TECDOC-1402 an example of a fact sheet for electrical components used in one of the Swiss NPPs is illustrated. ENSI intends to provide a description of the structure of the fact sheets used in the different engineering domains of the Swiss NPPs as an annex to the thematic presentations during the workshop. There is a direct link between the fact sheets and the TLAA. The results of the monitoring and the maintenance programmes to be performed in the SWISS NPPs (see chapter 2.3.3 of the NAR) have to be implemented in the fact sheets. These plant programms include methods for the prediction of time dependent degradation like cable deposition, cable accelerated ageing tests, monitoring of fatigue-relevant components or monitoring of embrittlement in the RPV materials. All these informations will be considered in the revalidation of the TLAA.
CH-93 |  | EC | Switzerland | 01. General information | 7 | "…These processes defines the responsibilities and procedures for the ageing-related assessment of safety relevant SSCs…" Questions: Are the responsibilities and procedures pretty similar between the NPPs? Size of the teams dedicated to ageing management? |  | As described in Chapter 2.3 of the Swiss NAR the implementation of the overall AMP require similar responsibilities and procedures in all Swiss NPPs. The more than 25 individual members of the GSKL group and their expert teams are responsible for the implementation of the overall AMP in their plant. For specific tasks they form individual teams with persons from other departments or fields of their plant.
CH-94 |  | EC | Switzerland | 01. General information | 7 | "According to requirements in guideline ENSI-B10 only specialist personnel with high level of qualification and specific experience in the area may be responsible for ageing management …" Questions: Is it possible to have examples of competence and experience requirements used by the Swiss NPPs to appoint expert in the field of ageing management? |  | ENSI (and of course the licensees) require persons with a technical or scientifical degree or similar qualification and theoretical background concerning ageing management. As described before, the individual members of the GSKL group and their expert teams are responsible for the implementation of the overall AMP in their departments of their individual plants. On one hand, the GSKL group and their expert teams act for new persons working in the field of ageing management as a platform for knowledge transfer. On the other hand, experienced members are involved in international activities, in particular in contributing to the drafting of different IAEA Techdocs and Safety Guides and to the IAEA IGALL project.
CH-95 |  | EC | Switzerland | 01. General information | 8 | " According to the guide, structures are inspected at least every 10 years for the ageing mechanisms. " What is the exact frequency of inspections for all SSCs identified, specifically dedicated to ageing ? |  | On page 8 of the NAR a maximum inspection interval of 10 years is mentioned with regard to civil structures. The regulatory basis defining the maximum inspection intervals and the minimum inspections requirements for all SSCs are given on page 11 of the NAR. Taking these regulations into account it is an important task of the ageing management process to define new inspections or reduce existing inspection intervals if relevant ageing effects are meant to challenge the integrity and functionality of the SSCs. There are many examples were intervals for augmented inspections are set by the process of ageing management, e.g.: - RPV nozzle dissimilar metal welds with nickel-based alloy 182 and 82 with UT-inspection intervals as low as 3 years. - Yearly inspections (UT or VT) on core shroud indications. - Annual mechanized visual leak inspection of all RPV penetrations. - Inspections for piping which may undergo FAC as defined by a plant specific COMSY analysis. - LIRA measurements on selected cable sections. - Yearly inspection of inlet structures (service water systems) - Annual electrical and optical testing of some safety relevant cables.
CH-96 |  | EC | Switzerland | 01. General information | 14 | "ENSI also performs targeted inspections based on the information it received. " Question: What is the frequency of inspection performed by ENSI on the topic ageing management? |  | In general, the scope of regular based AM-focused inspections performed within ENSIs annual basic inspection programm is limited. As indicated in chapter 2.6 of the NAR ENSI prefers to focus on targeted inspections based on the informations gained from the regulatory oversight process. Typically, most inspections of mechanical components are performed during the annual refuelling outages. Specific targets for these inspections are selected based on the inspection and maintenance programs. Inspection topics include non-destructive examinations of major components such as RPV welds, system walk-downs, replacement of components, etc. The inspection includes a review of the relevant procedures, the execution of the work, and the obtained results. A particular focus of inspections is placed on special measures defined on the basis of AMP findings, such as an extended scope of NDE due to (inter)national operating experience. The implementation of the ageing management program itself is reviewed through regular meetings with the licensee (which are not necessarily conducted in the form of a formal inspection) and through review of the annual reporting according to guideline ENSI-B02. ENSI is reviewing the updated fact sheets for civil structures, including randomly also the detail inspection reports of the testing institute. Main findings with a possible relevance to the structural safety of buildings are visually inspected by civil engineering specialists from ENSI to make an independent assessment. Recent examples of ENSI-inspections in Beznau NPP are possible AAR-damages at the weathered concrete containment, the shadow gaps with locally beginning of corrosion of reinforcement due to the carbonation of the concrete at different buildings, fire protection bulkheads, roof sealing membranes, inspection gallery in the foundation plate. ENSI inspects ageing management of electrical components as part of its annual inspection planning. In the case of a thematic inspection, the corresponding system (for example reactor protection system or well water pump) is also assessed with regard to aging (for example module boards) including the associated connections and wiring (visual inspection) and any abnormalities were noted and evaluated. The metrological tests (for example, Tan δ) and the trend monitoring are checked on the basis of the annual reporting for aging monitoring with regard to the basics and the latest findings, and the planned maintenance work is checked.
CH-97 |  | EC | Switzerland | 01. General information | v | "With the introduction of guideline ENSI-B01 in 2011, the ageing management programme was especially expanded to include all safety classified structures" Questions: Were the structures not included in the AMP before? What is the current situation following the introduction of ENSI-B01? |  | In the initial phase of implementing an AMP for civil structures in the Swiss NPP the focus was on buildings which contain the safety relevant components (e.g. reactor building, electrical building and special emergency building). These buildings belong to the building class BC I. In the context of establishing the programme for LTO of the Swiss NPPs ENSI decided that the existing AMP for civil structures has to be expanded with respect to all buildings which contain safety related components (e.g. the turbine building and radwaste building). These buildings belong to the building class BC II. The todays AMPs for civil structures in the Swiss NNP comprise all buildings classified as BC I and BC II.
CH-98 |  | EC | Switzerland | 01. General information | vi | "By establishing a common project of the GSKL, …is ensured through the specially-founded expert teams" Questions: Size of the team? Differences between the NPPs? |  | As described in Chapter 2.3 of the Swiss NAR the implementation of the overall AMP require similar responsibilities and procedures in all Swiss NPPs. The more than 25 individual members of the GSKL group and their expert teams are responsible for the implementation of the overall AMP in their plant.
CH-99 |  | EC | Switzerland | 03. Electrical cables | Generic 17-34 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found. |  | The different cable groups defined for the AMP in the Swiss NPPs have been described in chapter 3.1.1 of the NAR.
CH-100 |  | EC | Switzerland | 03. Electrical cables | Generic 17-34 | The report does not mention MV cables buried or in trenches. Does this mean that such (safety relevant) cables do not exist in Swiss plants? |  | The information about cable routing is collected in the fact sheets part 3. Most of the safety relevant cables in the Swiss NPP are laid dry. Otherwise they are qualified for wet conditions.
CH-101 |  | EC | Switzerland | 03. Electrical cables | Generic 17-34 | The acceptance criteria for cable measurements are either not mentioned at all, or reference is made to maintenance procedures (KKL). However this information was requested in the TPR Technical Specification. |  | The acceptance criteria are established in the cable fact sheets part 3 (Examples for low voltage cables: Insulation resistance ≥ 1 MOHM according electrosuisse, Elongation at break e ≥ 50%; examples for medium voltage cables: Tan delta: values according to EPRI, Report 3002000557).
CH-102 |  | EC | Switzerland | 04. Concealed pipework | 35-38 | Beznau NPP: The argumentation of the licensee, that the design of the essential service water system excludes any relevant degradation mechanism is reasonable in principle. However, some sort of periodic inspection at least on an occasional basis (every 10 years) would be desirable. Are there any plans for such inspections? |  | No inspections have been performed before the service water system at Beznau NPP was replaced partially in 2011/2012. From todays point of view no inspection of the 3m part of stainless pipe is planned neither from inside nor from outside. During planned maintenance work at the raw water pumps visual inspection of the accessible piping can be used as reference.
CH-103 |  | EC | Switzerland | 04. Concealed pipework | 35-38 | Goesgen NPP: Difficult to understand how renewed concealed pipework of service water systems look like. Which materials are used for which section? Which sections are coated? What is the environment of the pipe (dry atmosphere for sections in ducts, soil for buried sections?)? |  | The primary and secondary service water system in Gösgen NPP consist of different kinds of pipework. The type of pipework used is depending on the diameter. Concealed pipework with a diameter smaller 350 mm was built during erection time from low carbon steel without a coating of the inner surface. The outer surface was coated. Concealed pipework with a diameter between 350 and 600 mm consists of low carbon steel with an inner and outer coating. Concealed pipework with a diameter larger 600 mm consist either of cement pipework or of low carbon steel pipework having an inner and outer cement coating. The piping either is buried in soil (e.g. low carbon steel pipework having an inner and outer cement coating) or is within non-accessible channels (e.g. pipework with a diameter below 350 mm). In general, the experience with concealed pipework is positive. Visual inspections of the inner surface by means of walkdows within the piping of large diameter pipework showed no signs for degradation of the functionality of the pipework. The experience with the low carbon steel pipework having an inner coating is positive as well. The performed inspections show, that generally the inner coating is in good condition. In few cases, damages of the inner coating have been found. The corrosive medium (river water) caused in these cases corrosion of the low carbon steel. However, this type of piping is used in KKG in concealed areas as well as in accessible channels. In those pipings appeared neither leakages nor loss of piping wall thickness that endangered the functionality of the systems. However, due to the river water running through the system, corrosion is a relevant ageing mechanism for uncoated low carbon steel piping and coated low carbon steel piping, if the coating is damaged. Therefore, in the last 20 years the uncoated pipework made from low carbon steel in the concealed as well as in the accessible areas of the plant were replaced by austenitic pipework as part of the preventive maintenance. Up to now, KKG has 20 years of positive experience with austenitic pipework in service water systems (river water) for accessible as well as concealed pipework. In the concealed as well as in the accessible areas no leakages were detected at austenitic pipework. In two cases of concealed piping the low carbon steel piping was not replaced by an austenitic steel piping but equipped with a polymeric inlay. The inlay is made of Polyethylene and was mounted during an outage of the system. The method used allowed the mounting of an inlay in the existing low carbon steel pipework from the erection time.
CH-104 |  | EC | Switzerland | 05. Reactor Pressure Vessels | Chapter 5.1.3, page 42 | Correct "while the reference temperature ART must not fall below a value of 93 C". It should be the opposite: "while the reference temperature ART must be less than 93 C" |  | This notice is correct. Thank you very much.
CH-105 |  | EC | Switzerland | 07. Concrete containment structures | 60 | It is mentioned that one special test has been performed to confirm that the pre-stressing of the annular girder between dome and outer cylinder is sufficient. Could you provide some details on how the level of pre-stressing was determined. Was any relaxation of the pre-stressing force found? Is it necessary to have a more systematic monitoring of this in future? |  | The level or loss of pre-stressing was not scope of the investigations at the anchor heads (see also question to this topic). The loss of pre-stressing because of relaxation, creep, shrinkage is considered in the design. The tendons are grouted and the loss of prestressing is not relevant for the ultimate resistance. The serviceability of the concrete containment plays a minor role, as the primary containments in the Swiss NPPs are steel shells which are designed to withstand the overpressure load cases and to fulfil the leak tightness requirements.
CH-106 |  | EC | Switzerland | 07. Concrete containment structures | 55-58 | Section 7.1.3. There is not really any information provided regarding acceptance criteria, e.g. for cracks identified during visual inspections. |  | The mentioned GSKL civil engineering guide provides a separate appendix with a detailed description of assessment and acceptance criteria for all types of structural elements. It is not easy to define quantitative acceptance criteria from predominantly visual inspections. However the detailed assessment criteria may be categorized as "semi-quantitative". They contain quantitative elements, some examples: for level 1 and 2: depth of carbonation significantly less than coverage depth of the reinforcing steel bars; for level 2: less than 10% of the surface with significant cracks.
CH-107 |  | EC | Switzerland | 07. Concrete containment structures | General | Is there any monitoring of settlement of the reactor buildings at Swiss NPPs? |  | The monitoring of settlements in Swiss NPP is not uniform and varies from plant to plant. Basically there is no permanent instrumentation and measurement present, the settlements are measured by conventional survey systems according to the inspection plan every 5 to 10 years. In Mühleberg NPP the measurements have been discontinued, because the last results showed, that the settlements have come to a complete stop.
CH-108 |  | EC | Switzerland | 09. Overall assessment and general conclusions | 62 | The SALTO peer review is a comprehensive safety review covering the evaluation of programmes and performance for the safe continued operation of nuclear power plants on the basis of the IAEA’s Safety Standards and other guidance documents. What is the regulatory view on the benefits to the licensee of inviting such a review, and does it plan to encourage licensees to invite such a review in the future? |  | Taking into account that the licensees of the Swiss NPPs had already been required to introduce an AMP for safety-relevant SSCs at the end of 1991 and based on ENSIs conclusion concerning the implementation of an effective and comprehensive AMP in chapter 2.7 of the NAR the benefit of such an review is judged to be limited. Although the basic principles and scoping and screening processes of the Swiss AMP and SALTO are similar there are differences in the AMP approach itself which makes it difficult to review the AMP of the Swiss plants using the SALTO methodology. From ENSIs point of view it is more promising to review the Swiss AMPs in the frame of an OSART mission (LTO modul) as already succesfully performed for the NPP Mühleberg.
CZ-1 |  | Poland | Czech Republic | 01. General information | 30 | 1. How do you ensure independent evaluation of the existing maintenance practices by independence committee? What kind of criteria this body must fulfill to achieve required status and give guarantee of independency? | Website | The independent committe/advisory group (in the meaning of SSR 3 Requirement 6 ) is based on internal documentation where the status of this committe is defined - the chairman, deputy chairman, QA manager, internal safety supervisor are not from reactor division and the rest of the committe is composed also of staff outside from reactor operation division - former employees of regulatory body, guests like former reactor director as personnels with relevant expertise
CZ-2 |  | Bulgaria | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | p. 26 | In subchapter “Methods used for identifying SSCs within the scope of overall AMP” , “c” is stated that “From the list of all NPP equipment the following equipment is selected for the purposes of AM: c) Equipment recommended from the PSA ” Would you provide more information about the methods and instruments (software) which are used to identify such equipment for the purposes of AM? Would you give some examples for such equipment if it’s possible. | Website | Identification of SCs into the scope according PSA is performed for following failure cosenquences: - SCs which failures affect realiability of reactor unit to respons on initiating events considered in PSA - SCs which failures cause initiating event - SCs which failures can cause both above mentioned effects Criteria used for identification of these SCs are: - F-V (FC) - Fussel-Vesely Importance (Fractional Contribution) - CFDP - Conditional Fuel Damage Probability - CLERP (Conditional Large Early Release Probability) - RIF (Risk Increase Factor) Example of equipment in the scope of AMP selected according to criterion c) Equipment recommended from the PSA: - Rubber compensators in the tercial cooling water pipelines near main condensers
CZ-3 |  | Bulgaria | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | p.21 | Would you please clarify whether the following IAEA reports and guides had been used too: 1. IAEA, Methodology for the Management of Ageing of Nuclear Power Plants Components Important to Safety, Technical Reports Series No. 338, IAEA, Vienna (1992); 2. IAEA, Data Collection and Record Keeping for the Management of Nuclear Power Plants Ageing, Safety Reports Series No. 50-P-3, IAEA, Vienna (1991); 3. IAEA, Maintenance, Surveillance and In-service Inspection of Nuclear Power Plants, Safety Standards Series Safety Guide No. NS-G-2.6, IAEA, Vienna (2002); 4. IAEA, A system for the Feedback of Experience from Events in Nuclear Installations, Safety Guide No. NS-G-2.11, IAEA, Vienna (2006) | Website | Yes, these reports had been used also. Reports 1. and 2. were used in 2004 and 2005 as a one of basic documents during development of Ageing management methodology for Czech NPPs under Research project of the Ministry of Industry and Trade and ČEZ mentioned on the page 49. Safety guide 3. is used as a one of basic document for development and implementation of appropriate programmes (maintenance, surveillance, ISI) mentioned on the page 39. External experience is evaluated according to ČEZ methodology ČEZ_ME_0723 Internal and External Feedback from Operating Experience in NPP, which corresponds also to IAEA safety guide 4.
CZ-4 |  | EC | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 29 | How did SÚJB evaluate the OAMP effectiveness indicators used by the operators? |  | SÚJB evaluates the OAMP effectiveness through the evaluation of health reports, inspections and operational experience feedback.
CZ-5 |  | EC | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 29 | It would be appreciated if examples could be provided of the effectiveness monitoring of individual specific AMPs and the performance indicators used. |  | Examples of performance parameters for Flow accelerated corrosion AMP: - ratio of number of inspections to total number of components in the programme (resulting trend can show the stability of the programme and overall status of components in the programme) - ratio of performed inspections to number of inspections planned within this programme - AMP effectiveness indicator (U=1-x/∑, where x = number of failures on SCs in the scope of AMP caused by flow accelerated corrosion, ∑ = total number of components in the programme)
CZ-6 |  | EC | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 31 | Sub-section a) of the Ageing assessment topic is not adequately addressed. One reference is included, relevant to the development of component specific AMPs, but certainly more documents could be listed which are relevant for the preparation of OAMP. |  | In this chapter only main management system documents is mentioned. Other management system documents are mentioned on page 22. Next requirements are stated in the Ref. 26. Within the stage of understanding of ageing, other sources, for example technical specification of equipment, manufacturer´s recomendation, technical documentation and legislative requirements serves also as a basis for preparation of specific or component specific AMPs.
CZ-7 |  | EC | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 49 | Not clear if the last paragraph of 2.5.1 applies for both operators, given the previously provided information about regulatory conditions in the Decision on Operation for Dukovany NPP. |  | Yes, it applies for both Czech NPPs (operator of both NPPs is the same).
CZ-8 |  | EC | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 21, 50 | How often would Dukovany NPP have to update the documents demonstrating the possibility of safe LTO according to the condition in the latest Decision on Operation? |  | FSAR, Health Reports, results of AMPs - each year AMR, TLAA - every 5 years PSR - every 10 years
CZ-9 |  | General AMP expert group | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation |  | Has a dedicated plant programme to manage technological obsolescence been developed and implemented? | expert group 3 on other topics / expert group 1 | A programme to address obsolescence is part of the maintenance programme. The Care of asset department is responsible for availability and quality of spare parts and information on availability and quality of spare parts for each technological system is presented in the Health Report every year.
CZ-10 |  | General AMP expert group | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 19 | An important attribute in ageing management is the establishment of acceptance criteria. Are there established criterion that the SSCs shall maintain their intended function during design basis events (incl. severe accident)? | expert group 3 on other topics / expert group 1 | General requierement are given in Decree No. 329/2017 Coll. To ensure the fulfillment of intended safety functions of each SCC for DBA, the criteria are defined within the AMPs (component, specific), maintenance programme (maintenance templates), ISI, Limits and Conditions. Criteria given in above mentioned programmes covers fulfillment of pasive and active safety funcions of such SCCs.
CZ-11 |  | General AMP expert group | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 26 | Has the plant adopted a suitable organizational structure for preparation and implementation of the AM programme? Is the number of staff and their required qualifications needed to run the activities adequate to the scope of work and duties? | expert group 3 on other topics / expert group 1 | Yes the company adopted a suitable organizational structure for preparation and implementation of the overall AMP. For both NPPs there is a common Ageing Management and LTO department which is responsible for implementation and coordination of OAMP, this department is part of Design Authority section which was created in January 2016. Number of staff is continuously increased in connection with the implementation of new AMPs (2 new entrances in 2017, 1 in 2018). The company has implemented Knowledge management programme for ensuring and maintaining the transfer of know-how from experienced staff to new entrances. CEZ is also member of EPRI and staff participate in international programmes, for example SALTO, IGALL etc.
CZ-12 |  | General AMP expert group | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 26 | Are there another SSCs subjected to the ageing management (Safety Class 4) whose failure may prevent SSCs important to safety from fulfilling their intended functions? | expert group 3 on other topics / expert group 1 | Yes, according to chapter 2.3.1.1 of National assessment report from the list of all NPP equipment the following equipment is selected for the purposes of AM: a) All selected equipment under the Atomic Act [2] (equipment with the assigned Safety Class 1, 2, 3) b) Equipment with the criticality level 1 and 2 assigned under ČEZ_ME_0608 [34] and equipment fulfilling the safety function of category 1 or 2 important to nuclear safety (under ČEZ_ME_0901 [35]) c) Equipment recommended from the PSA d) Other equipment recommended on the basis of global good practice and operating experience So it means, that SSCs selected according critera b, c, d are SSCs without safety class.
CZ-13 |  | General AMP expert group | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 26 | Are the master list of plant SSCs subjected to the ageing management developed and properly documented? And is the relevant data for all SSCs accessible (indicating e.g. intended function, safety class, other scoping criteria, etc)? Which total number of SSCs are included in the list (approx.) | expert group 3 on other topics / expert group 1 | Master list of plant SSCs subjected to the ageing management is developed and properly documented in a database. In database there is also included relevant data like safety class, other scoping criteria and information on intended function. For example approximately 200.000 SSCs (for 4 units) are included in the list for Dukovany NPP.
CZ-14 |  | General AMP expert group | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 38 | Does the plants used risk-informed approach for determine time interval and extent of testing for in-service inspection of mechanical components? | expert group 3 on other topics / expert group 1 | In-service inspection programme of mechanical components is primarily based on deterministic approach. But Risk-informed approach is implemented within few AMPs (for example AMP on areas with risk weld joints, AMP for steam generators).
CZ-15 |  | General AMP expert group | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 46 | Has the plants established a list of existing time limited ageing analyses (TLAAs)? Which methods and information sources were used to identify the TLAAs? | expert group 3 on other topics / expert group 1 | For Dukovany NPP there is a list of existing TLAAs. For Temelin NPP it is now in development. Existing TLAAs are identified on the basis of review of these information sources: - FSAR - NPP archive containing design documentation (including original Structural and lifetime assessments) - database of Structural and lifetime assessments performed during operation - EQ database Results of this review are then compared with the list of TLAAs included in IAEA IGALL. Results of this comparison together with results of ageing management review are then evaluated and needs for development of additional TLAAs are considered.
CZ-16 |  | General AMP expert group | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 42 | Does the plants developed electronic database and are there all information and documentation necessary for an effective ageing management in auditable and retrievable form? | expert group 3 on other topics / expert group 1 | Plants use following electronic databases in ageing management process: LTOs - contains results of specific ageing management programmes and results of periodic ageing assessment Asses Suite 8 - contains information on all maintenance activities, and also results of periodic ageing assessment Also where it is usefull there are developed specific databases for specific ageing management programmes (e. g. Cables AMP, Flow accelerated corrosion AMP, AMP for RPV). These databases contain all detail information of these programmes.
CZ-17 |  | Germany | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 20 | In section 2.1. it is mentioned that SJUB intends to revise Regulatory Saftey Guide BN-JB-2.1 "Ageing Management for Nuclear Power Plants" to take into account IAEA SSG-48 "Ageing Management and Development of a Programme for Long Term Operation of Nuclear Power Plants". Untill when will this revision been made? What are the expected changes to the Guide? | email | Primary intention for revision of SÚJB guide on AM for NPP is to adopt the new legislative (which requirements are based on actuall international requirements). Also the better precision of defined requirements needs to be done. The date of revision is given by SÚJB internal managing document for revisions of SÚJB safety guides. Planned date is 09/2018.
CZ-18 |  | Germany | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 24 | In Section 2.3.1.1 it is mentioned that one of the ageing management principles of CEZ with reference to CEZ_ST_0065 is that the maintenance of major components shall be carried out to timely detect ageing effects and to allow for preventive and remedial actions. Which components fall under this principle? | email | This is a general statement from high level corporate document where the main safety requirements for NPPs are established. This requirement is fulfilled by selection of SSCs for ageing management: a) All selected equipment under the Atomic Act [2] (equipment with the assigned Safety Class 1, 2, 3) b) Equipment with the criticality level 1 and 2 assigned under ČEZ_ME_0608 [34] and equipment fulfilling the safety function of category 1 or 2 important to nuclear safety (under ČEZ_ME_0901 [35]) c) Equipment recommended from the PSA d) Other equipment recommended on the basis of global good practice and operating experience
CZ-19 |  | Germany | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 29 | In section 2.3.1.2 it is mentioned that the AMP of LVR-15 will be brought in line with new requirements of the revised atomic act until end of 2018. What are the main changes that need to be implmented in the AMP of LVR-15 to be in line with the atomic act? | email | The new law and decree require setting rules and selection criteria which SSC are selected for AMP (not ony safety systems); setting up the system for monitoring and detection of the status, selecting methods for testing and tracking; setting up the criteria of acceptability corrective measures. The process has to be set up more systematically, also other components those failures can affect the fulfilment of safety function shall be evaluated.
CZ-20 |  | Netherlands | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 2.3.1.2/p29 | Could you provide the most important examples of grading? | email | The graded approach was used for system of selection of SSC for which the ageing management was set (maily for SSC with direct influence on nuclear safety) and in setting up the corrective and preventive measures based on the importance of the system
CZ-21 |  | Netherlands | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 2.3.1.2/p30 | Why does the AMP not contain experiments, some of which might exist for a longer time and might have safety impacts (IAEA had recommended Belgium to consider this). | email | During the main reconstruction in 1987-1989 the AL vessel was replaced with SS vessel but no surveillance program was set up with material samples - the main concern is not the radiation embrittlement but corrosion of joints of SS vessel and AL radial beam tubes - since 2008 there is an surveillance sample (same size, same material) for this purpose. For assesment of welds on connection of primary piping the measurement of vibration is being set up, during the I&C reconstruction the assesment of residual life of electric cables was carried out, etc. But this can not provide the same info as long-term systematic measurement or experiments.
CZ-22 |  | Netherlands | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 2.3.3.2/p40 | No information is provided concerning trending. Please provide the main parameter trendings that are carried out. | email | The system of service inspection programme is gathering data and their trends, including: - vibration and run of main circulation pumps (as an indication of the need for adjustment), measurement of current through the electric motor and inlet and outlet pressure (as indication of motor and pump status) - insulation resistance of electic components (as an indication of the necessity of exchange) - tightness of seals (as an indication of the necessity of exchange) - measurement of wall thickness of heat exchanger pipes (as indication possible corrosion) - visual inspection of surface of reactor vessel, fuel storage, main pumps (as an indication of the origin and development of corrosion or physical damage) - measurement of wall thickness of horizontal neutron beam tube as indication of possible corrosion - measurement of geometry changes of absorbers on test stand as indication of possible swelling or damage on the rod
CZ-23 |  | United Kingdom | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 24 | The report states that "lifetime shall be managed for all equipment, in a graded manner in relation to the specified category of equipment". Please explain how this is implemented and provide some examples of the differences in ageing management for high and low category equipment. | Website | For the most important SSCs (RPV, SG, presurrizer, SC1 pipilines, etc.) there is ageing management strategy based on performance of components specific AMPs and AMPs specific for degradation mechanism. For the rest of SSCs in the scope for AMP there is ageing management strategy based on preventive maintenance. Setup of AMPs for SSCs under the both strategies is based on the results of the ageing management review and is maintained updated on the basis of overall ageing management activities (e.g. monitoring of effectivense of ageing management for all SCCs in the scope).
CZ-24 |  | United Kingdom | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 24 & 42 | It appears that the overall AMP is reviewed at each PSR and also an ageing management review (AMR) is undertaken every 5 years. What is the difference between the review in the PSR and the AMR? | Website | The main difference is that in PSR the overall AMP is reviewed on programatic level. In the AMR there is AMP reviewed for each particular component in the scope.
CZ-25 |  | United Kingdom | Czech Republic | 02. Overall Ageing Management Programme requirements and implementation | 51 | The first paragraph of page 51 appears to say that for Temelin there are outstanding activities for implementation of the overall AMP and these will be completed (terminated) in 2018. Please provide further explanation of what needs to be completed and whether it includes any inspection activities or modifications on the plant. | Website | Evaluation of PSR after 20 years of operation will be finished in December 2018. AMR and identification of TLAAs will be completed by the end of 2018. Part of AMR is also one-time inspections. Results and recomendations from PSR and AMR will be included in Action plan with many measures and modifications which will be implemented from 2019.
CZ-26 |  | Bulgaria | Czech Republic | 03. Electrical cables | p. 55 | Could you provide more detailed information about the results from the two methods mentioned – cable deposit and accelerated aging. Do the results overlap and which method gives better results? | Website | Accelerated ageing is always the first step. From the results, ageing curves are prepared; they show trend of functional properties change with time. Theses curves for individual cables are used for prediction of the cable ageing in service at different temperatures and dose rates. Accelerated ageing is performed at conditions relevant for cables, e.g for some old PVC cable the ageing time was 670 days. It means the acceleration factor is quite low. Results from the cable deposits are used for precising the ageing curves. Of course, cable ageing in deposits gives better results as the cables age at normal service conditions.
CZ-27 |  | Bulgaria | Czech Republic | 03. Electrical cables | p.69 | Could you please clarify is the condition of cables removed from operation similar to the laboratories assessment and the cable deposit assessment? | Website | In the past, occasionally, cable removed from the service were evaluated in laboratory and compared the in service condition with prediction. In 2017 a systematic measurement was performed. 79 cables of 16 different safety cable types were removed from Dukovany NPP service. All these cables had known history and environmental operation conditions (e.g. temperature and dose rate). Elongation at break of jacket and at least of two insulations of each cable were measured. Results were compared with prediction based on models from accelerated ageing and presised from deposit samples. Criteria were met in more than 96 %, i.e. very good agreement model vs. reality.
CZ-28 |  | Bulgaria | Czech Republic | 03. Electrical cables | chapter 3 | Could you provide more information about the process of inspection and assessment of ageing of airtight cable penetrations in “Temelin” NPP. | Website | Regular visual inspection and leakage test are performed. These methods provide sufficient inputs for ageing management of airtight cable penetrations.
CZ-29 |  | Bulgaria | Czech Republic | 03. Electrical cables | p.52 | No information is presented concerning the cables’ insulation material such as: polyethylene (PE) insulation, cross-linked polyethylene (XLPE) polyvinyl chloride (PVC), ethylene vinyl acetate (EVA), ethylene propylene rubber (EPR), a silicone halogen-free compound (SiHF) etc. Would you please give more information on that matter? | Website | Page 53 shows number of safety related cables in Czech NPPs. For all these types the materials are known. Old safety cables from Dukovany NPP are made of PVC, PE, and in few cases XLPE. Modern cables installed since nineties at both Czech NPPs are made of XLPE, EVA, EPR, EPDM, SiR. SiR is only exceptionally.
CZ-30 |  | Cables expert group | Czech republic | 03. Electrical cables | 57/58 | Are there any other power safety cables, with voltage >3 KV, buried or in trenches, that could be affected by significant moisture or submergence? | expert group 3 | In the Temelín NPP, there are no power supply cables buried or in trenches with the voltage level over 3 kV that are classified as safety cables. Dukovany NPP operates few safety related cables over 3 kV in trenches, buried are not safety related. In trenches they are installedn in a position, which excludes possibility to be submerged. Cables affected by moisture (few location with condensed water) were reported - found during visual inspections. Location with possible soak were sealed. No failure due to moisture.
CZ-31 |  | Cables expert group | Czech republic | 03. Electrical cables | 62 | In terms of the degradation mechanism for cables, have those been analysed for the degradation mechanisms “water treeing formation"? | expert group 3 | Water treeing formation is degradation mechanism important for high voltage cables (please note, Czech rules do not use the term medium voltage, see page 57). This degradation mechanism has been described in ageing management programme for high voltage cables which was issued in 2014 and again more detailed in 2015.
CZ-32 |  | Cables expert group | Czech republic | 03. Electrical cables | 62/79 | Were there specific walk downs on cable routings, for identification of hot-spots on the cables, performed at Dukovany and Temelin sites? | expert group 3 | First walkdowns related to cables were performed in 1997 when started systematic environmental monitoring program. Firstly, the walkdowns were focused on the locations where harsh parameters were expected, like steam generator, primary piping etc – on hot spots. At the same time first monitors were installed at these locations. With increasing knowledge the cable walkdowns were extended to whole NPP Dukovany as well as Dukovany, i.e. not only on hot spots. For the routing exists a schedule.
CZ-33 |  | Cables expert group | Czech republic | 03. Electrical cables | 69 | The "VKK Validation and verification" project, where numerous cables from Dukovany NPP were tested, was implemented in 2017. Is this project completed by now and what are the relevant findings, in terms of comparison of mechanical properties to the results of other analysis undertaken? | expert group 3 | In 2017 a systematic measurement was performed. 79 cables of 16 different safety cable types were removed from Dukovany NPP service. All these cables had known history and environmental operation conditions (e.g. temperature and dose rate). Elongation at break of jacket and at least of two insulations of each cable were measured. Results were compared with prediction based on models from accelerated ageing and presised from deposit samples. Criteria were met in more than 96 %, i.e. very good agreement model vs. reality.
CZ-34 |  | Cables expert group | Czech republic | 03. Electrical cables | 74 | The "recommendations have been issued to replace the older types of cables from the most stressed locations, e.g. KPOBOV, KPOSG, KMPVEV". Did this replacement already took place? | expert group 3 | Safety related cables: KPOBOV (only 7 remaining cables at NPP, 3 of them at temperature 42 °C, the rest below 40 °C, all are scheduled to be replaced), KMPEVE (only 1 remaining, operation at 30 °C), KPOSG (complicated replacement due to the lead armoring, the replacement of cables operated above 40 °C has been already scheduled for 2018-2020)
CZ-35 |  | Cables expert group | Czech republic | 03. Electrical cables | 74 | The recommendation for the replacement of the cables, was it in effect the outcome of the " VKK validation and verification" project or was it due to the prediction by the AMPC ? | expert group 3 | Recommendation for cable replacement was the outcome of AMPC – from accelerated ageing experiments, deposit samples and cables removed from NPP operation. Process VVK validation and verification was finished 12/2017. Results from this process are one of the inputs for next remedial actions.
CZ-36 |  | Concealed pipework expert group | Czech Republic | 03. Electrical cables | 53 | It is stated in Para 3.1.1.1 that the AMPC selection of cables includes all types of safety cables including optical ones. No mentions were found in the report about optical cable assessment. Were fibre-optic cables actually assessed? What acceptance criteria are used for assessment of fibre-optic cables? | expert group 5 | Fiber optic cables are out of the scope of Technical Specification. Hence, they were only mentioned, but details were not provided. Ageing management programme focused on fiber optic cable was prepared in 2016. It summarizes all safety optical cable at Czech NPPs, their operation conditions operation history and functional measurement performed at NPP etc. In 2018 fiber optic cables will be installed in cable deposits. Since 2015 accelerated ageing experiments have been performed. Main criterion is attenuation. Its critical value depends on the cable length.
CZ-37 |  | Concealed pipework expert group | Czech Republic | 03. Electrical cables | Chapters 3.2, 3.3 | Were some weaknesses of AMPC program identified by the licensees and/or regulator? | expert group 5 | The need to implement the AMPC more precisly for safety cables in mild enviroment was identified. Based on this fact the regulator imposed on licencee (within the licence for further operation of the Dukovany NPP conditions) to perform the diagnostic measuring on sufficient sample of cable types used on NPPn in a mild environment. Licencee continuously works on meeting this requirement.
CZ-38 |  | EC | Czech Republic | 03. Electrical cables | 174-179 | It would be helpful to have the insulation material indicated for the cable types. |  | Materials for each cable type have been identified, they are based mainly on PVC, PE, XLPE, EVA, EPR, EPDM, SiR. They are described e.g. in software system VVK. Not only materials are described, system VVK provides more information about all cable types e.g. producer, structure, technical conditions, photo, worst installation at NPP and other.
CZ-39 |  | EC | Czech Republic | 03. Electrical cables | 67, 72 | What is the frequency of visual inspections of cables? |  | Visual inspections of cables are performed according to schedule described in Visual inspection programme, typically every 4 years in the worst locations like steam generator room. Interval is longer for locations with milder conditions. There is a plan to inspect all the rooms where safety related cables are installed. At present, around 300 rooms in each NPP have been inspected, some of them more times.
CZ-40 |  | Finland | Czech Republic | 03. Electrical cables | 19-21 | Requirements for ageing management are given as conditions of case by case decisions. Some countries have specific regulations for ageing management or part of certain technical regulation is dedicated to ageing management. Does SÚJB degree No. 21/2017 have specific requirements for ageing management? | Website | Decree No. 21/2017 Coll. determines the requirements on ageing management process in § 11. In § 12 the requirements on AM programme are given. More information can also be found in chapter 2.1 - pages 19-21.
CZ-41 |  | Finland | Czech Republic | 03. Electrical cables | 59-60 | The difference of PCS (Protection and Control System) and I&C is not clear. Could that be explained more? | Website | Historically, the safety part of the system is called PCS, while the other (safety related and non-safety) parts are called I&C. The PCS system consists of reactor main control system for measurement and control of neutron flux (neutron instrumentation, evaluation of signals to trip system, HMI, signal and system for operation of the safety rods) The I&C system consists of so called selected circuits (classified as safety related) based on measurement of technical parameters (temperature, pressure difference) which provide independent safety signals for reactor trip system (exceeding the outlet coolant temperature, temperature difference on the core, core head loss and water level in reactor) and other type of measurement (which are not classified as safety important SSCs)
CZ-42 |  | Finland | Czech Republic | 03. Electrical cables | 66-72 | Is thermography used to supplement the cable load and environmental parameters monitoring? | Website | Yes, thermography has been used. Mostly in areas outside the containment, because these locations are assessable during NPP operation.
CZ-43 |  | Germany | Czech Republic | 03. Electrical cables | 54, 68 | On p.54 and 68 it is described how cable deposits are used in the ageing management of Czech NPPs. In Dukovany the cable deposits were retrofitted in 2005 after several years of operation. Thus it is necessary to use cables for the deposits that have been subjected to an sufficient thermal and radiological load. On p. 68 it is further specified which cables were used for the deposits. Cables from the warehouse are described as "adequately pre-aged". How did those cables get exposed to a sufficient dose rate? Is the radiological loading covered by cables removed from NPP operation during replacements? If so, was it possible to use cables whose operational loading has both radiological and thermal loads of all cables in the respective ageing management group covered? | email | First part of cables for deposits in Dukovany NPP was taken from warehouse and pre-aged to simulate 20 years operation at the worst NPP conditions where these cables are operated. Pre-ageing was performed in UJV Rez where the cables were irradiated at 70 °C at the dose rate around 5 Gy/h. After 460 days of irradiation only thermal ageing at 70 °C continues for next 7 months. Later on, another cables have been installed into different cable deposits. They were cables removed from NPP or warehouse or supplier. In some case pre-ageing was necessary, some of them could be installed directly into the deposits. An analysis for each cable has been performed, i.e. where the cable was operated, how long it was in operation, worst condition of the same type at NPP etc. Then it has been decided if the cable need or not pre-ageing, at which conditions and in which deposit will be installed. All these information are summarized in separate documents.
CZ-44 |  | Germany | Czech Republic | 03. Electrical cables | 63 | Regarding non-destructive in-service testing of cables visual inspections are mentioned several times (e.g. p. 55 and 67). However electrical measurements are only briefly mentioned for MV cables on p.63 (tan delta and PD measurements). Are there any insulation resistance measurements and trending carried out on LV/MV cables, e.g. during preventive maintenance? | email | Yes. There are a lot of measurements performed at NPP. E.g. system ECAD is used for LV/HV cables at both Czech NPPs (Please note we have not category MV in Czech). Results from ECAD measurement are evaluated as function of time, always with marking and recommendation. The individual cable routes are measured and evaluated within regular maintenance and measurements of individual equipment, e.g. thermocouple or pressure sensors calibration, neutron flux measurement, tests of valve functionality, control of the fiber optic cable communication etc. These measurements are evaluated and achieved; but primarily they are not designed for cable ageing management programme
CZ-45 |  | Germany | Czech Republic | 03. Electrical cables | 65 | On p. 65 it is described how cables are re-qualified at UJV Rez on a "regular" basis. The reviewer understands that this also coveres LOCA tests if necessary. Is there a typical interval after which relevant parts of the qualification are reevaluated or is this an on-demand requalification for when the qualified lifetime is going to end? | email | Yes, it covers LOCA or HELB conditions if the cables need to perform their functions during accident. If cable is within the qualification period, re-qualification process is not needed. However the process of re-qualification starts app. 6 years (depending on type of the cable) before the end of qualification period .
CZ-46 |  | Germany | Czech Republic | 03. Electrical cables | 67 | On p.67 visual inspections of cable routes are described as an part of the monitoring, testing and inspection process. Is there a time frame specified for the maximum permissable duration in between inspections on individual cables? | email | Visual inspections are scheduled in Visual inspection methodology. The time interval depends on the location. For cables outside of containment with service temperature 25-30 °C, the time interval is 10 years. Opposite, very short interval 1 or 2 years is at specific locations.
CZ-47 |  | Netherlands | Czech Republic | 03. Electrical cables | 3.1.3 | What frequencies are used for the testing/inspection activiteits mentioned in chapter 3.1.3? | email | NPPs:The interval is described in Methodology for cable ageing monitoring. Environmental monitoring (according requirement), identification of hot spots (according requirement), visual inspections (1-10 years interval), deposit samples measurement (typically 5 years, if cable is degraded earlier), new samples for deposits (every year evaluated needs), residual life time evaluation with recommendations (every year), protocol of cable qualification (every year), methodology revision (according requirement), etc. On LVR-15 based on program of operation controls: - before every campain or once a month as a part of complex tests of systems - 1 year preriod for tests as a part of neutron instrumentation and I&C system and power supply - 5 year period as a part of revision of power distribution system
CZ-48 |  | Netherlands | Czech Republic | 03. Electrical cables | 3.1.3 | The inspection history mentioned in 3.1.3 seems to give an overview of the history of inspections, not the way the inspection history is used for trend monitoring. How are trends in inspection results controlled? | email | NPPs: Summary of inspection is on page 72. Trends are evaluated and reported. Visual inspection: The inspection interval within one location is 1-10 years, always a comparison with previous inspections is carried out and reported. If an important finding was detected, one year later is this finding checked if the problem was solved. At present, the visual inspection database has been modified to have better survey. Environmental parameters monitoring: changes are not expected. Nevertheless, selected locations on both Czech NPPs have been re-checked after 5-15 years of operation. Results are reported. Changes in the properties of cable deposits, their degradation: All the results are summarized in database, it allows to plot trends. Samples that are measured within one year are summarized and compared with previous measurement in end-of-year report. Moreover, all the deposit samples are described in separate report. This report displays trends in mechanical properties changes. Samples removed from operation, information from maintenance: information summarized in protocol of cable life time, which is issued every year. Trends are evaluated every year in Health reports. NPP operates SW system LTOsuite. Within this software, the equipment, including cables, are periodically evaluated. Research reactor: On LVR-15 the trending is used as a part o measurements of insulation resistance and gradual tracking of deterioration of properties of cables and thus the need for change
CZ-49 |  | Netherlands | Czech Republic | 03. Electrical cables | 3.1.4 | In section 3.1.4, it is stated that when a cable is assessed as near the end of its lofe, remedial actions are applied to extend the residual lifetime. Only a cable that is found non-compliant is immediately repaired or replaced. Why not take preventive actions such as replacement when the cable is assesed as at the end of its life? | email | End of life is assessed (calculated) using software VVK. It includes models and results from accelerated ageing, refined from cable deposit and operation samples measurement. Model uses also overall environmental parameters for selected room. Hence, results are always associated with some uncertainty. Therefore, it is only residual life-time assessment and must be firstly compared with on-site checking. Immediate cable replacement would be too conservative.
CZ-50 |  | Switzerland | Czech Republic | 03. Electrical cables | 38 | Table21: Is there an AMP for electronic devices (capacitor, relais, modules)? | Website | This question is out of scope of Technical Specification for Chapter 3 Electrical cables. There is no special AMP on these components. As the preventive maintenance is realized; degradation effects are known.
CZ-51 |  | Switzerland | Czech Republic | 03. Electrical cables | 57 | Textline8: What isolation material is used with temperatures of 60°C and dose rates of 0.1 Gy/h? What experiences have been made with it? Are there no locations with higher dose rates for cables? | Website | Chapter with these information deals with HV cables. There are installed only 2 cable types; PVSG-polyethylene cable with lead armoring) and 6-AYKCY (PVC cable). Nevertheless, only few cables are at these conditions. The PVC cable has been installed in cable deposit located at main circulating loop with parameters exceeding 60 °C/0.1 Gy/h. Cable is in good condition, elongation at break and insulation resistance is regularly mesured. PVSG cable has been thoroughly tested in UJV Rez laboratory within qualification of this cable type. Higher dose rate than 0.1 Gy/h and temperatures above 60 °C have been measured at NPP only at very few locations near main circulating loops. There are not cable routes. Cables connection sensors on primary loops are qualified for these values.
CZ-52 |  | Bulgaria | Czech Republic | 04. Concealed pipework | p.86 | Regulator’s assessment and conclusion on ageing management of concealed pipework for both nuclear power stations was presented. Additionally, as it was written, the In-service Inspection Programme was adjusted by the operator in 2016. There was no clear information about problems revealed for those pipework and how they had been resolved. Would you please give more information? | Website | The ISI programme wasn´t set properly to reveal, sufficiently in advance, any irregularities and defects caused by system operation in the way to prevent significant malfunciton of the system, mainly corrective maintenance was applied.
CZ-53 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | 79 | It is stated that the buried portions of ESW in the Dukovany NPP are currently replaced by new lines. What was the reason to replace lines? | expert group 5 | The replacement of lines was reactive action on pipe leakage. The break was a consequence of combination of support left in place during plant commisionning and mechanical loading caused by trucks. In 2014 a leak was found in piping having similar configuration like the buried portion of ESW. The first event resulted in outage of two units (plant can run with less than 200 % ESW backup for 24 hrs only). Since an excavation is always neceessary for any inspection of ESW piping in question and since the excavation is a major part of any BP repair, it was decided to replace 30 yrs old piping for brand new one having a potential of hassle free operation till plant deccomisioning.
CZ-54 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | 81 | The risk values A and C, involving intermediate risk values, should be elaborated. | expert group 5 | The risk values A-B-C are a representation of BPWORKS(tm) green-yellow-red scale. BPWORKS(tm) asigns color code to particular segment of pipeline on a basis of degradation likelihood and event consequences. For the purposes of AMP, the line score is equal to the score of its worst section. Numerical values of particular inputs and algorithm description are available for EPRI members only since those informations are EPRI know how.
CZ-55 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 77 | The report states that the condition of concealed service water pipes situated inside buildings is predicted on the basis of the knowledge of the condition of pipe sections accessible for inspection and the repair history. Are safety margins included into these predictions to account for possible specific degradation processes that may occur to unaccessible pipe sections because of their environment (e.g. water infiltrations, leaks from neighbouring pipes etc.)? | expert group 5 | Wast majority of service water piping located inside buildings is accesible, only minor sections are conceled usually when going through wall. All degradation mechanisms having an effect on these piping are initiated from inner surface of the pipe. There is no OpEx indicating an defradation from the outer surface. Since material and medium are same for both free and concealed sections of SW piping, the assumption on same degradation confirmed by AMR and no further degradation mechanism of non-accessible part of system was not revealed, additional safety margins for non-accessible piping are not considered.
CZ-56 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 77 | May the Czech Republic provide the AMP documents ČEZ_ME_1036 [94] and ČEZ_ME_1043 [95] | expert group 5 | Both documents were send to WS secretariat together with answer file. Unfortunatelly, both documents are in czech language only.
CZ-57 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 78 | Could the Czech Republic summarise the analysis of the 2014 event mentionned on page 78 and the experience learnt. | expert group 5 | The break was s a consequence of a support left in place during plant commisionning. Lesson Learned: 1) Even the very best AMP deals with known facts only. 2) There are always thinks not covered by blueprints and plant systems. 3) Do oportunistic inspections always when possible.
CZ-58 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 78 | May the Czech Republic indicate if its AMP include a weak signal data analysis? If yes, may the Czech Republic elaborate on this analysis. | expert group 5 | It is not clear what does "weak signal data analysis" mean but we think, that AMP does not include "weak signal data analysis".
CZ-59 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 78 | The report mentions the use of the EDMET method to determine the mean wall thickness for the sections measured. May the Czech Republic specify the precision reached by the method and the systematic and statistic uncertainties associated with the method? Is the method more dedicated to global or local corrosion? | expert group 5 | The method is dedicated to uniform corrosion. The method can find a wet surface, which is caused by damaged outer diameter coating. Measuring uncertainty is 4 %.
CZ-60 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 78-80 | It is stated in the report that ventilation system "could be considered as safety relevant". May the Czech Republic justify the absence of this system in the AMP for the LVR-15 research reactor? Does the Czech Republic plan to include the LVR-15 process ventilation system within the AMP for the LVR-15 reactor? | expert group 5 | The LVR-15 with power max power 10 MW is not obligated to have a gas-tight containment, it has only a hall with ventilation system with 4 main lines (from hot cells, from place below the vessel, from place under the lid and the hall itself). During 2011 the ventilation system was reconstructed (new monitoring system of gas releases, replacement of seals and closing flaps) plus till today continuos change of fans. In the new AMP due to new law requirements the system have to be set-up for monitoring and detection of the status of this SSC, selecting methods for testing and tracking; setting up the criteria of acceptability corrective measures
CZ-61 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 80 | The reports seems to indicate in page 80 that the EDMET method is able to measure precisely the length of an uninsulated pipe section or localise local defects in the pipe insulation. Could the Czech Republic clarify the capabilities of this method which was presented earlier in the report are a means to determine the mean wall thickness? Could the Czech Republic provide a report or article on this method and obtained results? | expert group 5 | EDMET is complex method and allows to find local defect of insulation by reflectometric methods TDR and TDP (except wall thickness). TDR - Time Domain Reflectometry, TDP -Time Domain Pulses.
CZ-62 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 83 | Soil resistivity / Aggressivity measurements are mentioned in the report. Soil properties are often subject to seasonal variation. Are these seasonal variations taken into account in a conservative way? | expert group 5 | Soil resisitivity is a factor affecting a design of piping. Once piping was commisioned and became a subject of AMP, there is no other utilization of soil measurement than checking whether there is no sudden change. Soil resistivities are replaced for conservative default value for winter and summer when using BPWORKS(tm) code. This replacement results in conservative values of outer diameter leak/break likelihoods, but so far the results are in agreement with OpEx.
CZ-63 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 83 | Could the Czech Republic specify if the loops with corrosion coupons mentioned in page 83 are relevant to all the pipelines covered by the AMP (ie. same steel type and grade, representative geometry, same transported fluid etc.)? | expert group 5 | These loops are parallel to ESW, NESW and tower water. Coupons are made from the same steel grade like piping of these systems.
CZ-64 |  | Concealed pipework expert group | Czech Republic | 04. Concealed pipework | P 84 | The report states that periodic inspections of the buried pipeworks of the LV-15 research reactor are not conducted and that inspections are performed during exposures caused for example by construction work. Taking into account the age of the installation could the Czech Republic justify its knowledge of the condition of the buried pipework of this installation? Could the number of inspections performed, their dates, and relevance with respect of the whole safety pipe system be provided? | expert group 5 | Buried pipes are designed so that even in the event of leakage there can be no leakage of activity to the environment (in the ventilation there is a vacuum so that it would leak from the environment and lower the vacuum in the hall, the secondary is pressurized against the primary so that even when the exchanger leak is not contaminated) plus the reactor has a sufficient primary heat capacity for removal of the residual heat, even in the event of a complete loss of power (natural circulation) or when the secondary flow is interrupted. Last inspections were performed during reconstruction of nearby buildings during 2011-2015. For secondary circuit a new investments are planned in 2018/2019 during which the heat exchangers and support pipes will be replaced.
CZ-65 |  | Finland | Czech Republic | 04. Concealed pipework | 86 | What are the corresponding safety and operation challenges, like maintaining safe shutdown condition, flooding risks, etc. connected to AMP? | Website | We consider the malfunction of UHS and/or flooding of some SSCs in case of large ESW pipe break as a challenge.
CZ-66 |  | Germany | Czech Republic | 04. Concealed pipework | 78 | The AMP for concealed pipework does not include piping inside buildings and channels. These pipes appear to be addressed only by walkdowns. As neither the outside nor the inside surface condition can be assessed by walkdowns, how will the degradation of this piping be determined? | email | An operational experience from lines in turbine hall (the same steel and medium) shows that major degradation mechanisms are uniform corrosion and pitting from ID. These lines are covered by AMP on Service Water Piping (measurements on accessible parts of pipelines with similar degradation mechanisms, materials and loads). The uniform corrosion is addressed by UTT under ISI program and by oportunistic UTT. The pitting is revealed by leak and adressed by corrective maintenance, which is cheap and fast inside buildings and channels. Walkdowns together with UTT measurement and corrective maintenance described above are fair measures to manage leaks.
CZ-67 |  | Germany | Czech Republic | 04. Concealed pipework | 82 | As described visual testing from the inner side is only carried out on the circulating cooling water in Dukovany. Are there any reasons not to carry out visual testing on other systems in Dukovany and also in Temelin? | email | The Dukovany ESW pipes have too small diameter (DN600) and no manholes, the Temelin ESW (DN800) is accesible in channels. These lines are covered by AMP on Service Water Piping (measurements on accessible parts of pipelines with similar degradation mechanisms, materials and loads). The uniform corrosion is addressed by UTT under ISI program and by oportunistic UTT of accessible pipes and replaced parts of concealed pipelines is instrumented by EDMET method. AMP covers also other systems with similar degradation mechanisms and materials.
CZ-68 |  | Germany | Czech Republic | 04. Concealed pipework | 83 | The periodic inspection of water corrosion parameters is carried out once a year in both plants. What kind of parameters are measured and what are the criteria for remedial actions? | email | These parameters are annual corrosion loss and Ryznar index adressing risk of fouling are the most important parameters. The criterions are minimal wall thinckness and there is no particular criterion for Ryznar index.
CZ-69 |  | Netherlands | Czech Republic | 04. Concealed pipework | p.78 | BPWORKS software is used to estimate the probability of corrosion of metallic pipelines. Are any provisions made to identify any unexpected degradation mechanisms (besides general corrosion) during monitoring, testing and inspection? | email | The measures addresing ageing effects (degradation mechanism results) are ISI program UTT in accessible places, oportunistic UTT, oportunistic VT and destructive testing during excavation works, flow test for fire water, aireal thermography, DCVG, tightness checks, EDMET, on-line acoustic measurements. All these methods does not address corrosion, in fact they adress wall thining/loss, regardless whether it is a result of corrosion or any other unexpected degradation mechanism. The Dukovany and Temelin OpEx is that wall thinning/loss is an effect of corrosion, but there is always an evaluation of degradation mechanism if something is found. Other source of information on unexpected degradation mechanism is OpEx sharing with Slovenske Elektrarne, WANO and within EPRI.
CZ-70 |  | Netherlands | Czech Republic | 04. Concealed pipework | p.80 | A new EDMET method is developed under R&D activities. Could you please elaborate in more detail the main results/advantages/experience with this method for diagnostics of concealed pipework? | email | Main results - assesment of the wall thickness, finding of local defect of insulation. Advantages - NDT, diagnostics in the working condition of pipes. Experience - ESW in NPP Dukovany.
CZ-71 |  | Netherlands | Czech Republic | 04. Concealed pipework | 4.1.1, p.79 | Since the operating conditions, pipe material and diameter as well as environment can influence the degradation mechanism, this information should be mentioned in the NAR. Could you please provide this information? | email | NPPs: Dukovany: Raw Water: CS, coal tar coating, DN1200, fresh river water, ambient temperature Temelin Raw Water: CS, coal tar coating, DN1600, fresh river water, ambient temperature Dukovany: Circ. Cooling Water: CS, coal tar coating or embeded in concrete, DN3200 to DN1800, fresh river water (cycles of conc.=2 to 3) Temelin: Circ. Cooling Water: CS, embeded in concrete, DN3400 to DN800, fresh river water (cycles of conc.=6) Dukovany: ESW: CS, coal tar coating or embeded in concrete, DN600, fresh river water (make-up for Circ. Cooling Water) Temelin: ESW: CS, embeded in concrete, DN800, fresh river water with NALCO biocide treatment Dukovany: NESW: CS, coal tar coating or embeded in concrete, DN530, fresh river water (cycles of conc.=2 to 3) Temelin: NESW: CS, embeded in concrete, DN800, fresh river water (cycles of conc.=6) For LVR-15 the description of the burried pipes of secondary circuit is on p.80.
CZ-72 |  | United Kingdom | Czech Republic | 04. Concealed pipework | 85 | Section 4.2.1 highlights the age of the AMP for concealed pipework. What is the basis for the continued confidence in the overall fleet position while the AMP develops? Is it based on a lack of evidence or lack of failures? | Website | The formal AMP origins in 2016, but the introduction of the formal program does not mean that no measures were in place. Wast majority of measures now evaluated within AMP was already used in the plants (fire water flow tests, UTT at accesible places, DCVG, BPWORKS(tm) since 2014, walkdowns, ...). These measures were evaluated by particular systems owners, now the systematic approach is used. The AMP will be continually improved on the basis of operational experience and world practice. The lack of failures also plays role.
CZ-73 |  | Bulgaria | Czech Republic | 05. Reactor Pressure Vessels | p. 109-110 | Information, related to regulator’s assessment and conclusions for the Ageing Management Programmes (AMP) of reactor pressure vessels for Dukovany and Temelin NPPs was presented. Would you please give more information about the strengths and weaknesses, if any, which had been identified at both stations and/or by regulator during reactor pressure vessels AMP realization? | Website | For both of the plant the surveillance programmes had to be modified. The changes in programme for Dukovany NPP is described in chapter 5.2.1, for Temelín NPP f.e. the thermal monitors had to be replaced by another type.
CZ-74 |  | Bulgaria | Czech Republic | 05. Reactor Pressure Vessels | p.102 | We could not find information related to the NDT (Not Destructive Testing) and its periodicy, methods used at NPP Temelin for VVER 1000 RPV and RPV specimens. Would you please share your experience on that matter? | Website | For NAR as the example the information about VVER 440 RPV was selected as it represents older design and it is in operation for longer time. The bases for ISI development were similar for both Czech NPPs, methods used and extend of the inspections performed are similar.
CZ-75 |  | EC | Czech Republic | 05. Reactor Pressure Vessels | Chapter 5.1.2.1, page 97 and 99 | IASCC is identified as a degradation mechanism in the reactor pressure vessel. This is true only for the RPV internals, which are outside of the Technical Specification of the Topical Peer Review. |  | Yes, IASCC should not be included. It is artifact from the beginning of the evaluation when it was performed for RVI too. The fluence level of RPV material is below threshold for IASCC initiation.
CZ-76 |  | EC | Czech Republic | 05. Reactor Pressure Vessels |  | No information is provided in the report on the possible presence of hydrogen flakes in RPV base material. How was this issue investigated for Dukovany and Temelin? |  | The part of the ISI Programme is regular volumetric inspection of circumferential region of base metal. The sensitivity of inspection used was evaluated with respect to the ability to detect hydrogen flakes and other types of surface parallel defects. More, the extended inspection of majority of base metal region were performed to exclude existence of hydrogen like flakes defects. Further, the technology of manufacturing was evaluated to assess potential for occurrence of hydrogen flakes. On the basis of analysis performed the possibility of hydrogen flakes like defects formation was excluded.
CZ-77 |  | Finland | Czech Republic | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Website | One of the big challenge is preparation for evaluation according to the new VERLIFE methodology that contains some new requirements. Also the recalculation of PTS analysis is now in progress that can bring some new challenges. For the future, maybe the licencee effort to reduct the excessive conservatisms in analysis by using the modern computation codes can be expected. Safe shutdown conditions is regulated by Limits and Conditions for Safe Operation. Compliance with LaC is one of the parameter evaluated anually as one of the parameter.
CZ-78 |  | Germany | Czech Republic | 05. Reactor Pressure Vessels | 102 | In the programme for monitoring operating parameters important to safety any unauthorised changes in operating parameters important to safety are periodically (once a year) evaluated with respect to their impact on ageing. What kind of unauthorised changes has happened so far in the plant? | email | The operational regimes are categorized into the three categories: normal, abnormal and accidental. Each deviation from normal operational conditions has beeen evaluated in frame of AMP from lifetime of the RPV point of view. There have not been any accidental operational regimes since beginning of the operation, only very limited number of abnormal regimes (2).
CZ-79 |  | Germany | Czech Republic | 05. Reactor Pressure Vessels | 103 | The outputs of maintenance are periodically evaluated in order to assess development of potential degradation mechanisms that have not yet been identified. Both preventive maintenance and random maintenance activities, if any, are reviewed. What is the goal and the kind of maintenance that is performed in a random manner? | email | Random maintenance is in proper term corrective maintenance, it means maintenance based upon non acceptable condition of the component. Its goal is to reestablish state of the component which is required for further operation. Especially for RPV this usually means removing objects from primary circuits, polishing of scratches …
CZ-80 |  | Germany | Czech Republic | 05. Reactor Pressure Vessels | 103 | Welds and base material of reactor pressure vessel in the Dukovany NPP are tested every four years, alternately from the outside and the inside. What are the scope and the applied technique of the base metal inspection? Are comparable inspections of base metal also performed in Temelin? | email | Inspections are performed from both external and internal surfaces. The basic method used is UT ultrasonic pulse-echo and TOFD. Further the inspections used are ET (cladding) and PT for nozzles welds. The same NDT methods are used at NPP Temelin.
CZ-81 |  | Germany | Czech Republic | 05. Reactor Pressure Vessels | 103 | Welds between the extension piece and the main circulation piping are inspected from the outside at an interval of 8 years and from the inside at an interval of 8 years. Are these inspections also performed alternately as at the vessel welds? | email | Yes. The same technology as for RPV is used .
CZ-82 |  | Netherlands | Czech Republic | 05. Reactor Pressure Vessels | Ch.5 | The information provided in this NAR in its chapter 5 on ageing management of reactor pressure vessels, is to a great extent qualitative. However in the Technical Specification for the NARs, the countries are requested to report in their NARs on the acceptance and action criteria for the various ageing phenomena. Apart from indicating those criteria, it is obvious that the NARs must discuss the compliance of the reactors with these criteria. Could you please provide this information? | email | NPPs: Generally criteria are developed on the basis of normative documentation of Czech Association of Mechanical Engineers. The ammount of analysis for developing acceptance criteria is above the scope of this report. These criteria are included in AMP of RPV, evaluated on time per year. This document was discussed with IAEA expert during LTO preparation and provided to the Czech regulator during licence renewal process as part of the Safety documentation. For LVR-15 based on research of SS vessels the criteria is (p-101): - total fluence on the vessel as a part of radiation embrittlement - the action is neuton fluence calculation and independent reviews; by the last review the total fluence will not significantly change vessel properties till at least 2028
CZ-83 |  | Poland | Czech Republic | 05. Reactor Pressure Vessels | 101, 107 | 1. What is the reason of corrosion horizontal channels and flange seals? 2. Does the decrease overpressure during pressure strength test concerns only RPV or others pressure equipments like SG? | Website | 1) The reason is based on fact that during reconstruction in 1987 -1989 the vessel was changed to stainless steel but the beam tubes remained aluminum, so the junction of these 2 metals can accelerate corrosion and the Al beam material as itself can degrade 2) decreasing of overpressure during pressure strength tests concerns also on other equipment - SG, MCP, pipings, valves...
CZ-84 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | p108 | Page 108, a yearly assessment of ageing management is performed through the evaluation of the individual ageing management parameters. What are those parameters and what are the normal and limit values defined for each parameter ? | expert group 2 | Aging management parameters are: Cumulative usage factor value, Tk temperature value, SCC occurrence indication (if any), Performance of ISI and Preventive maintenance according to approved plan, Technical aging parameter, Legislative aging parameter. TLAA parameter. Normal values are derived from national standards (Fatigue, TLAA), evaluation performed (Tka, TLAA) and as Boolean values. When parameter is equal or lower than normal value than no remedial action is needed in defined time period. The ammount of analysis for developing limit values is above the scope of this report. These criteria are included in AMP of RPV, evaluated on time per year
CZ-85 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | p97-98 | How often is the structural integrity of RPV’s assessed based on the periodic results of the surveillance program ? | expert group 2 | The evaluation of structural integrity is performed 1 time per year after each operation campaign on the basis of updated parameters, i.e. not only upon data from Surveillance specimen program but also upon data from fluence monitoring and evaluation, number of operational transients, results from ISI, maintenance and so on ...
CZ-86 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | p97-98 | could you provide the characteristics (pression, temperature) of the PTS event which helped defining the Tka. | expert group 2 | The more than 70 PTS scenarios were evaluated at the level of thermo hydraulic calculation. On the basis of TH result the 40 worst scenarios from point of P-T loading was evaluated to the level of structural integrity analysis.
CZ-87 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P99 | are loads due to seism taken into account ? | expert group 2 | At page 99 is list of identified degradation mechanisms and chapter about individual degradation mechanisms acceptance criteria establishment process. Seismic loading do not cause aging of the components, it is not degradation mechanism. Seismic topic is covered by other plant programmes separately from AM. Results from all plants programme are than gathered in health reports.
CZ-88 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P99 | Page 99, in fracture mechanical evaluation, is the shift of Tk due to strain ageing and thermal ageing taken into account as well as the shift of Tk under irradiation? | expert group 2 | Tk shift is evaluated according to normative documentation of Czech Association of Mechanical Engineers. The methodology for evaluation of VVER NPP components is based upon VERLIFE procedure. The VERLIFE (Guidelines for integrity and lifetime assessment of components and piping in VVER during operation) was elaborated under 5th and 6th EU Framework program. The evaluation of Tk shift is based upon experimental data from surveillance specimens program. The surveillance specimens are exposed to operational temperature and neutron flux during operation. The strain ageing does not have any influence in belt region of RPV.
CZ-89 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P99 and 106 | : Pages 99 and 106, what is the method (database, trend curves, codes and standards) used for the determination of Tka ? | expert group 2 | Normative documentation of Czech Association of Mechanical Engineers. The methodology for evaluation of VVER NPP components is based upon VERLIFE procedure. The VERLIFE (Guidelines for integrity and lifetime assessment of components and piping in VVER during operation) was elaborated under 5th and 6th EU Framework program.
CZ-90 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P107 | Page 107, do you use any of those mitigation’s methods to reduce the effect of radiation embrittlement : shieldings, thermal annealing ? | expert group 2 | The neutron flux is decreased by core shroud and core basket and by “burned” fuel assemblies which are positioned at border of the core – low leakage zone approach. The annealing methodology was elaborated and incorporated into Surveillance specimens program. Annealing procedure has not been used up till now. The quality of RPV material has been sufficient for safe operation.
CZ-91 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels |  | Do you make use of neutron absorber rods made with Hafnium, for instance, in the Czech reactors to decrease the neutron flux ? | expert group 2 | Hf elements are used for improvement of heat balance as part of fuel assemblies only.
CZ-92 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | page 98, In fracture mechanical evaluation, what are the dimensions of the postulated reference crack ? | expert group 2 | 13 mm (base material) + 1 mm (into cladding layer) or : according to qualification limit of used ISI inspection
CZ-93 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | page 98, In case of usage factors close or up to 1, are non-destructive examinations performed on certain parts of the RPV (studs, upper head penetrations) in order to check the absence of flaw which could be caused by low cycle fatigue, under the defence-in-depth approach ? Are those NDE qualified ? | expert group 2 | Yes, the UT and ET methods perforemd at RPV are qualified.
CZ-94 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels |  | Do you make use of a transient bookkeeping to identify the number of cycles ? | expert group 2 | Yes. Complete operational history is archived in LTOs database.
CZ-95 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | Stress corrosion cracking is assessed once a year for some components (pressure vessel liner, vessel upper head liner, vessel head nozzle shrouds, relevant parts of the flange). What is the method of assessment ? Are there any ISI ? | expert group 2 | Selected parts of the SCs are inspected by VT, PT method every year and further by ET, UT, inspection method during longer intervals according to their susceptibility to development of SCC. They are performed in frame of ISI.
CZ-96 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | do you consider that BMI nozzles, upper head penetrations, reactor vessel radial keys, claddings, repaired parts with alloy 182 and/or dissimilar metal welds concerned by PWSCC ? | expert group 2 | There is no alloy 182 used in VVER 440 RPV, no BMI nozzles. The only parts that are in contact with PW medium are austenitic cladding and austenitic welds. Those materials are considered non sensitive to SCC under operational condition of RPV and under defined PW controlled chemistry. The part of ISI are NDT of material in contact with medium.
CZ-97 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | Are there any guidelines defined for the water chemistry ? | expert group 2 | Yes. AMP Water chemistry
CZ-98 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels |  | Were head and bottom penetrations and dissimilar metal welds stress-relieved during the manufacturing ? | expert group 2 | There are no bottom installed penetrations in VVER reactors. There are no dissimilar welds with exception of interface of cladding & basic metal of RPV. The welding of the austenitic cladding was performed according to approved technical documentation. Part of the process is annealing procedure after welding (stress relieved).
CZ-99 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels |  | The NAR doesn’t deal with underclad defects in RPV shells or in nozzles. Do you consider there is no risk ? Do you perform any in-service inspection to assure the absence of underclad defects, under the defence-in-depth approach ? | expert group 2 | Parts of the ISI program are inspections focused on identification of possible underclad defects (UT, TOFD). Existing underclad defects are monitored and evaluated with respect to possible risk of their growth.
CZ-100 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels |  | How is the effect of thermal ageing taken into account in RPV beltline and on other components than RPV beltline region and specially what is the impact of a flaw outside the beltline region ? | expert group 2 | Thermal aging is evaluated with help of surveillance specimens. But it is necessary to emphasize that it is not possible to get information about the future state of the material with respect to the thermal aging but only information about current state of the material because there is not any acceleration factor for thermal aging possible in reactor. Nevertheless the procedure and limit value of Tk shifts due to temperature aging for RPV steels is defined in the methodology for evaluation of resistance against fast fracture in normative documentation of Czech Association of Mechanical Engineers. That methodology is based upon VERLIFE - Guidelines for Integrity and Lifetime Assessment of Components and Piping in VVER during Operation) and was elaborated and published under 5th and 6th EU Framework program of EC. The Tk shift due to temperature aging for RPV steel of VVER 440 (15CHMFA(A)) is 0°C for time of operation longer than 100 000 hours. This is in agreement with results from surveillance specimens program; test performed by manufacturer of RPV Skoda JS and other information resources in literature.
CZ-101 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels |  | Have you ever need to pre-heat the injection security water to reduce the severity of thermal shocks ? | expert group 2 | Yes, preheating of highpressure tanks of emergency cooling water was introduced. The preheating of lowpressure tanks of emergency cooling water is one of the possible remedial actions planned in case that embrittlement of RPV material exceeds current operational limit.
CZ-102 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels |  | Did you perform any ISI to assure the absence of hydrogen flakes in RPV shells after the Belgian REX ? | expert group 2 | The part of the ISI Programme is regular volumetric inspection of circumferential region of base metal. The sensitivity of inspection used was evaluated with respect to the ability to detect hydrogen flakes and other types of surface parallel defects . More, the extended inspection of majority of base metal region were performed to exclude existence of hydrogen like flakes defects. Further, the technology of manufacturing was evaluated to assess potential for occurrence of hydrogen flakes. On the basis of analysis performed the possibility of hydrogen flakes like defects formation was excluded.
CZ-103 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P91 | - Page 91: What are the operating conditions, including pressure, hot and cold leg temperatures, during reactor operation? If available, upper dome coolant temperature should be provided since it is related to thermal aging of closure head. | expert group 2 | Temperature / pressure parameters in RPV and primary circuit are monitored and archived. Exact values are: 267/296 C, 12.25 Mpa, temperature of the water in the core 310 C.
CZ-104 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P91 | - Page 91: Underclad defects have been observed in several other RPVs in the past. Does the AMP include provisions for inspection and identification of (if any) underclad defects? | expert group 2 | Parts of the ISI program are inspections focused on identification of possible underclad defects (UT - TOFD). Existing underclad defects are monitored and evaluated with respect to possible risk of their growth.
CZ-105 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P91 | - Page 91: Are there any provisions for evaluation of atmospheric corrosion on the outside surface of dissimilar welds? | expert group 2 | The atmospheric corrosion in environment of NPP Dukovany (inner space of buildings) is negligible and it is not considered as potential degradation mechanisms. Nevertheless the external surface of RPV, safe ends and connected piping including weld is checked during preparation of NDT.
CZ-106 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P96 | - Page 96: Have any of the RPV closure heads been replaced? | expert group 2 | No. No reason for that.
CZ-107 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | - Page 98: What is closure head temperature? If temperature is higher than 300oC, has thermal aging been assessed for closure head? | expert group 2 | Operating temperature in the hot leg of primary circuit is 296°C (measured). The maximal water temperature measured in the channels of the core is 310°C so we do not expect the temperature of the upper head material to by higher than 300°C. The temerature aging is not taken as issue, it has not been assessed. The general world experience is monitored.
CZ-108 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | - Page 98: Does the evaluation of thermal aging take into account the Ph content of the RPV? | expert group 2 | The thermal aging is evaluated with help of surveillance specimen according normative documentation of Czech Association of Mechanical Engineers. Thermal aging is evaluated with help of surveillance specimens. Thus, the evaluation of thermal aging take into account the Ph content of the RPV. But it is necessary to emphasize that it is not possible to get information about the future state of the material with respect to the thermal aging but only information about current state of the material because there is not any acceleration factor for thermal aging possible in reactor. Nevertheless the procedure and limit value of Tk shifts due to temperature aging for RPV steels is defined in the methodology for evaluation of resistance against fast fracture in normative documentation of Czech Association of Mechanical Engineers. That methodology is based upon VERLIFE - Guidelines for Integrity and Lifetime Assessment of Components and Piping in VVER during Operation) and was elaborated and published under 5th and 6th EU Framework program of EC. The Tk shift due to temperature aging for RPV steel of VVER 440 (15CHMFA(A)) is 0°C for time of operation longer than 100 000 hours. This is in agreement with results from surveillance specimens program; test performed by manufacturer of RPV Skoda JS and other information resources in literature.
CZ-109 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | - Page 98: Are there any provisions, e.g., monitoring or inspection, for reducing moisture retention under insulation? | expert group 2 | Thermal aging is evaluated with help of surveillance specimens. Thus, the evaluation of thermal aging take into account the Ph content of the RPV. But it is necessary to emphasize that it is not possible to get information about the future state of the material with respect to the thermal aging but only information about current state of the material because there is not any acceleration factor for thermal aging possible in reactor.
CZ-110 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | - Page 98: It mentioned that changes in Tk are assessed once a year. What is the process for this evaluation? Is it based only on surveillance specimens or models, or both? Please provide more details on irradiation and thermal aging models used for evaluations. | expert group 2 | Nevertheless the procedure and limit value of Tk shifts due to temperature aging for RPV steels is defined in the methodology for evaluation of resistance against fast fracture in normative documentation of Czech Association of Mechanical Engineers. That methodology is based upon VERLIFE - Guidelines for Integrity and Lifetime Assessment of Components and Piping in VVER during Operation) and was elaborated and published under 5th and 6th EU Framework program of EC.
CZ-111 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | - Page 98: What is the low-cycle fatigue usage factor for each component? | expert group 2 | The Tk shift due to temperature aging for RPV steel of VVER 440 (15CHMFA(A)) is 0°C for time of operation longer than 100 000 hours.
CZ-112 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | - Page 98: Does the fatigue analysis take into account the presence of any defects, e.g., underclad defects? | expert group 2 | This is in agreement with results from surveillance specimens program; test performed by manufacturer of RPV Skoda JS and other information resources in literature.
CZ-113 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | - Page 98: “Stress corrosion cracking”. Are BMI and CRDM penetrations susceptible to SCC? | expert group 2 | There are no bottom mounted instrumentation. The CRDM penetrations that are in contact with medium are manufactured from austenitic materials including welds but due to design (stress concentration, geometry…) they could potentially have higher probability of SCC development. Those regions are included in ISI: VT and PT inspection.
CZ-114 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P98 | - Page 98: It is stated that “corrosion development is unlikely”. Please provide definition for “unlikely” and the basis for this given that corrosion has been observed in other RPVs in the past. | expert group 2 | All parts of RPV including nozzles which are in contact with primary medium are made from austenitic cladding or from austenitic titanium stabilized stainless steel. There was performed extensive research concerning those steels to assess their corrosion resistance under condition of primary circuit medium which confirmed expected corrosion resistance. As corrosion is stochastic process the wording “corrosion is not possible” was not used, instead the wording “corrosion is unlikely“ was used. Under the condition of primary water we have never encountered corrosion of RPV materials that is in contact with medium during operation.
CZ-115 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P99 | - Page 99: “The following degradation mechanisms affect specific RPV components”. Which aging mechanisms affect nozzles, CRDM, BMI, studs? | expert group 2 | There are no BMI. Nozzles: Fatigue: wear, potentially SCC. CRDM: fatigue, wear. Studs: fatigue, wear, loss of preload.
CZ-116 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P99 | - Page 99: “The assessment of critical regimes was updated between 2007 and 2008”. Which are the “critical regimes”? | expert group 2 | The critical regimes were LOCA H200 and P13, that is loss-of-coolant accident (LOCA) with leakage through a partial break D200 and Main Steam Header Break outside the Containment respective.
CZ-117 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P99 | - Page 99: “IASCC”. There is limited information on IASCC in section 5. How is this aging mechanism affecting the RPV? | expert group 2 | Yes, IASCC should not be included. It is artifact from the beginning of the evaluation when it was performed for RVI too. The fluence level of RPV material is below threshold for IASCC initiation.
CZ-118 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P103 | - Page 103: What type of inspections cover CRDM and BMI points? | expert group 2 | There are no BMI. The inspections of CRDM used are VT and TV (part of ISI).
CZ-119 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P103 | - Page 103: What is the area coverage for ultrasonic and eddy-current testing? | expert group 2 | ET: cladding, welds and basic metal from internal and external surfaces, radiuses of the nozzles, thread bolts, thread nests (M140) UT: cladding, welds, nozzles and basic metal from both sides, thread bolts.
CZ-120 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P103 | - Page 103: “…selected inspection points…”. Which are these “selected inspection points” and how are they selected? | expert group 2 | In the scope of ISI are parts of the RPV important for its required function and where is possible to expect initiation and development of the material degradation.The results of ISI are evaluated one time a year and ISI perofmance plan for each outage is approved by Czech regulator. The original ISI was based upon recommendation and requirements of the manufacturer, updates are performed with regards to the AMP of RPV (including experience from operation of NPP Dukovany, experience of others operators and with regards to the state of art of nuclear industry).
CZ-121 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P104 | - Page 104: What is the maximum years of operation simulated by the available surveillance specimens? | expert group 2 | The timeschedule of the Surveillance specimens program is designed and updated to provide information for assumed LTO period (consideration of 60 years of operation).
CZ-122 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P104 | - Page 104: Are the specimens taken during RPV manufacturing or were manufactured separately? | expert group 2 | The surveillance specimens were taken during RPV manufacturing.
CZ-123 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P106 | - Page 106: Is water chemistry monitoring part of preventive actions to reduce degradation due to corrosion? | expert group 2 | Yes. This is covered by AMP Water chemistry.
CZ-124 |  | RPV expert group | Czech Republic | 05. Reactor Pressure Vessels | P108 | Page 108: “…fatigue damage has been identified…”. Could you provide more details on the severity of the damage and how this was addressed? | expert group 2 | Fatigue damage was identified by means of calculation method based upon real operational parameters and history (CUF) No fatigue damage of the material (crack) has been found up till now.
CZ-125 |  | Bulgaria | Czech Republic | 07. Concrete containment structures | chapter 7.1.2 | In conjunction with chapter 7.1.2 ASSESSMENT OF REINFORCED CONCRETE CONTAINMENT, please, clarify the acceptance criteria related to the different ageing mechanisms. | Website | ČEZ: Generally, the acceptance criteria are derived from amount, rate, and extent of damage which degradation mechanism caused. It must be taken into account whether the degradation does have the impact on intended structure/component function. For example, for degradation caused by seepage of undeground water and leaching we used the amount of area which is affected (for example, criterion 20 % of affected area requires detailed survey), the colour of leachate, whether the construction is mostly wet or dry. For prestressed containment the limit for minimal prestressing force is set. Also the minimum compresive strenght of concrete is set. The crucial thing is to assess progress of the indications over the time. The effects of degradation must be assessed in a comprehensive way, taking into account the possible coincidence of more degradation mechanisms and the required function of the component and location of the failure. For this reason, the indications found are assesed by team of facility manager, ageing management specialist and the supervisor (chartered engineer is taking part), so the expertise is ensured. The decision on the acceptability of the defect found is within the competence of the team mentioned above as well as the proposed corrective measures. The LVR-15 is not obligated to have a reinforced concrete containment - it has only a ventilated confinement (reactor hall). For the reactor hall the acceptability criterion is the stability of the object which is periodically checked visually and by means of a print of possible cracks and evaluation by an external experts on structural statics and dynamics
CZ-126 |  | Bulgaria | Czech Republic | 07. Concrete containment structures | chapter 7.1.4 | In conjunction with chapter 7.1.4 PREVENTIVE AND CORRECTIVE ACTIONS FOR CONCRETE STRUCTURES OF THE CONTAINMENT, please, clarify the criteria and procedures for taking actions. | Website | ČEZ: Generally, the acceptance criteria are derived from amount, rate, and extent of damage which degradation mechanism caused. It must be taken into account whether the degradation does have the impact on intended structure/component function. For example, for degradation caused by seepage of undeground water and leaching we used the amount of area which is affected (for example, criterion 20 % of affected area requires detailed survey), the colour of leachate, whether the construction is mostly wet or dry. For prestressed containment the limit for minimal prestressing force is set. Also the minimum compresive strenght of concrete is set. The crucial thing is to assess progress of the indications over the time. The effects of degradation must be assessed in a comprehensive way, taking into account the possible coincidence of more degradation mechanisms and the required function of the component and location of the failure. For this reason, the indications found are assesed by team of facility manager, ageing management specialist and the supervisor (chartered engineer is taking part), so the expertise is ensured. The decision on the acceptability of the defect found is within the competence of the team mentioned above as well as the proposed corrective measures. For LVR-15 the purpose of action is to ensure the stability of the object - preventative action is monitoring the stability of the building and correction based on follow-up recommendations based on monitoring result.
CZ-127 |  | Bulgaria | Czech Republic | 07. Concrete containment structures | p.112 | In “07. Concrete containment structures” were explained different ageing mechanisms for civil structures and the respective control methods. However, in the text was missing information concerning the acceptance criteria for each of the possible ageing mechanisms and what were the corrective measures for not fulfillment those acceptance criteria. Would you please clarify? | Website | The effects of degradation must be assessed in a comprehensive way, taking into account the possible conjunction of more degradation mechanisms and the required function of the component and location of the failure. For this reason, the indications found are assesed by team of facility manager, ageing management specialist and the supervisor (chartered engineer is taking part), so the expertise is ensured. The decision on the acceptability of the defect found is within the competence of the team mentioned above as well as the proposed corrective measures.
CZ-128 |  | Concrete containment PCPV expert group | Czech Republic | 07. Concrete containment structures | par 7.1.2. | Specify which part of the RD programs is managed by Licensee and which from Industry or other relevant bodies | expert group 4 | All RaD programmes listed in NAR are managed by licencee, who define the task assignment. Contractors are listed below. Institute of Nuclear Research Řež: - Research programme - Boric acid influence on the concrete (Dukovany) - Moisture monitoring of reinforced concrete of internal structures of containment - Laboratory corrosion resistance testing for concrete and reinforcement in water solutions of boric acid (Temelín) Technical University Brno: - Long-term monitoring of load-bearing structural concretes around the Dukovany NPP reactor cavity - Evaluation of the measurements carried out during integrity verification test of Dukovany NPP Unit 1
CZ-129 |  | Concrete containment PCPV expert group | Czech Republic | 07. Concrete containment structures | par. 7.1.3 | It is not clear if there are “third part certification organization”, during the monitoring, testing, sampling and inspection. Please clarify | expert group 4 | We don´t understand the right definition of "third party certification organization" and what should be its purpose. We asked on it to WENRA RHWG and didn´t received the answer. However, monitoring, testing, sampling and inspection is made by licensee in close cooperation with suppliers. E.g. Technical university Brno, Institute of Nuclear Research Řež, VÚEZ Levice, and so on, as geodesic office, laboratories for concrete testing or underground water testing. Institute of Nuclear Research Řež is also used for technical consultations as a general supervisor or technical support organization.
CZ-130 |  | Concrete containment PCPV expert group | Czech Republic | 07. Concrete containment structures | par 7.1.3 | In the paraghrap 7.1.3, the point a and b of the WENRA TS are sometimes reported and correct (Description of activities and frequencies), the point c is almost missing (acceptance criteria). Please enhance the information | expert group 4 | Generally, the acceptance criteria are derived from amount, rate, and extent of damage which degradation mechanism caused. It must be taken into account whether the degradation does have the impact on intended structure/component function. For example, for degradation caused by seepage of undeground water and leaching we used the amount of area which is affected (for example, criterion 20 % of affected area requires detailed survey), the colour of leachate, whether the construction is mostly wet or dry. For prestressed containment the limit for minimal prestressing force is set. Also the minimum compresive strenght of concrete is set. The crucial thing is to assess progress of the indications over the time. The effects of degradation must be assessed in a comprehensive way, taking into account the possible coincidence of more degradation mechanisms and the required function of the component and location of the failure. For this reason, the indications found are assesed by team of facility manager, ageing management specialist and the supervisor (chartered engineer is taking part), so the expertise is ensured. The decision on the acceptability of the defect found is within the competence of the team mentioned above as well as the proposed corrective measures.
CZ-131 |  | Concrete containment PCPV expert group | Czech Republic | 07. Concrete containment structures | par 7.1.3 | The NAR does not explain how the first 5 point of page 28 of the WENRA TS are used. Please clarify | expert group 4 | The general principles are described in chapter 2 and are valid for all technical topics. Outputs from AMP and other relevant programmes are used as inputs to anual assessment of containment which is agreed by expert comitee. Trends and potential progressive deterioration are evaluated in health reports. Remedial measures (for ex. changes of testing interval etc) are stated overthere.
CZ-132 |  | EC | Czech Republic | 07. Concrete containment structures | 119 | A short section on procedures for identification of degradation mechanisms is provided at the bottom of p119 relating to Dukovany NPP. A similar section would have been expected for Temelin NPP. Is Temelin using the same approach? |  | Temelin uses the same approach. The report was compiled from parts which were elaborated by various specialists. An error has occurred. The paragraph applies to both power plants, which is not mentioned in the heading.
CZ-133 |  | EC | Czech Republic | 07. Concrete containment structures | 121 | Reference to IAEA-TECDOC-1025. It seems that this publication has been superseded by IAEA NP-T-3.5. What is the process for the identification of the latest versions of standards or new standards after their release and what is the process and timescale for their introduction into the ageing assessment and management programmes? |  | IAEA NP-T-3.5 was took into account in 2016 when the Ageing Management Review within the licencing process for Dukovany unit 3 and 4 LTO have been elaborated. It will be also take into account in Ageing Management Programmes revision, which is usally made in 5 years period.
CZ-134 |  | EC | Czech Republic | 07. Concrete containment structures | 130 | Starting on page 130, a detailed list of tests and inspections carried out at Temelin NPP is provided. However, unlike the corresponding list provided for Dukovany NPP starting on page 126, no information is provided related to the frequency of the tests and inspections carried out at Temelin. |  | Most inspections are carried out once a year. Prestressing and temperature is measured by embedded systems once a month. In the six-year period it is carried out: - measuring the thickness of the liner - check for mechanical damage on the removed pretensioning cable - control of preservative vaseline - moisture control under the anchors housings - geodetic measurement of structural deformations - tensile control by prestressing hydraulic jack.
CZ-135 |  | EC | Czech Republic | 07. Concrete containment structures | 131 | Under the point 'Reinforced concrete testing (carried out ...without sampling)' three types of test are mentioned. Please could you provide some further details on the nature of these tests, how they are carried out and their frequency. |  | Concrete strength by schmidt test hammer is made once a year. The depth of carbonation of concrete is occasionally tested during construction work on the containment - eg. drilling for technology fastening. Concrete carbonation with XRF and XRD analysis is made once per 10 years. Corrosion of reinforcement is unlikely when carbonatation does not reach the depth of reinforcement.
CZ-136 |  | EC | Czech Republic | 07. Concrete containment structures | 122 - 124 | Degradation mechanisms: Starting on page 122 there is a rather complete list of potential degradation mechanisms relevant for the ageing management of the concrete containment structures. At the bottom of page 123, degradation mechanisms specifically addressed under AMPs for containments are listed. This list is considerably reduced compared to the list mentioned above, but it is not quite clear what it represents. For example, settlement is missing (it is also not mentioned in the list of inspections in section 7.1.3.1), although it is clear that settlement is considered because there are specific AMPs for settlement (p117, 119). As another example, carbonation is not mentioned in the list at the bottom of page 123 but it is monitored, as mentioned e.g. in section 7.1.3.1 on p 131. Please can you clarify. |  | Degradation mechanisms specifically addressed under the AMPs for containments are not the reduction of the previous (rather complete) list, but on the contrary, their extension. For containment both lists are relevant. For "common" buildings, the first list only. The first list is used for all buildings under the scope of Ageing Management Program (AMP Monitoring of Buildings). The second list listed further degradation mechanisms relevant for containment which are specifically addressed under the AMP for containments.
CZ-137 |  | EC | Czech Republic | 07. Concrete containment structures | 123, 124 | Little or no information is provided on the acceptance criteria for the identified degradation mechanisms or for the listed inspections in section 7.1.3. |  | ČEZ: Generally, the acceptance criteria are derived from amount, rate, and extent of damage which degradation mechanism caused. It must be taken into account whether the degradation does have the impact on intended structure/component function. For example, for degradation caused by seepage of undeground water and leaching we used the amount of area which is affected (for example, criterion 20 % of affected area requires detailed survey), the colour of leachate, whether the construction is mostly wet or dry. For prestressed containment the limit for minimal prestressing force is set. Also the minimum compresive strenght of concrete is set. The crucial thing is to assess progress of the indications over the time. The effects of degradation must be assessed in a comprehensive way, taking into account the possible coincidence of more degradation mechanisms and the required function of the component and location of the failure. For this reason, the indications found are assesed by team of facility manager, ageing management specialist and the supervisor (chartered engineer is taking part), so the expertise is ensured. The decision on the acceptability of the defect found is within the competence of the team mentioned above as well as the proposed corrective measures.
CZ-138 |  | EC | Czech Republic | 07. Concrete containment structures | General | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | The parts which are not accessible for inspection are not directly included in AMP. Outputs of AMP of accessible parts are relevant and used for evaluation of inacessible parts (the same materials, loads, degradation mechanism etc. are considered). Also internal and external operating experience is used. If there would be any degradation which could affect their ability to perform their required functions there should be some evidence of this degradation, for example deterioration of containment tightness or defects on adjacent structures. Consequently, the attention is paid to these indirect phenomena.
CZ-139 |  | Finland | Czech Republic | 07. Concrete containment structures | 112 - 120 | Concerning the Temelín NPP, is it possible to measure all tendons or only certain rep-resentative tendons? If only representative tendons are measured, how are they selected? | Website | All tendons are measured on monthly basis. All anchors are equipped with the strain gauges.
CZ-140 |  | Germany | Czech Republic | 07. Concrete containment structures | 137 | According to chapter 7.1 the AMP for Containment in the Dukovany NPP includes among others: “Hermetic steel liners”. In sub-chapter 7.2.1 is stated that from 2017, steel hermetic liner thickness will be measured with the use of the phased array ultrasonic method. Thus the results of these measurements could not be included in the report considered. However, in sub-chapter 7.2.1 it is indicated that the results of the assessment show that no limit value for the monitored parameters is exceeded. Which other results than from ultrasonic method have been taken into account when concluding in the assessment that no limit value is exceeded? | email | Results from - Overall leakage from the hermetic zone during periodic integral tightness testing - Leakage from the hermetic zone during tightness test through the drainage system of controlled leakage from the spent fuel pool - Local tightness tests of hermetic hatches, closures and doors at the boundary and within the hermetic zone area - Concrete temperature of the reactor shaft - Deformation of the roof and wall of the bubblercondenser tower during tightness test - Long-term monitoring of potential radiation effects on the concrete have been taken into account. None of above mentioned methods indicated any exceeding of limits.
CZ-141 |  | Germany | Czech Republic | 07. Concrete containment structures | 139 | It is stated: “The results of non-destructive testing showed that compressive strength of concrete meets the requirement for the minimum guaranteed compressive strength of concrete of the concrete class used”. It is known that up to now none of the non-destructive test (NDT) methods for evaluation of compressive strength of thick walled concrete structures can be considered as reliable with regard to results, see for example “Proceedings OECD/NEA WGIAGE Workshop on the Non-destructive Evaluation of Thick-walled Concrete Structures” (Prague, Czech Republic; 17-19 September 2013). The different NDT methods together with the deep analysis (incl. probabilistic one) should be applied for reliable evaluation. Which NDT method and complementary analyses have been used for the assessment? | email | The non destructive test use the Schmidt test hammer. It is based on Czech technical standard ČSN 73 1373 "Non-destructive testing of concrete - Determination of compressive strength by hardness testing methods". Further specification and adjustment of the calibration relationship (between schmidt test and compressive strength) was carried out in cooperation with Technical university in Brno. Also destructive tests on concrete specimens have been used by Technical university for this task.
CZ-142 |  | Germany | Czech Republic | 07. Concrete containment structures | 141 | In sub-chapter 7.2.1 the AMP for Civil Structures Parts of Pools with Double Liner in the Temelín NPP considers among others visual inspection of austenitic pool liner. It is stated that the measured thickness of austenitic steel liner ranges from 95% to 100% of the design thickness. The acceptance criterion itself is not given in the report. It is concluded: “The pools with double lining in the Temelín NPP Unit 1 and Unit 2 can be considered operable on a long-term basis. The structure meets the assumptions for safe operation of the NPP in the next period”. Can Czech Republic provide the acceptance criterion for the thickness of austenitic steel liner? | email | Nominal thickness is 6mm. Acceptance criterion is 5,4mm (90% of nominal).
CZ-143 |  | Germany | Czech Republic | 07. Concrete containment structures | 126 | It is stated that the leakage from the hermetic zone during tightness test through the drainage of controlled leakage system from the spent fuel pool and refuelling pool was measured. Afterward it is stated that the proportion of leakage through the part of inac-cessible hermetic liner in the overall leakage of hermetic zone is determined. This is only one place in the whole report where the inaccessible area is mentioned. Are there no other inaccessible areas, neither in Temelin NPP nor in Dukovany NPP, which might be considered in the AMP? | email | The parts which are not accessible for inspection are not directly included in AMP. Outputs of AMP of accessible parts are relevant and used for evaluation of inacessible parts (the same materials, loads, degradation mechanism etc. are considered). Also internal and external operating experience is used. If there would be any degradation which could affect their ability to perform their required functions there should be some evidence of this degradation, for example deterioration of containment tightness or defects on adjacent structures. Consequently, the attention is paid to these indirect phenomena.
CZ-144 |  | Netherlands | Czech Republic | 07. Concrete containment structures | 7.1.2 | Is the pretensioning monitored continuously throughout the year by sensors or is monitoring conducted periodically? | email | Strain gauges are installed on all anchors. Data is read and evaluated once a month.
CZ-145 |  | Netherlands | Czech Republic | 07. Concrete containment structures | 7.1.3 | Is the drainage system of the spent fuel storage pool monitored for clogging due to the presence of boric acid in water and associated corrosion effects? And is the effect of seepage of water to the concrete below assessed? | email | Temelín: The test of tube patency is carried out with pressure air. If there is suspicion on clogging, endoscopy is used. Dukovany: The amount of water is monitored and chemical analyses are made from each section and air flowrate during the containment leakage test is measured. Based on these facts we assume the tubes are not clogged. The effect of potential seepage of boric acid water into concrete is subject of RaD programmes driven by CEZ and its suppliers and also EPRI (e.g. Product Id: 1025166). Current results show, that concrete has huge neutralization capacity and the degradation is slow and should not be crucial issue. Of course, it depends on many circumstances (width of cracks, velocity of flow, aerated vs. nonaerated environment...) and it should be subject of monitoring and RaD programmes.
CZ-146 |  | United Kingdom | Czech Republic | 07. Concrete containment structures | 140 | Section 7.1.2 considers the ageing mechanisms applying to concrete containments. This section should include for waterstops, seals and gaskets but consideration of these SSCs is not given in this section. Please confirm the types of seals included in the AMP, together with their ageing mechanisms and acceptance criteria. | Website | Waterstops, seals and gaskets against underground water are generally inaccessible. Their condition is judged from the state of the adjacent structures. The symptoms of leakage into the structure are checked. Waterstops, seals and gaskets against atmospheric precipitation are generally visible and are checked by occasional walkaround checks. Also the symptoms of leakage into the structure are checked.
CZ-147 |  | United Kingdom | Czech Republic | 07. Concrete containment structures | General | The report makes reference at various sections to research studies in relation to the effect of boric acid on concrete. This is an area of common interest to PWR operators. Please provide more information on the scope of these studies. | Website | The scope is similar as for example in "2012 Technical Report, EPRI, Welding and Repair Technology Center: Boric Acid Attack of Concrete and Reinforcing Steel in PWR Fuel Handling Buildings". We are interested about changes in pH, carbonatation, corosion of concrete and reinforcing steel, changes in weight of specimens, decrease of strength. We made specimens with respect to original concrete recepture for each power plant. We use boric acid water with continously keep concentration 12g/l as most agressive environment for one set of specimens. The second set of specimens is submerged in boric acid water 12g/l which is restore once a year (to original concentration 12g/l). The third, control set is maintained in 100% water humidity air.
ES-1 |  | Bulgaria | Spain | 09. Overall assessment and general conclusions | p. 166 | On page 166 of the report is written that the effectiveness of AMP is measured by quantitative and qualitative indicators. Would you provide some examples of used quantitative and qualitative indicators? | Website | For each Ageing Management Program an "AMP tracking report" is periodically issued. This "AMP tracking report" summarizes the results of AMP activities and includes the AMP effectiveness indicator that assesses its effectiveness taking into account the three following aspects: 1) Activities results: If all foreseen activities have been performed and no significant ageing effects have been detected, the maximum indicator value is achieved, otherwise postponed activities and/or detected ageing effects will reduce the indicator value. 2) Operating Experience: Any internal or external experience affecting the AMP results and was not previously taken into account, could reduce the indicator value. 3) Commitments: When the implementation of an enhancement proposal or other commitment that affects the AMP is delayed, the indicator value is reduced. The indicator trend is also evaluated every year. Almaraz and Trillo NPPs measure AMP effectiveness on a qualitative basis, considering if the AMP is detecting the ageing mechanisms and effects before the loss of intended function.
ES-2 |  | United Kingdom | Spain | 03. Electrical cables | 55 | Section 03.11 states that cable jackets and shielding serve only to protect the insulation, as a result of which they do not participate in the intended function of the cable and do not require this process of AMR. Section 03.1.3 explains that visual inspections of cable jackets are undertaken. Please expalin the apparent consistency betweem these aections and clarify whether cable jackets are inspected as part of the AMR | Website | There is not any inconsitency. Many references (Eg: EPRI 1013475) states clearly that, cable jackets are used to protect the isulation, and, for most cases their ageing have not significant effects on the normal ageing process of the primary cables insulation. For the accesible cables, the required visual inspections, and mechanical tests (Indenter method) have to be performed in the jacket. Visual inspection only can be applied directly on insulation in the cable ends sections when jacket has been eliminated. For most cables, jackets are built with materials that age faster than the insulation material so, if jacket is not degraded, we can consider that insulation is in good conditions. On the other hand, the results of Indenter tests performed over the jackets are correlated with the corresponding values in the insulation.
ES-3 |  | United Kingdom | Spain | 03. Electrical cables | 57 | Section 03.11 states that thermographic cameras are normalised to detect hot spots in cables and connections located close to high temperature sources or piping. Section 03.1.3. explains the means by which visual and tactile inspection is undertaken, but doesn't include a thermographic camera. Please confirm if thermographic cameras are used to assist visual and tactile cable inspections. | Website | Some Spanish plants have performed walkdowns on cable routings, to search for hot- spots location. In those walkdowns thermographic cameras have been used only for identification of thermal hot spots. The walkdowns results are used to select the cables in worst environmental conditions, that are consequently included in the sample of cables to be visually inspected. Themographic cameras are not used to assisst the visual and tactile inspection activities
ES-4 |  | Finland | Spain | 03. Electrical cables | 55-61 | Report does not clearly indicate if there are cables which have performance requirements in case of accident conditions. If there are such cables how this is considered in the AMP? | Website | Cables that must function under accident conditions (EQ cables) are identified in the Plant "Environmental Qualification Program Report". Ageing of these cables is primarily assessed, inside EQ program, managing their qualified life. Additionally, and as a consequence of CSN recommendations, (see page 59 of NAR) EQ cables have been included by Spanish Plants in the scope of their cable AMP-1 and AMP-2 (See pages 68, 69 of Spanish NAR).The monitoring, testing, sampling and inspection activities described in those AMP are applied to EQ cable as well as to non-EQ cables. Independently, in the fact of a long term operation application EQ cables must be subjected to a Time Limited Ageing Analysis to determine their useful life.
ES-5 |  | United Kingdom | Spain | 02. Overall Ageing Management Programme requirements and implementation | 31 | Section 2.A.5. discusses the licensee's experience of the application of the overall AMP. Although originating from a fabrication issue, did the discovery of hydrogen flakes at Doel and Tihange in 2012/2013 result in any changes to the overall AMP or any learning that was applicable to plant other than the RPV? | Website | These events (Doel and Tihange) were analysed within the frame of industry experience. In addition, as it was a fabrication issue, and no ageing mechanism nor effect was identified, it did not result in any change to the overall AMP. Regarding if it resulted in any learning that was applicable to plant other than the RPV, fuel oil carbon steel buried tanks and piping, with cathodic protection could be affected by free hydrogen produced by improper voltage settings for the cathodic protection system. The Spanish NPPs do not have fuel oil carbon steel buried tanks or piping, with cathodic protection, then hydrogen damage is no considered as a potential ageing mechanism.
ES-6 |  | United Kingdom | Spain | 02. Overall Ageing Management Programme requirements and implementation | 13 | Section 2.3.1 describes the organisational structure and ageing management committee's role. How does the licensee senior management maintain oversight of the ageing management programme? What reports or key performance indicators are provided to senior management? | Website | Minutes of Ageing Management Committee (AMC) meetings are signed and registered by the Ageing Management Coordinator. Senior Management is informed on the Overall Ageing Management Programme regularly during Plant Steering Committee meeting; this includes the conclusions of annual reports on AMP follow-up, with an assessment of the AMP's results, and for some plants, AMP perfomance indicators. AMC meetings minutes are summarized in the “Annual Ageing Management Activities Reports” required by the regulatory body (CSN).
ES-7 |  | United Kingdom | Spain | 02. Overall Ageing Management Programme requirements and implementation | 36 | Section 2.4 states that the results of applying the AMP activities are analysed in order to determine if they are effective. What are the measures to judge whether they are effective? | Website | Results of the examination and monitoring activities, as well as the periodic analysis of the operational experience are used to verify that the AMP works properly. Working properly means that the AMP: - Detects the ageing effects managed by the AMP before the loss of intended function of the components. - In case of loss of intended function, it is analised what did not work properly in the AMP systematic and improvements are introduced in order not to happen again. Additionally, for each Ageing Management Programme an "AMP tracking report" is prepared periodically. This "AMP tracking report" summarizes the results of AMP activities and includes the AMP effectiveness indicator that assesses its effectiveness taking into account the three following aspects: 1) Activities results: If all foreseen activities have been performed and no significant ageing effects have been detected, the maximum indicator value is achieved, otherwise postponed activities and/or detected ageing effects will reduce the indicator value. 2) Operating Experience: Any internal or external experience that affect the AMP could reduce the indicator value. 3) Commitments: When the implementation of an enhancement proposal or other commitment that affects the AMP is delayed, the indicator value is reduced. The indicator trend is also evaluated every year. Almaraz and Trillo NPPs measure AMP effectiveness on a qualitative basis.
ES-8 |  | Slovenia | Spain | 02. Overall Ageing Management Programme requirements and implementation | 44 | Regulatory oversight process (Page 44): Regarding the content of annual reports required by the CSN during operating period. What is expected extend of information on implementation of individual AMP programs? Is CSN going to extend required scope of annual reporting in the LTO period? | Website | There is not an extend of information established by rule. Tipically, licensees give a page or two pages summary for each AMP, giving information about the activities, operational experience analyses and tracking reports among others, developed the previous year within the AMP and their results. In the last edition of the Spanish ageing management rule IS-22, the minimum content of the annual report is established, which is the activities developed the previous year, their effectiveness assessment, status of improvement proposals and the identification of the expected OAMP updates. During LTO period, the Spanish ageing management rule IS-22 requires the same annual report, giving the same information, but taking into account the scope required in that period.
ES-9 |  | Finland | Spain | 05. Reactor Pressure Vessels | § 5 | Thimble guide tubes are referred several times in chapter § 5 . A detailed drawing could be useful to better understand their construction and location and also the observed wearing cases. | Website | The thimbles are component used on Westinghouse PWR to monitor the neutron flux distribution. The BMI system incorporates guide tubes and Flux Thimble. The guide tubes are approximately one inch outside diameter stainless steel tubes which are attached to penetrations on the reactor vessel bottom head. The guide tubes extend from the reactor penetrations to the seal table which is located outside of the vessel. The BMI Flux is a long slender stainless steel tube, that passes through the guide tube, through the vessel penetration, through the reactor vessel lower internals, and finally extends to the top of fuel assembly. The thimble is subjected to reactor coolant on the outside surface and to atmospheric conditions on the inside. The thimbles are classified as ANSI Safety Class II. Westighouse analysed the Flux Thimble wear problem on the WCAP-12866, in which were established criteria for accurately measuring, predicting and dealing this issue.
ES-10 |  | Slovenia | Spain | 07. Concrete containment structures | 158-160 | Regulator’s assessment and conclusions on ageing management of concrete structures (Page 158-160): Does CSN perform inspections dedicated to AMP of concrete structures and other oversight on this area also with help of TSOs specialized for concrete structures? Are also third-party certification organizations activities required by the CSN for this area? | Website | CSN performs the inspections devoted to AMP without any help from TSOs. CSN does not require any third party certification. However some requirements from third party certification organizations are stated in the licencee inspection prodecures, such as NDEs personel cerfification.
ES-11 |  | Slovenia | Spain | 05. Reactor Pressure Vessels | 120 | Inspection of thimbles (page 120): The program to verify the thimbles integrity is based on detecting reductions in their thickness. The acceptance criterion is 80 % loss of thickness. On which basis is the acceptance criterion determined? Do you have experiences with damage/leaking thimbles? | Website | The bases for the acceptance criteria of 80% loss of thimble thickness is based on the WCAP-12866. This criterion has been established based on the results of several collapse test and compared them to the results obtained from an extensive FEA program. The Spanish Westinghouse PWR have experiences with damage thimbles but not with leaking.
ES-12 |  | Slovenia | Spain | 05. Reactor Pressure Vessels | 126 | Licensee's experience of the application of AMP (page 126): Are the root causes for Almaraz NPP 2010 findings (loss of thimble thickness due to wear and boric acid accumulations on the thermal insulation of the vessel head) identified? | Website | Yes. The loss of thimble thickness is due to wear of the thimble where the annular gap between the thimble and the reactor lower internal instrumentation column is smaller. Up to now, there have not been any leaking. The boric acid acumulations are caused by leakage of one coneseal.
ES-13 |  | Slovenia | Spain | 05. Reactor Pressure Vessels | 127 | Zinc injection at Asco NPP (page 127): The plant includes also the injection of zinc as preventive controls associated with the chemistry of the primary circuit. Do they experience some negative effects on nuclear fuel assemblies till now? | Website | The addition of zinc can have adverse effects on fuel and, in fact, there is operative experience in this regard. However, as a results of that operational experience analysis, ANAV has adopted preventive measures to prevent these effects since the beginning of the Zn addition, such as follow-up of the flow maps to check potential fouling in the fuel, periodic cleaning by ultrasound, Zn concentration control according to nuclear designs, etc. At Asco NPP no signs of corrosion have been observed in the elements attributable to the injection of Zn, nor have there been fuel failures attributable to it.
ES-14 |  | United Kingdom | Spain | 04. Concealed pipework | 84 | Section 4.1.1 discusses the AMPs in-place for the management of concealed piping. What arrangements are in-place to monitor the compliance at each station against these AMPs? What assurance is available that each station are adopting a consistent approach via the AMPs? | Website | According to the adopted methodology (American), after defining an AMP and its activities, each plant has to perform an AMP assessment against the 10 atributes of NEI 95-10 guideline, in order to verify the AMP consistency. The references taken for the assessment are the corresponding AMP on chapter X and XI on NUREG-1801, revision 2 (2010), and the applicable LR-ISG (2012-2016), where it is stated a recommended acceptable approach for the AMP features. The CSN, in periodic inspections every other year, verifies the consistency of these AMP evaluations.
ES-15 |  | United Kingdom | Spain | 04. Concealed pipework | 102 | Section 4.3 discusses the use of BP Works software, suggesting a need to demonstrate the effectiveness of the approach. Are there plans to follow-up on this action? Are there any thoughts on what this demonstration would look like? | Website | Almaraz and Trillo NPPs are the ones who use BPWorks in their concealed pipework program, to categorize them according to risk and plan their inspections and tests given that categorization; the rest of the Spanish NPPs use also risk information to select the piping location to inspect , as it is described in LR-ISG-2015-01 (ie., susceptibility to degradation and consecuences of failure), having into consideration characteristics such as coating type, coating condition, cathodic protection effectiveness, backfill characteristics, soil resistivity, pipe contents, and pipe function. CSN does not know yet the results of application of the methodology that follows the NEI 09-04 because it has been implemented recently in these plants, which means that there is not yet available application data (results). This position can be evaluated through tracking reports, which in the case of Almaraz and Trillo NPPs these report cover a period of 3 to 4 years of implementation of the AMP. Due to the fact that inspections of the CSN are performed every two years, this program of concealed pipework will be included in the inspection agendas of at least the two following inspections (2018 and 2020). That is, the CSN will inspect in 2018 the OAMP of both plants (Trillo and Almaraz) and this AMP in particular, and during these inspections it will be possible to check the scope, the categorization of the pipes, and the examination records, as well as the general state of implementation of the new AMP. Likewise, the annual report that these plants send to the CSN includes information about the activities of the program and its execution, as well as the status of the improvement proposals of all the AMPs. Regarding a quick assessment of whether BPWorks and the risk-based classification is adequate, it can be evidenced if the effects of aging are detected before the failure of the pipeline, or if, on the contrary, through-wall defects occur in the concealed pipes which were classified as low risk according to the BPWorks.
ES-16 |  | United Kingdom | Spain | 04. Concealed pipework | 106 | Section 4.3 highlights a variance from one station to the next, in terms of the implementation of the AMPs. How is it intended to ensure at least some element of consistency across the stations? | Website | CONSISTENCY BETWEEN PLANTS. According to the adopted methodology (American), after definig an AMP and its activities, each plant has to perform an AMP assessment against the 10 atributes of NEI 95-10 guideline, for AMP consistency. The references taken for the assesment are the corresponding AMP on chapter X and XI on NUREG 1801, revision 2 (2010) , and the applicable LR-ISG (2012-2016), where it is stated a reccommended acceptable approach for the AMP features. Regulator in periodic inspections every other year verifies the consistency of these AMP evaluations. The status implementation of the programmes varies from one plant to another for different reasons such as the diversity of scope in the program (systems and lines) and activities to be implemented. The adecuacy of each program on each plant must be based on the results of the program and on all activities being implemented and on the evaluation of the effectiveness of each program. For the CSN, as a regulatory body, we understand that an AMP is fully implemented when all inspection, testing and monitoring activities are being developed. To assess their adequacy, their effectiveness must be evaluated positively (in summary, the AMP detects degradations before the loss of intended functions.
ES-17 |  | United Kingdom | Spain | 05. Reactor Pressure Vessels | 115 | "Section 05.1.2 - AMPs are based on the provisions of NUREG-1801. Are the IGALL reports also used for AMPs or planned to be used in the future?" | Website | Up to date, the methodology chosen by CSN is the American methodology. However, several specific aspects contemplated in IGALL are taken into account for AMPs. In this case, according to the NUREG there are no big differences on AMPs.
ES-18 |  | United Kingdom | Spain | 05. Reactor Pressure Vessels | 127 | "Section 05.2 - Traces of boron in vessel head penetrations following visual inspection at Ascó NPP. a. Were these traces of boron found on one of the old vessel closure heads or on one that had been replaced? b. Was it found on a vessel head with Alloy 600 penetrations or Alloy 690 penetrations?" | Website | The traces of boron were detected on the new closure head instaled at unit 1 of Ascó NPP. The old vessel head was replaced by one that had been manufactured for another Spanish plant, but had never been put into service before. The material of the CRDM penetrations is Alloy 600.
ES-19 |  | United Kingdom | Spain | 07. Concrete containment structures | 155 | Section 7.2 The “In-service inspection of containment (concrete)” programme has led to the detection of grease stains on the outer surface of the containment building, due to leakage across the outer walls arising from a loss of sheath leak tightness. Please provide more information on the root cause and the implications for long term strand protection. | Website | The report ordered by the licensee concluded the following: -The vertical cracks were caused by the concrete retraction in the outer wall. -The grease leaked due to the fact that tendon ducts were not perfectly watertight and other paths which were more permeable were sealed (e.g. concrete hollows, concrete joint…). -The grease has no impact on the chemical characteristics of the concrete and very low incidence on the physical properties. -The grease flux is limited through the cracks and not through the sound concrete. -The presence of water in the grease does not produce the corrosion of the rebars and do not modify the steel properties. -The presence of grease has not influence in the steel-concrete bond.
ES-20 |  | United Kingdom | Spain | 07. Concrete containment structures | 153 | Section 7.2 Licensee Experience at ASCÓ NPP. During refuelling outage R21 in unit 1, the perimeter joint of the containment building was found to be degraded and with discontinuities, allowing water to enter to the lower elevations of the liner, an inaccessible area. Please provide more information on the likely leak path for the ground water and any efforts made to prevent further ingress. | Website | Due to this incident in the R21, a program inspection was established for both units. So in the following outages the liner-concrete joint was inspected performing around 600 liner thickness measurements and repairing if necessary. Apart from that, around 25 measurements were performed in the liner below the concrete and in the leak-chase channels area (concrete removal was necessary). Moreover, due to USNRC Information Notice IN-14-07 “Degradation of leak-chase channel systems for floor welds of metal containment shell and concrete containment metallic liner”, additional inspections have been included in the In-Service Inspection Manual.
ES-21 |  | Finland | Spain | 04. Concealed pipework | 105 | What are the corresponding safety and operation challenges, like maintaining safe shutdown condition, flooding risks, etc. connected to AMP? | Website | The main goal of the AMP is maintaining their SSC intended functions. For the concealed pipework, the main functions are pressure boundary and flow distribution. As it is shown in table 04.1 (page 84) that includes the systems managed by this AMP, selected according to the Spanish ageing management rule IS-22 criteria, such as: 1.- The capability to shutdown the reactor and maintain it in safe shutdown conditions 2.- Safety relevant elements whose failure might prevent satisfactory compliance with any of the safety functions. 3.- Safety important elements to which credit is given in the safety assessments of the faciltiy relating the requirements on fire protection.
ES-22 |  | Switzerland | Spain | 02. Overall Ageing Management Programme requirements and implementation | 10 | Does CNS Instruction IS-22 also require an (adapted) AMP for the transmission phase from definitive shutdown to approved decommissioning? | Website | Spanish ageing management rule IS-22 does not establish any requirement in definitive shutdown nor approved decommissioning. Nevertheless, in the case of SMG, requirements have been established via Complementary Technical Instruction.
ES-23 |  | Switzerland | Spain | 02. Overall Ageing Management Programme requirements and implementation | 10, 12 | Did you compare CNS Instruction IS-22 with the new IAEA (draft) safety guide DS485? If yes, what are the results of this comparison concerning physical ageing? If no, do you intent to perform such a comparison? | Website | No. Up to date, Spanish regulations follow the American rules. Anyway, IAEA Safety Guides are taken into account as references for ageing management activities in the Spanish OAMPs.
ES-24 |  | Switzerland | Spain | 02. Overall Ageing Management Programme requirements and implementation | 14, 15 | What role do the safety classification of SSCs and insights from the Probabilistic Safety Analyse (PSA) concerning the safety importance of components play within the scoping process? | Website | In Spain, the ageing management rule IS-22 is focused as a deterministic rule (not probabilistic), so PSA results are not considered in the scope of the ageing management. So the scope of the ageing management is established in the criteria mentioned in page 14 of the Spanish NAR.
ES-25 |  | Switzerland | Spain | 02. Overall Ageing Management Programme requirements and implementation | 39, 40 | What indicators are used in the Spanish NPP to evaluate the effectiveness of the implemented AMPs? | Website | For each Ageing Management Programme an "AMP tracking report" is prepared periodically. This "AMP tracking report" summarizes the results of AMP activities and includes the AMP effectiveness indicator that assesses its effectiveness taking into account the three following aspects: 1) Activities results: If all foreseen activities have been performed and no significant ageing effects have been detected, the maximum indicator value is achieved, otherwise postponed activities and/or detected ageing effects will reduce the indicator value. 2) Operating Experience: Any internal or external experience that affect the AMP could reduce the indicator value. 3) Commitments: When the implementation of an enhancement proposal or other commitment that affects the AMP is delayed, the indicator value is reduced. The indicator trend is also evaluated every year. Almaraz and Trillo NPPs measure AMP effectiveness on a qualitative basis.
ES-26 |  | Switzerland | Spain | 03. Electrical cables | 15, 16 | Textline7: How are "active" electrical components covered concerning ageing management (motors, valves, electronics)? i.e. as for mechanical RHR pumps. | Website | As it has been explained in the chapter 02 of the Spanish NAR, active electrical and I&C equipment are not included within the scope of the OAMP. Ageing management of that equipment is performed using the corresponding electrical maintenance programmes, the application of Maintenance Rule and other plant programmes, as an example the equipment environmental qualification programme, etc.
ES-27 |  | Switzerland | Spain | 03. Electrical cables | 68 | Trillo-Textline7: “…the cables in question were replaced with new cables, which are now changed every 6 years…” - what temperatures/humidity/etc. level is predominant there to force a 6-year change cycle of the cables? | Website | The cables, with ETFE insulation, were subjected to very high temperature (until 99ºC) in normal operation. This temperature was the combination of the room temperature, self heating coming from the solenoid coil (normally energized) and hot spots ( proximity to main steam pipes)
ES-28 |  | Switzerland | Spain | 04. Concealed pipework | 86 | What is the reason for the additional application of NEI 09-14 Rev. 3 for NPPs Almaraz and Trillo? What is the experience gained from this program? Are there conflicts regarding the recommendations and requirements for inspection programs defined by NEI 09-14 and NUREG-1801, respectively? | Website | REASON As holders informed, the reason for the application of NEI 09-14 at Almaraz and Trillo NPPs is because the guide provides the opportunity to identify the scope of examinations and monitoring activities based on the results of a risk ranking and therefore focusing the direct inspections on the most vulnerable areas. The program has served to identify the scope of the direct inspections and monitoring program needed to be performed. OPERATING EXPERIENCE As it is explain in page 105, Trillo NPP had some leakages and degradations between 2009 and 2015 in the fire protection system (FPS) and this operating experience motivated the Almaraz and Trillo plants to modify their activities related to the FPS in accordance with NEI 09-14, and decided to apply it to the entire concealed pipeline program, as an improvement to the activities included in their AMP, to address the problem of these leakages, in accordance with the NEI 09-14. CONFLICTS Evidently there are differences between the NEI 09-14 and LR-ISG-2015-01. LR-ISG-2015-01 (February 2016) is more modern than the NEI-09-14 in its revision 3 (April 2013). The main difference lies within the scope selection criteria and as a result the scope of the NEI 09-14 is wider to that of NUREG-1801. The examinations required by both programs are similar, however, some differences have been found in the criteria for the examination sample increase after finding any degradation. Inspections sampling increase criteria are more restrictive in GALL report. The extent of examinations established in table XI.M41-2 of LR-ISG-2015-01 vs NEI 09-14 is different. NEI 09-14 establishes a range of one to three inspections per buried pipe grouping. Likewise, NEI 09-14 gives credit to indirect inspections. The NRC has not credited indirect inspections, e.g. guided wave examinations, as an alternative to direct visual inspections of the external surfaces of buried pipelines.
ES-29 |  | Switzerland | Spain | 04. Concealed pipework | 89, 90 | The section on “internal surfaces” refers to AMPs that have a focus on external surfaces. How are these applied to internal surfaces, for which the relevant ageing mechanisms are usually different? | Website | Section 04.1.2.2 is discribing the ageing mechanism and effect that applies inside the concealed piping within the scope of this chapter, and the AMPs which are used to monitor and control the degradation from inside (internal surface) of the pipes. From the combination of the piping materials vs their environments, the AMR process is carried out to determine the ageing mechanisms and effects that are applicable to each pipe. The ageing mechanisms are different depending on the pipe of each system, its material and its internal environment, but in all cases the resulting ageing mechanism is "loss of material" with the exception of the case of stainless steel in contact with borated water (SCC). Spanish plants use up to 9 AMPs to manage the degradation of the internal surface of buried pipelines. As a consequence of this question, some mistakes have been detected in tables 04.4 and 04.6, which are indicated below: TABLE 04.4 CORRECTED *AMP.XI.M2 Water Chemistry: It is also applicable to AS NPP. *It has to be added a line in the table, "AMP.XI.M21A Closed Treated Water Systems": It is applicable to AS NPP as an AMP used to manage CC system. *AMP.XI.M17 FAC & LR-ISG-2012-01: It is not applicable to COF NPP. TABLE 04,6 CORRECTED *It has to be added a line in the table "Component Cooling Water Systems". *It has to be added a column in the table "M21A Closed Treated Water Systems": It is applicable to "Component Cooling Water Systems". *M17/LR-1SG-2012-01: It is not applicable to RCIC.
ES-30 |  | Switzerland | Spain | 04. Concealed pipework | 92 | What are according to the experience of the Spanish NPP the most effective techniques used for the monitoring of the outer and inner surface of not accessible pipework? Are travelling manipulators used in the Spanish NPP for monitoring not accessible pipework? | Website | The techniques used for monitoring concealed piping at Spanish plants are those mentioned in the NAR. There have been demonstrations tests at some plants with other techniques, such as Guided Waves, that have not been conclusive. According to the inspections carried out to date, the CSN has no evidence that robots are used inside concealed pipes to assess the state of the internal surface. In general, the piping pressure test is an activity really useful to verify that there are no leakages. Specifically for the FP system, it could be highlighted that the monitoring of the jockey pump is a key activity for the detection of a degradation with loss of intended function. To monitor how the external surface of a pipe is, the best technique would be through direct visual inspections (excavations) and visual inspection of the interfaces (manholes and others).
ES-31 |  | Switzerland | Spain | 04. Concealed pipework | 93 | Table 04.5: Why are there no visual inspections prior to LTO for NPPs VA2 and COF? | Website | VA2 NPP. This plant does not perform direct visual inspections (only opportunistic ones) because the holder is taking the alternative offered by the LR-ISG-2015-01 in which it is allowed not to perform direct visual inspections if you perform a pressure test to 25% or more of the pipes of the scope with a maximum frequency of 5 years, at a pressure of 110% of the design, with 8 hours duration. COF NPP. It has no buried pipes, only inaccessible pipes that run through trenches.
ES-32 |  | Switzerland | Spain | 04. Concealed pipework | 94 | What is the operating experience gained from opportunistic direct inspections? | Website | The AMP-XI-M41 of the LR-ISG-2015-01 clearly indicates that opportunistic direct inspections should be carried out whenever a pipeline within the scope of the program is accessible, for any reason, related or not to this AMP (the reason). During the plant operation, all those occasions in which, with another intention, parts of buried pipe within the scope are discovered, direct visual inspections will be performed to them (backfill, coating and base metal). The result of these inspections is documented and can replace the inspections indicated as visual inspections before LTO (programmed ones on the pipes of the systems within the scope) in case of fulfilling the criteria of selection of the same and/or will serve as operational experience of the program and information for future evaluations. During qualified opportunistic direct visual inspections, the condition of the pipe is checked on the outer surface, taking into account its backfill and coating. For example, in the case of Ascó NPP, two opportunistic inspections were performed in 2015 on the Fire Protection System, when thicknesses were measured by ultrasonic tests. In these two opportunistic inspections, no significant degradations were observed, and the measurement of UT showed thickness values ​​much higher than the minimum required.
ES-33 |  | Switzerland | Spain | 04. Concealed pipework | 95 | How do you make sure that the 3 m uncovered piping section selected for the inspections is representative for the buried sections of piping? | Website | The AMP.XI.M41 of the LR-ISG-2015-01 indicates in point 4.c "guidance related to the extent of the inspections for piping" that if the inspection is based on the number of inspections instead of on the percentage of length of the pipeline, it will be exposed 10 feet (3 meters) of the pipe in each inspection.
ES-34 |  | Switzerland | Spain | 04. Concealed pipework | 101 | Mitigation of stress corrosion cracking in stainless steel is done through control of water chemistry. Table 04.3 shows that both VA2 and AS have stainless steel piping with borated water and therefore a susceptibility to SCC. Water chemistry management is done only for VA2 (Table 04.4). What is the SCC mitigation concept for AS? | Website | There is a mistake in tables 04.4 and 04.6. The AMP.XI.M2 Water Chemistry also applies to Ascó NPP for stainless steel/treated borated water combination. As a consequence of this question, some mistakes have been detected in tables 04.4 and 04.6, which are indicated below: TABLE 04.4 CORRECTED *AMP.XI.M2 Water Chemistry: It is also applicable to AS NPP. *It has to be added a line in the table "AMP.XI.M21A Closed Treated Water Systems": It is applicable to AS NPP to manage CC system. *AMP.XI.M17 FAC & LR-ISG-2012-01: It is not applicable to COF NPP. TABLE 04.6 CORRECTED *It has to be added a line in the table "Component Cooling Water Systems". *It has to be added a column in the table "M21A Closed Treated Water Systems": It is applicable to "Component Cooling Water Systems". *M17/LR-1SG-2012-01: It is not applicable to RCIC.
ES-35 |  | Switzerland | Spain | 05. Reactor Pressure Vessels | 122 | What is the number of surveillance capsules and how many of them are tested? | Website | Vandellós II, Ascó 1&2 NPPs (PWR-W): There were 6 capsules 4 of which have been tested. The remaining (2) are stored in the Spent Fuel Pool. Almaraz NPP (PWR-W): There were 4 capsules of which all 4 have been tested. Trillo NPP(PWR-KWU): There were 3 capsules, of which 2 were withdrawn together at the 2nd. operation year. Cofrentes NPP (BWR-GE): there are 3 surveillance capsules with probes and dosimeters. Two surveillance capsules were withdrawn during refueling outages 6 (1991) and 13 (2002); after the probes analyses, the probes were reconstituted and deposited again in the following refueling outage. Nowadays there is one surveillance capsule for the 40 years withdrawal and, two available surveillance capsules for the long term operation period.
ES-36 |  | Switzerland | Spain | 05. Reactor Pressure Vessels | 122 | Is acceptance of neutron embrittlement considered by screening criterion according to PTS rule 10CFR 50.61? What is the highest RTNDT? | Website | Yes. The RPV (PWR) should be verified to the presurised thermal shock (PTS) screening criterion according to the rule 10 CFR 50.61. The value of RTPTS for the vessel beltline material above which the plant cannot continue to operate without justification are 270º F for plates and axial weld materials, and 300ºF for circumferential weld material. The RTPTS must be determined for each vessel beltline material using the EOL fluence for that material. If the screening criterion is nor fulfilled, the RPV must also be analysed according to the alternative pressurized thermal shock rule 10 CFR 50.61a. The maximum RTNDT (54 EFPY) in each plant are the following: Vandellós II NPP: 184,57ºF, Ascó 1 NPP: 188,25ºF, Ascó 2 NPP: 166,07ºF, Almaraz 1 NPP: 143,74 ºF, and Almaraz 2 NPP: 165,72 ºF. For Cofrentes NPP the maximum RTNDT is 98,6 ºF (PTS is not applicable to Cofrentes due to being BWR technology).
ES-37 |  | Switzerland | Spain | 05. Reactor Pressure Vessels | 130 | Is it planned to include effects of environmental fatigue to AMP in future? | Website | Yes. Spanish utilities are addressing EAF for LTO according to NUREG-1800 and NUREG-1801.
ES-38 |  | Czech Republic | Spain | 03. Electrical cables | 55 | "The report states: Cable jackets and shielding serve only to protect the insulation, as a result of which they do not participate in the intended function of the cable and do not require this process of AMR. The deterioration of the mechanical properties of the cable jacket due to aging can lead to a violation of the sheath. When the sheath is disturbed, the ambient moisture may penetrate the cable insulation and accelerate its aging process leading to the loss of its insulation resistance. From my point of view, the AMR process should be required for for the cable jacket." | Website | The text in page 55, tries to express that the most important element of a cable, in order to fulfill its intended function, is the insulation. Visual inspections required by Spanish plants cable AMP's, are performed on the jackects, and jacket degradation is evaluated in order to determine the corresponding insulation degradation. For most cables, jackets are built with materials that age faster than the insulation material so, if jacket is not degraded, we can considered that insulation is in good conditions.
ES-39 |  | Finland | Spain | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Website | The main goal of the AMP is maintaining RPV integrity. According to the Spanish rule IS-22 criteria, safety related elements that are required to continue operating during and after any design basis event that might occur in order to guarantee the integrity of the reactor coolant pressure boundary are within the scope of ageing management.
ES-40 |  | Czech Republic | Spain | 03. Electrical cables | 57 | "Spanish NPPs have used radiation and temperature limiting conditions for a period of 60 years, as specified in EPRI 1013475" Using only literature data for assessing the life time can insert big mistakes. It must be checked what property is limiting, if the plant have the same cables as tested etc. Reference is OK for first survey, but the life time must be based on experiments on really installed cables. | Website | The EPRI 1013475 radiation and temperature limiting condition values for 60 years of operation, are only applicable to non EQ cables, in order to determine, as a first survey, which of them will need a subsequent ageing management review. EPRI values are not applicable to cables that must function under accident conditions (EQ cables), for which their environmental qualification proccess define a "qualified life". During the period of normal operation qualified life is managed by the "Environmental Qualification Maintenanace Program". In case of applicaton for a long Term Operation permit, cable qualified life is reanalysed by a Time Limited Ageing Analysis.
ES-41 |  | Czech Republic | Spain | 03. Electrical cables | 79 - 83 (annex to chapter 3) | Are all the cables listed in Annex 1 included in ageing management programmer in Spain? | Website | NO. The cables included in the scope of Spanish NPP AMPs are those identified in tables 03.2 and 03.3 of the Spanish NAR. Cables in table 03.1 are all the cables types existing in the plants, but as a consequence of the "Plant spaces approach" performed in each NPP, most of them have been screened out from the scope of the cable AMPs.
ES-42 |  | Czech Republic | Spain | 07. Concrete containment structures | chapter 2.4 - generally (36-40) and chapter 7 - generally (136-149) | How often - or if even - are the inspection intervals of civil structures reassessed? Are those inspection intervals changes based on operational experiences and ageing effect treds? Is the NPPs age, especially when considering the LTO phase of operation with higher risk of ageing effects appearance), taken into account for establishment of the inspection intervals? | Website | As stated in the CSN 1.18 safety guide, an inspection should be performed at least once in five years. This period could be exceeded due to outage plans, so long as two inspections are performed in the ten years period. After the inspection, and based on the results and the trend of the ageing effects, the next inspection time is provided. The inspection intervals are only based on the ageing trend and the ageing mechanism (e.g. structures in moist environment).
ES-43 |  | Czech Republic | Spain | 07. Concrete containment structures | chapter 7.1.1. (137-138) and chapter 7.2. (157) | Have you ever detected the ASR (alkali-silica reaction) in reinforced concrete structures structures of nuclear power plants during their operation? If so, which parts of structures were affected? Please describe, if the appearance was found in monolithical parts of constructions built on site or in imported prefabricated materials. If ASR was found, how did you proceed this issue? | Website | During Spanish NPP construction period, aggregates were chosen so ASR reaction were prevented. However after the operating experience showed in the USNRC Information Notice IN-2001-20, particular inspections were performed to assess the potential ASR reaction. Only in Cofrentes NPP some surface cracks could be attributed to ASR, so more studies were carried out. In 2012 Cofrentes NPP carried out some investigations in order to verify if the surface cracking that exist in some small areas of the structure surface in contact with the environment could be due to the Alcali-Silica reaction (ASR). The initial investigation did not provide a clear assessment regarding the degradation of the concrete, recommending some additional investigation to be performed. The initial investigation was performed by AIDICO Institute. AIDICO was closed later on and it was not possible to continue with the second phase of the investigation. During 2017, CIMNE was contracted to continue with the AIDICO recommendations and to finish the pending investigation. A national specialist in the area, is leading this project. The status of the project is the following: • The AIDICO report has been revised and some gaps have been found regarding the record details of the test performed. There is no detailed information regarding the process or protocol used for the test. In the pictures included in the report, it is no clear evidence of presence of silica gel, as it is stated in the conclusion. • Cofrentes NPP life management structure database has been revised to check the photography of the surface cracking pattern found in the some NPP structures, and made a plan for in-situ inspection. The cracking pattern found in the existing photos is smaller than the one produced by ASR and it is probably due to shrinkage of the surface cement. Nowadays licensees are preparing in-situ inspection to define the location where additional testing proposed by AIDICO will be performed and to prepare a complementary testing to produce an assessment regarding the existence of ASR degradation in Cofrentes NPP structures. It is foreseen to finish this analysis by mid of 2018.
ES-44 |  | Czech Republic | Spain | 07. Concrete containment structures | chapter 2.3.3. (32-36) | In what form you have processed the zero-condition passportization of flaws and malfunctions of NPP civil structures? Is this base passportization updated on the basis of results of regular maintenance activities and/or more detailed survey of intednded structural objects? Do you regulary evaluate appearance of new flaws or changes in previously found flaws and malfunctions with respect to the base zero-condition passport? What kind of documentation do you use for planning and conducting of this constructional-technical survey (e.g. ISO 13822)? What kind of degradation that was found within the constructional-technological surveys is most often (please provide examples, e.g. shear cracks, bend cracks, shrinkage and creeping of concrete, carbonation of concrete CO2, corrosion of reinforcement or concrete, mechanical overload, stability loss of constructions - tilting, bracing, excessive bending, etc.)? | Website | - It is understood that zero-condition passportization refers to the Reference Inspection. In such case, for all the Spanish NPP's, this reference inspection, that sets the starting point and reference for future inspections, was carried out and documented in an specific report. - Flaws are registered and their evolution are followed in successive inspections. For structures surveillance an inspection plan is created. This plan identifies all the structures that needs to be inspected with the associated inspection frequency. - Yes. Several AMP are implemented (Maintenance Rule, ISI (IWE, IWL, IWF), IST, tendons presstres surveillance), etc. and the flaws are evaluated and followed. Planning/Conducting: TS, ASME XI, 10 CFR 50.65, ACI 349 / 318, Safety Guide 1.15 (CSN), EHE (Spanish Concrete Rule) define inspection frequencies which are accomplished through the corresponding AMP. - The degradation mechanisms that have been identified are included in section 7.2. No degradation mechanisms that could affect the intended functions of the containment structures have been identified at the Cofrentes, Almaraz and Trillo NPP's. ANAV: Corrosion in liner and other metallic locations. No remarkable flaws in concrete have been detected. Water has been found (and removed) in presstressed tendons caps.
ES-45 |  | Czech Republic | Spain | 07. Concrete containment structures | chapter 7.1.3. (142) | Do you have geodetic measurement and assesments of settlement and tilt of civil structures important for (main production block, containment, confinement) and related to (ventilation chimney, building with dieselgenerators, blackout dieselgenerators, main pump station, end heat receiver, etc.) nuclear safety in your aging management programs? Did you find any problems with uneven foundation settlement of NPP civil structures? Did you identify any typical flaws (shear cracks) caused by civil structures settlement? If so, please specify and describe, how did you deal with this issue | Website | All the NPP have topographic control of settlement for structures related to safety in their Maintenance Rule programs. In Ascó 2 NPP there have been uneven settlement for their structures since the construction period. There are cracks due to this issue that are controlled with the implementation of the Ground Movement Surveillance program. In the rest of the fleet this issue is of very low significance.
ES-46 |  | Czech Republic | Spain | 07. Concrete containment structures | chapter 7.1.2. (140-142) | In what way and how often do you perform monitoring of containments steel hermetic lining condition? Is it measured punctually on test spaces chosen in advance within the construction phase, or is the measurement conducted aeraly e.g. by phased-array probes? Did you change test spaces during operation or was the number of test spaces extended/narrowed based on the inspection results? Have you ever found problems with thickness weakening in base material or weld joints of the containment hermetic steel lining during operation of any nuclear facility ? If so, please specify and describe, how did you deal with the situation. | Website | - The inspection/monitoring activities are included in section 7.1.3. As part of In-Service Inspection the metallic lining is monitored by visual inspections and ultrasonic test according to ASME Code. Visual inspections and UT are performed. In the case of PWR WH plants, metallic containment lining is visually inspected with a frequency of 3 years. Additionally to the information included in the NAR, the Trillo NPP metallic containment liner is inspected each 12 months as required by Technical Specifications and structural inspections under the Maintenance Rule process. The Almaraz NPP metallic containment lining is inspected during each refueling outage under Maintenance Rule process. - It is understood that the question relates to UT included in section 7.1.2. UT are performed according to the ASME code, including zones that require augmented inspection as a consequence of previous visual inspections and surface areas which require augmented inspections that are not accessible on the side requiring augmented inspection. - Loss of thickness has not been observed at Cofrentes, Trillo nor Almaraz NPP's. ANAV: Yes, there is operating experience of loss of wall thickness in the containment liner. During the Ascó Unit 1 NPP 21st Refueling Outage, signs of corrosion in 3 areas in the liner (under the acceptance criteria (nominal thickness - 10%)) on the joint which seals the protection concrete liner with the liner itself, were identified. The indications were detected while performing the requirements of Subsection IWE, Category EA, item E1.11 (visual inspection). It was decided to remove the joint and carry out further inspections in that area which, according to the criteria of IWE, is an inaccessible area and, therefore, excluded from the in-service inspection requirements. A visual inspection of the liner was performed and also volumetric measurements were made every 20 cm (along the 360º in the elastic joint area). Additional volumetric inspections were performed in order to find the minimum liner thickness in the regions in which visual inspection detected signs of degradation. The liner perimeter was divided into areas of 15°, and the thicknes was measured at 649 points located under the sealing joint. The results of these measurements are as follows: • 4 measurements between 3.6 and 4.4 mm • 126 measures between 4.5 and 5.7 mm • 325 measures between 5.8 and 6.4 mm • 194 measures 6.5 mm (liner nominal thickness) or greater Based on these results, it was decided to determine the status of the metal liner embedded in the concrete area. The inspections were held in areas where the lower thicknesses were obtained previously. 30 inspections in total were made of the embedded liner. Volumetric inspections at every location were performed by using grids of 10 x 10 cm. In these cases, all the measurements (504 inspection points in total) were superior to 5.7 mm. 89 areas with pitting corrosion were identified in the embedded liner. Thus, additional volumetric measurements were performed around the affected region. For the pitting areas, thickness values were determined by subtracting the depth of the pitting to the thickness of the nearest area, with the following results: • 1 measurement of 3.7 mm • 36 measurement between 4.5 and 5.6 mm • 37 measurement between 5.8 and 6.4 mm • 15 measurement 6.5 mm or greater Areas with measured thicknesses below 4.5 mm were repaired (4.75 mm for areas affected by pitting). The acceptance criteria indicated in IWE-3511.3 is 5.85 mm (10% loss of nominal thickness). A reassessment of the minimum required thickness of the liner, considering the design requirements, concluded that the minimum thickness of the liner is 3.7 mm. All areas with thicknesses between 4.5 and 5.85 mm, which have not been repaired, were accepted through engineering assessment as specified in Article IWE-3122.3. Superficial examinations were also carried out showing no indications (cracks) around the most degraded regions. Description of Repair Welds: 3 to 4 mm weld overlay on the affected regions. The extension depends on the location (affected region). SMAW F113. Filled material: E7018 C: SB942520. All the welds were visually inspected and superficially (penetrating liquid) tested. Vacuum box (-0.8 bar) was also done to all the repaired areas with acceptable results.
ES-47 |  | Czech Republic | Spain | 03. Electrical cables | 56 | "…adverse …..those corresponding to the design normal operating conditions (T,R)…." Common practice is that real values are used. But these are mostly lower than design values and thus design are more conservative. Does the environmental conditions were measured and compared with design values in Spanish NPPs? | Website | YES. All Spanish NPP have developed environmental conditions monitoring programs for identifying the "actual values" of temperature and radiation in all areas including equipments that require environmental qualification. The actual values measured are compared with design values, as an activity of the environmental qualification maintenance performed in each plant, for managing the qualified life of those equipments. The actual temperature and radiation values will also be used as a basis, for the resolution of the "Time Limited Ageing Analysis on Environmental Qualification " that each plant will have to develop in case of an application permit for Long Term Operation.
ES-48 |  | Belgium | Spain | 05. Reactor Pressure Vessels | 119 | In case of LTO, will the need to perform volumetric inspections for vessel bottom instrumentation penetrations be assessed? | email | The CSN is considering the need that licensees carry out one-time volumetric inspection of the BMI penetrations in case of the plant´s long-term operation.
ES-49 |  | Belgium | Spain | 05. Reactor Pressure Vessels | 117 | Has an enhanced inspection programme been developed for dissimilar welds between the vessel nozzels and the piping? | email | Yes, they are inspected under the code case N-770-2 recently introduced as obligatory in the 10CFR50.55a American law section. Since 2009 dissimilar weld inspectons have been performed according to the programme defined in the Code Case N-770 (see tables 05.9 and 05.10 in pages 119 and 120 respectively of the Spanish NAR).
ES-50 |  | Belgium | Spain | 02. Overall Ageing Management Programme requirements and implementation | 33 | Which edition of the ASME Code Section XI is currently used in the Spanish NPPs? | email | In Spain, American rules are followed for in-service inspection. In the American law, 10 CFR 50.55a establishes that the "inservice examination of components and system pressure tests conducted during successive 120-month inspection intervals must comply with the requirements of the latest edition and addenda of the ASME Code incorporated by reference in paragraph (a) of this section (10 CFR 50.55a) 12 months before the start of the 120-month inspection interval" For the Spanish NPPs, the current editions of the ASME Code Section XI are: Almaraz, Ascó, Cofrentes: 2007 edition and 2008 addenda. Trillo and Vandellos II: 2001 edition and up to 2003 addenda.
ES-51 |  | Belgium | Spain | 02. Overall Ageing Management Programme requirements and implementation | 36 | Which approach/tool is used to establish/optimize predictive maintenance programs (RCM? AP-913? Own program?) in the Spanish NPPs? | email | Currently, AP-913 process is used (voluntarily) in all Spanish NPPs, but with differente degrees of implantation. It is not required by regulation. In the past, RCM techniques were used to optimize the maintenance programme.
ES-52 |  | Belgium | Spain | 03. Electrical cables | 67 | The report explains that the intrusion of humidity in eletrical penetrations located in the annulus caused the subsequent failure of cables. Could you clarify a bit more the reason for this failure? Was it a manufacturing problem or a lack in the qualification programme (understimation of humidity in normal operation) ? Could you elaborate on how you later improved the programme for surveillance of humidity in the annulus? | email | The root causes for loss of insulation in one of the modules of the penetrations, were: * Manufacturing problems with one module AWG12 size, due to the section and high density of conductors inside the module. The insulation resin compound was not properly distributed inside one part of the module, therefore some air bubles appeared inside the module. * Water condensation during operation of the plant inside the reactor containment annulus due to some valve leakages. This eventually water condensation went by capilarity inside the module till the bubles air in the resin. Corrective actions were taken, replacing modules AWG12 in all penetrations and improving the annulus environmental conditions monitoring program, increasing inspections frequency and checking leakages with control of the annulus drain system.
ES-53 |  | Belgium | Spain | 03. Electrical cables | 60 | The scope of the cables subject to a process of AMR is limited to the cables located in adverse environment. As a result of this scoping process, are there types of cables that are not included at all in the AMR process because they none of them is located in an adverse environment? If this is the case, how was evaluated the opportunity to nevertheless perform an (somewat limited) ageing management programme for those cables as, for instance, a precautionary measure and to increase the knowledge basis ? | email | YES. As a consecuence of the plant spaces approach, those cables (cables without environmental qualification requirements) when properly designed according to their plant specification are not expected to be affected by ageing if an adverse environment is not present and are not included in the scope of the cable AMP. That is not to say that those cables are not never inspected or tested, because they are subjected to the maintenace activities (inspections and tests) of its circuits and associated electrical equipments.
ES-54 |  | Belgium | Spain | 03. Electrical cables | 74 | For the PWR plants : at what frequency are performed the periodic walkdowns for the identification of hot spots or other relevant conditions or what conditions triggers the need for the organisation of new walkdowns? | email | Initial Walkdowns for hot spots identification on accessible cables were initiated to select, among all the cables in scope of the AMP-1 (see NAR page 68) those located in worst service (enviromental or operation) conditions. The selected cables were included in the list of cables to be tested or visually inspected. For accesible cables, it is a plant choice to perform subsequent walkdowns, but this is not a requirement of the AMP-1. But, in the case of cables inaccessible or located in trenches or galleries, where significant humidity or stagnant water could exist, AMP-3 (see page 71 of the NAR) required to inspect (walkdowns) those trenches and galleries at least once a year.
ES-55 |  | Belgium | Spain | 03. Electrical cables | 58 | The report explains that an analysis is performed based on the documentation of the plants in order to identify cables existing in underground galleries, trenches or buried inside ducts in which water may accumalate and the cables be submerged or lead to a concentration of humidity capable of creating water treeing in the insulation. Could you elaborate a bit more on the type of analysis that is performed ? Based on what elements is it evaluated whether the cables located in underground galleries, trenches or that are buried may or may not be subject to high humidity ? | email | Conservatively, it is considered that cables located in underground galleries, trenches or buried inside ducts , at some time during the life of the plant can be subject to high humidity. So, initially and according to GALL AMP.XI.E3, all cables in such locations are selected. Later and in some cases, if the plant can justify (by the existance of reliable water exaust devices or by the performance of very frequent visual inspections) that water or significant humidity will not affect the cables in some locations, those cables could be eliminated from the AMP scope.
ES-56 |  | Belgium | Spain | 03. Electrical cables | 68 | In Almaraz NPP, cable degradation has been observed in containment affecting in particular cables connected to neutron detector chambers located in wells adjacent to the reactor vessel. What were the identified causes of degradations and what was the impact (if any) of this operating experience on the cable ageing management activities ? | email | Causes of degradation were the high radiation and temperature values existing in cables location. Degradation was identified by the low values of the measured insulation resistance of the cables.Consequently, cables connected to the neutron detector chambers are periodically substituted.
ES-57 |  | Belgium | Spain | 07. Concrete containment structures | 138 | What are the acceptance criteria related to the ageing mechanisms listed? | email | Acceptance criteria are plant specific, although values are quite homogeneous among them.
ES-58 |  | Belgium | Spain | 02. Overall Ageing Management Programme requirements and implementation | 13 | Could you precise the exact roles of the Ageing Management Coordinator and the Lifetime Management Coordinator? How are these two roles intricated and how are they interacting in practice? | email | They have been used as synonyms. It is a translation mistake. We wanted to use only "Ageing management coordinator".
ES-59 |  | Belgium | Spain | 02. Overall Ageing Management Programme requirements and implementation | 17 | The report indicates that the overall AMP applies only to passive SSCs since application of the Maintenance Rule (regulated in CSN Instruction IS-15) to active components guarantees that the critical functions, in components defined as being within its scope, are within acceptance levels. Does the operator perform checks to verify that all SSCs are either in the list of passive SSCs subject to the AMP or in the list of active SSCs subject to Maintenance rules. How does the regulator check that all safety SSCs are in one of the two lifetime management program (Maintenance or Ageing)? | email | Passive components scope is defined under the Spanish IS-22 ageing management (AM) rule (based on 10CFR54 American standard), and active components scope is defined under the Spanish IS-15 maintenance rule (MR) (based on 10CFR50.65 American standard). MR scope is wider than AM scope, with the exception of fire protection system, that is not completely included in the MR scope. In Spain, there is a specific rule (IS-30) that regulates fire protection system and their components performance. Maintenance Rule (MR) includes active components and structures, assesses the SSC performance, and how maintenance affects the SCC performance in order to verify the SCC intented function. If a system intented function is in the Overall AMP scope and in the MR scope, the active part of the components that perform the intented funtion are in MR and its passive part in the OAMP. A more complete explanation of this issued can be found in US Federal Register/Vol. 60, No.88/monday, May 8, 1995/ Rules and Regulation. NUCLEAR REGULATORY COMMISSION 10CFR Parts 2, 51, and 54. III Principal Issues; section (v) Excluding Structures and Components With Acive Funtions, and (vi) Excluding Fire protection Components With Active Funtion. According to IS-15 and IS-22, all safety SSC's should be included in the scope of both programmes, MR and Ageing Management. CSN has been performing, within the base inspection plan, inspections since 2005 every two years, including the scope of the overall ageing management programme. CSN inspections related to maintenance rule are also within this base inspection plan, since 2000.
ES-60 |  | Belgium | Spain | 02. Overall Ageing Management Programme requirements and implementation | 17 | "..They are long-lived, in other words they are not included in any periodic replacement programme based on maintenance of its qualified lifetime...". Are all types/groups of SSCs (mechanical/electrical, IPS,…) qualified in Spain? Does the elaboration of the overall AMP requires some efforts on qualification of equipments? | email | Qualification of equipment is part of the Current Licensing Basis (that is, Seismic and Environmental Qualification of Electrical and I&C Components) then, the overall AMP does not require additional qualification efforts, except if LTO is considered. For the Long Term Operation, the Environmental Qualification is identified as a TLAA. As result of the TLAA some equipment qualified for 40 years could be not qualified for LTO (more than 40 years), in this case the component is “short-live”.
ES-61 |  | Belgium | Spain | 02. Overall Ageing Management Programme requirements and implementation | 30 | "IAEA’s IGALL programme [40] in which many AMP’s have been developed, this having provided the Spanish plants with an additional reference for the development of their own AMP’s." Can you precise which proportion of the AMPs developed within IGALL Program are transposed within the Spanish NPPs. | email | As it is said in the text extracted from the Spanish NAR, IAEA's IGALL is an additional reference, but Spanish regulation follows the American standards (that is, AMP's from NUREG-1801, "GALL"). Additionally the two following AMP's specific for the Spanish NPP's have been included in the IGALL AMP's: - AMP 310: Ground movement surveillance. - AMP-208: High voltage insulators and transmission conductors. From a comparison made between IGALL vs GALL AMP's: - There are 76 AMPs in the IGALL. - 53 of the 76 IGALL AMPs have an "equivalent" AMP in the GALL Report. - 21 of the 76 IGALL AMPs are not applicable to the Spanish NPPs, because they apply to other NPPs technology, active components, obsolescence, etc.
ES-62 |  | Germany | Spain | 02. Overall Ageing Management Programme requirements and implementation | 37 | In Section 02.4 it is mentioned that in addition to the updating process described, during development of a design modification and prior to its implementation, the Cofrentes, Ascó and Vandellós II plants analyse its potential impact on the OAMP. Why is Trillo not mentioned in this list? Does the NPP Trillo not analyse the potential impact on the OAMP? | email | Almaraz and Trillo analyse the potential impact on the OAMP once the design modification is implemented. After a period of time, Almaraz and Trillo collect all the design modifications implemented during that period of time, and analyse their impact on the OAMP. In case of some design modifications affect the OAMP, then they update the OAMP taking into account all the changes at the same time. Cofrentes, Ascó and Vandellos update the OAMP in the same way, but they anticipate some work during the desing stage, so in the moment of updating the OAMP, they already know which design modifications have to be analysed.
ES-63 |  | Germany | Spain | 03. Electrical cables | 56-57 | On p. 56-57 it is mentioned that hot spots in the plant were identified via walkdowns. Is this identification process a periodical process or is this a one-off endeavour? | email | Initial Walkdowns for hot spots identification on accessible cables were initiated to select, among all the cables in scope of the AMP-1 (see NAR page 68) those located in worst service (enviromental or operation) conditions. The selected cables were then included in the list of cables to be tested or visually inspected. For accesible cables, it is a plant choice to perform subsequent periodic walkdowns, but this is not a requirement of the AMP. But, for the case of cables inaccessible or located in trenches or galleries, where significant humidity or stagnant water could exist, AMP-3 (see page 71 of the NAR) required to perform periodic walkdowns on those trenches and galleries at least once a year.
ES-64 |  | Germany | Spain | 03. Electrical cables | 65-67 | On pages 65-67 an ongoing research project/effort is described. For several destructive testing methods (EAB, OIT etc.) values for the validation of measurement results are or are to be derived. How are these values going to be used in the plants? As there are no cable deposits, the reviewer assumes samples will have to be taken from the cables in use at the plants themselves. | email | Regarding to samples for testing, in phases 2 and 3 of the coordinated research program (PCI), they have been taken from cables in use at the plant. Results of phases 1 and 2 have been incorporated in UNESA documents ES13/IT-02/03/04/05/06 (see NAR page 65) and have been taking into account for developing de cable AMPs, used during design life period (40 years). Phase 3 results, (expected for 2020) will be condition indicator values (Elongation at break, Indenter modulus, electrical tests) to be applied, during the Long Term Operation period, for cables that must function under accident conditions (EQ cables).
ES-65 |  | Germany | Spain | 04. Concealed pipework | 90 | On the one hand, flow assisted corrosion (FAC) does not appear in the table 04.3 of possible ageing mechanisms of the internal surfaces. On the other hand an AMP to manage FAC is described on page 101 as "an analysis, inspection and verification programme, as a result of which no preventive actions are performed." Does FAC play a role for concealed piping in the Spanish plants and if yes, how is it managed? | email | FAC does not play a role for concealed pipework. For the case of Cofrentes, both in table 04.4 and in page 101, a FAC AMP should not be ticked and mentioned; it is a mistake. FAC is affecting the RCIC system, but only the steam piping of the system which are not concealed. RCIC system has got concealed steainless steel piping for ambient temperature demineralized water, therefore no FAC is expected for this pipework. Vandellós II separates the version of AMP.XI.M17 included in the LR-ISG-2012-01 into two differen programs: AMP "Erosion Programme" and AMP "FAC Programme". The objective of this AMP "Erosion programme" in Vandellós II is to manage the loss of thickness due to various erosive mechanisms (cavitation, flashing and solid particles) of those components within the scope of the OAMP and that it is not postulated that they suffer degradation due to FAC. Erosion is postulated in the fire protection system. This mechanism is managed by visual or volumetric NDE in a sample basis. For Vandellós II NPP, FAC is not applicable in concealed piping. As a consequence of this question, some mistakes have been detected in tables 04.4 and 04.6, which are indicated below: TABLE 04.4 CORRECTED *AMP.XI.M2 Water Chemistry: It is also applicable to AS NPP. *It has to be added a line in the table "AMP.XI.M21A Closed Treated Water Systems": It is applicable to AS NPP as an AMP used to manage Component Cooling system. *AMP.XI.M17 FAC & LR-ISG-2012-01: It is not applicable to COF NPP. TABLE 04.6 CORRECTED *It has to be added a line in the table "Component Cooling Water Systems". *It has to be added a column in the table "M21A Closed Treated Water Systems": It is applicable to "Component Cooling Water Systems". *M17/LR-1SG-2012-01: It is not applicable to RCIC.
ES-66 |  | Germany | Spain | 05. Reactor Pressure Vessels | 124 | According to the licensee, the greatest accumulated fatigue usage factor of PWR RPVs was determined among others for the vessel bottom and transition zone, while the upper head dome to flange transition is not mentioned. What are the relevant loadings for the vessel bottom and transition zone? How large is the usage factor of the upper head dome to flange transition compared to these areas? | email | The upper head dome to flange transition cumulated usage factor is calculated considering the design analysis in each plant. In those cases in which the RPV head has been replaced the expected life in terms of fatigue may be valid for the LTO period. Relevant loadings: Heat-up, cool-down, hot stand-by feedwater cycles, normal stand-by loop, refueling outage, roll test, loss of power without reactor scram, blackout with natural refrigeration, full power scram with safety injection, unnoticed RCS depressurization, excessive feedwater flow and primary side hydrostatic test . As an example, below are included some data taken from the Time Limited Ageing Analysis (TLAA) for the new lifetime period requested by Vandellós II and Almaraz 1&2 NPPs (60 years). Vandellós II NPP: Design CUF 40 years for transition zone is 0.0082 and for the Reactor vessel head 0.0306. Expected CUF 60 years with environmental factor for transition zone is 0.004 (that value is low because the number of cyclic behavior is approximately 50% less). Expected CUF 60 years (does not apply environmental factor) for Reactor vessel head is 0.0306 (Fen-factor is not applicable because the vessel head is new (replaced in 2015), and it does not reach the 40 years of service life). Almaraz NPP: Almaraz Unit 1 (RPV head replaced in 1996): Design CUF 40 years: Vessel Head Flange & Vessel Flange Assembly: 0.9740. Bottom Head Juncture: 0.0090 (Design CUF 40 Environmental: 0.022). Vessel Wall Transition: 0.0100 (Design CUF 40 Environmental: 0.025). Almaraz Unit 2 (RPV head replaced in 1997). Design CUF 40 years: Vessel Head Flange & Vessel Flange Assembly: 0.9740. Bottom Head Juncture: 0.0070 (Design CUF 40 Environmental: 0.022). Vessel Wall Transition: 0.0100 (Design CUF 40 Environmental: 0.025).
ES-67 |  | Germany | Spain | 05. Reactor Pressure Vessels | 127/128 | The Trillo NPP experienced a corrosion-induced loss of material in the grooves that hold the inner and outer O-rings of the vessel closure head flange. How can this "loss of material" be characterized (pitting?)? Did any leakage between the two O-rings occur? Was there any root cause analysis? | email | After detecting loss of material traces, different analyses were performed to determine the origin of the findings. The analyses consisted in performing visual inspections, metallographic replica testing, and analysis of the cleaning agents. As a conclusion of these analyses it was determined that the findings were produced as a consequence of the surface sealing area being contaminated with particles before the silver O-ring was mounted and due to the remaining particles of the silver cleaning agents applied. In the following outage replicas from the sealing groove as well as samples from the O-ring was taken and the follow-up inspection showed no increase in the amount and depth of the already existing findings. As a result, the cleaning measures and agents to be used were analysed and the associated procedures updated.
ES-68 |  | Germany | Spain | 05. Reactor Pressure Vessels | 130 | While CSN considers environmentally assisted fatigue as a crucial aspect to be considered for license extension and some plants are approaching the end of their 40 year license, none of the licensees does address environmentally assisted fatigue. How will it be addressed for LTO? | email | Spanish utilities are addressing EAF for LTO. Up to date it has been considered the environmental usage factor for the period of LTO and the sentinel locations have been identified (using the EPRI guide TR-1024995). Before entering LTO, utilities will address the Usage factor through cycle counting or Stress based Fatigue as required by the AMP, ensuring the acceptance criteria are always met.
ES-69 |  | Germany | Spain | 07. Concrete containment structures | 153 | It is stated that during refueling outage R21 the perimeter joint of the containment building was found to be degraded. An addition to repairing the perimeter joint, liner thickness measurements were performed every 20 centimeters using ultrasonic techniques at the liner-concrete interface. Of the total 651 thickness measurements performed in the area of the joint, 4 of less than 4.5 mm were discovered (the nominal thickness of the liner is 6.5 mm). Of the total 415 thickness measurements performed in the area below the joint, 3 areas were found with G76thicknesses of less than 4.75 mm, which were also repaired. Why was this AMP not discussed to be improved in order to avoid degradation of liner thickness as low as 31% in the future? | email | It was a degradation due to an operational incidence, not due to an ageing mechanism.
ES-70 |  | Germany | Spain | 07. Concrete containment structures | 150 | In the report it is stated: “When an area or component does not meet the acceptance criteria, it may be declared as acceptable for continued service without repair if an engineering assessment determines that the indication or degradation is non-structural in nature or has no unacceptable effect on the structural integrity of the containment.” This point requires an additional explanation. How the area (component) can be declared to be acceptable if the acceptance criteria are not met? How the degradation can be non-structural in nature if this degradation occurred on the element (area) important to safety? | email | It could be declared acceptable after an engineering assessment if the safety function of the structure is still ensured. As stated in the ACI 349.3R code, a second set of acceptable conditions for observed degradation that have been determined to be inactive are set. These criteria are termed “second-tier”. Inactive degradation can be determined by the quantitative comparison of current observed conditions with that of prior inspections. If there is a high potential for progressive degradation or propagation to occur at its present or accelerated. rate, the disposition should consider more frequent evaluations of the specific structure or initial repair planning. An example of non structural degradation could be a lack of the liner coating without signs of corrosion.
ES-71 |  | Netherlands | Spain | 02. Overall Ageing Management Programme requirements and implementation | 02.2/p11 | The US-approach is used, but one reactor is from German origin. How is this coped with? | email | The US-approach establishes a high level criteria, so they can be applied to the German plant too. But, of course, specific details are considered in the analyses, like the SBO criteria, which is not applicable to the German plants due to all the emergency power supplies that they were designed with.
ES-72 |  | Netherlands | Spain | 02. Overall Ageing Management Programme requirements and implementation | 02.3/p13 | Some confusion about the Ageing Management Committee having tasks with respect to lifetime management. Is it true the Ageing Management Committee has a double role: overseeing ageing management and lifetime management? If so, is that considered to be the proper way to organise these things? | email | In Spain we use "lifetime" as a synonim of "ageing". We apologyse if it caused confusion in the understanding of the text and roles. So the ageing management committee has the functions detailed in the report, and summarising, the mail role is to coordinate all the activities that the different maintenance departments (electrical, I&C, mechanical, structures, chemical, etc.) have to perform in order to manage the ageing mechanisms and effects.
ES-73 |  | Netherlands | Spain | 02. Overall Ageing Management Programme requirements and implementation | 02.3/p21 | The EPRI documents listed are more than 10 years old. Have EPRI-developments thereafter been accounted for? Is Spain waiting for EPRI-updates? Are these 100% applicable to Trillo, without missing anything? | email | The EPRI reports listed are considered as initial reference, mainly due to its general scope and structure. EPRI reports do not include all kind of components, that is the case of Class 1 components, and other references have been also considered according to the plant design. Overall AMP is periodically updated therefore any new EPRI report or other relevant reference would be taken account. EPRI documents are aplicable to Trillo NPP, once the specifications of the Trillo specific materials and EPRI generic materials have been analysed and compared.
ES-74 |  | Netherlands | Spain | 02. Overall Ageing Management Programme requirements and implementation | 02.4/p36 | Is the IAEA International Reporting System (IRS) for Operating Experience used for collecting and sharing important ageing events? | email | The technical guides developed by the licensees where the operative experience analysis is explained, do not mention the IAEA as a source of information. In fact, CSN does not require to the licensees the IRS IAEA database as a source of information for the operative experience analyses. However, CSN analyses periodically (three times per year) the IRS database, and selects those that the licensees have to analyse.
ES-75 |  | Netherlands | Spain | 02. Overall Ageing Management Programme requirements and implementation | 02.4/p38 | Has Spain considered or is it considering to invite an IAEA SALTO mission in the coming years? | email | Yes. Vandellós II is preparing a SALTO mission by late 2018. During 2018, Almaraz NPP received an OSART Mission and Long Term Operation was one of the areas reviewed.
ES-76 |  | Netherlands | Spain | 03. Electrical cables | 3.1.1 / p.56 | The Tech.Spec. of the TPR states (in 3.1.1., p.15) that the scope of the AMP for cables should cover all relevant constituent elements, including the conductor, armouring/shield, and termination arrangements. This seems to be in contradiction to what is suggested here, namely that the AMP for electrical connections was not requested. For the sake of completeness, could the main components of the separate AMP for electrical connections be included? | email | TPR Tech.SPEc.point 3.1.1 refers to "cable termination arrangements". We understood that this is referring to "field cable connections", as splices or Raychem sleeves, that can be managed in the same way that its cable, but not to connections. As it is described on page. 55 "the electrical connections ageing management review is performed with respect to their inorganic or metallic materials and environments, and gives rise to an ageing management programme different and independent from the programme for cables, which is not part of the contents requested for this report". Anyway NPPs have developed an specific AMP based on XI.E.6 of NUREG 1801 (in page 63), this AMP is defined for LTO as "One-Time" Inspection, therefore, it is not a periodic activity. Otherwise, maintenance of electrical panels and cabinets as well as connections/connectors in active electrical components includes the periodic inspection of electrical connections in order to detect loosening, corrosion, dirty, and for some components, hot-spot by thermografy.
ES-77 |  | Netherlands | Spain | 03. Electrical cables | 3.1.2 / p.63 | Are the documents of the Main tools in the AMR process which are used to assess the performance also containing the acceptance criteria? Could you please give more info on these criteria? | email | Establishment of the acceptance criteria is not in the scope of the AMR. The acceptance criteria is developed in the specific AMP to manage the degradation mechanism and aging effects for which the AMP is developed. Additionally the acceptance criteria depends on the different test methods used. Anyway, some of the references in page 63 and 64 of the NAR, (eg: UNESA documents, IEEE-400-2001, IEC-270, EPRI 1020804, etc), have been used as references to determine the acceptance criteria.
ES-78 |  | Netherlands | Spain | 03. Electrical cables | 3.1.2 / p.68 | For the Trillo NPP: what is the 6y life expectancy of the cables based on, and how does that compare with the original life expectancy? Is this regular replacement now included as a policy in the plant's AMP? | email | The cables, are Pyrolid Ralocar with ETFE insulation and are subjected to very high temperature (until 99ºC) in normal operation. This temperature is the combination of the room temperature, self heating coming from the solenoid coil (normally energized) and hot spots (proximity to main steam pipes). As a consequence of a CSN inspection in 2003 on the cable EQ report, the licensee reevaluated the qualified life of the cables. Since then cables are changed every 6 years.
ES-79 |  | Netherlands | Spain | 03. Electrical cables | 3.1.3 / p.74 | For the TD-, PD-, and TDR-tests: is there any provision in the AMPs to identify trends from the historic inspections in order to detect progressive deterioration prematurely? | email | YES, as described in page 63, fulfillment of the 10 attributes established in NUREG-1800 is a requirement for all AMPs. Attribute 5 requires "Monitoring and trending" indicate that test results that are trendable provide information that can be used with the purpose to detect progressive degradation prematurely in order to take actions in advance. Anyway the question is explained in NAR description of the acceptance criteria for TD and TDR tests (pages 73 and 74).
ES-80 |  | Netherlands | Spain | 05. Reactor Pressure Vessels | Ch.5 | The information provided in this NAR in its chapter 5 on ageing management of reactor pressure vessels, is to a great extent qualitative. However in the Technical Specification for the NARs, the countries are requested to report in their NARs on the acceptance and action criteria for the various ageing phenomena. Apart from indicating those criteria, it is obvious that the NARs must discuss the compliance of the reactors with these criteria. Could you please provide this information? | email | The acceptance criteria are stablished by the requiered standard, rule or code. Cracking, loss of material: SCC, corrosion, leaks, fatigue (ASME XI IWB-3000). Loss of fracture toughness: neutron embrittlement (10 CFR 50.61 and 10 CFR 50 Appendix G). Cracking: fatigue (CUF < 1). For some specific cases, such as High Energy Line Break Locations, the criterion is CUF<0,1.
ES-81 |  | Netherlands | Spain | 07. Concrete containment structures | 7.1.3 | Reference is made to the leak test only. Does the programme also include a (periodic) pressure test? | email | Inspection on external surfaces of the containment structure are performed before, during and after the ILRT.
ES-82 |  | Netherlands | Spain | 07. Concrete containment structures | 7.1.3 | A question regarding trending of monitoring results. Is trending used to evaluate the monitoring programme and its frequency of activities like inspection? | email | Yes, as stated in the licencee inspection procedure, the frequency of the inspection is based on the trends assessment.
ES-83 |  | Netherlands | Spain | 07. Concrete containment structures | 7.3 | Has the regulator assessed the difference between the KTA 3401.4 and ASME XI and is it a choice of the operator of the KWU design to use a different programme than used for the Westinghouse plants? Is it the choice of the regulator to accept the use of different codes? | email | The KTA 3401.4, Steel Containment Vessels. Part.4: Inservice Inspections are required to Trillo NPP for the inspection of the metallic containment as it is a regulation from the country which the technology belongs. However the surveillance of the concrete structure surrounding the containment is based on American regulations (Maintenance Rule based on ACI 349.3R).
ES-84 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | table5.1 | Thimble guide tubes are referred several times. A detailed drawing could be useful to better understand their construction and location and also the observed wearing cases.f | expert group 2 | The thimbles are components used on Westinghouse PWR to monitor the neutron flux distribution. The BMI system incorporates guide tubes and Flux Thimble. The guide tubes are approximately one inch outside diameter stainless steel tubes which are attached to penetrations on the reactor vessel bottom head. The guide tubes extend from the reactor penetrations to the seal table which is located outside of the vessel. The BMI Flux is a long slender stainless steel tube, that passes through the guide tube, through the vessel penetration, through the reactor vessel lower internals, and finally extends to the top of fuel assembly. The thimble is subjected to reactor coolant on the outside surface and to atmospheric conditions on the inside. The thimbles are classified as ANSI Safety Class II. Westighouse analysed the Flux Thimble wear problem on the WCAP-12866, in which were established criteria for accurately measuring, predicting and dealing this issue.
ES-85 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | §5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | expert group 2 | The main goal of the AMP is maintaining RPV integrity. According to the Spanish ageing management rule IS-22 criteria, safety related elements that are required to continue operating during and after any design basis event that might occur in order to guarantee the integrity of the reactor coolant pressure boundary are within the scope of ageing management.
ES-86 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | 05.1.2 Ageing Assesment of RPV, page 112 | 5.1.2 In list of ageing effects and degradation mechanisms (DM) for Vessel shell the temperature embrittlement, tab. 05.2. is not included. Why? | expert group 2 | RPV thermal embrittlement is not identified as an ageing effect that requires management. The impact is not very significant according to EPRI guide MRP-80 that says “Research studies of thermal aging embrittlement of carbon and low alloys steels have been performed on reactor vessel steels, welds, and HAZ. Extensive experimental results show that the long term thermal aging embrittlement of reactor vessel steels and welds at PWR temperatures of 300ºC (572ºF) is very modest, with increase in DBTT on the order of 50ºC or less”. Thermal ageing could be considered as a non-limiting degradation, if it takes into account that the mean temperature in the RPV is 300ºC, that the highest temperature is in the upper part of the vessel and that all plants have replaced the vessel head (except Trillo NPP). However, this mechanism is partly taken into account in the irradiation surveillance programme, in which is analysed "beltline" and extended "beltline".
ES-87 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 112 | 5.2 The DM fatigue is not included for Vessel flange PWR, W, tab. 05.2. Why? | expert group 2 | It is a mistake. Fatigue is an ageing effect that requires management for the vessel flange in the RPV AMPs.
ES-88 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 114 | 5.6 tab 05.6: Why did you include Neutron Irradiation Embrittlement for inlet and outlet nozzles. The doses are so high at that region? | expert group 2 | The beltline region increased embrittlement over the operating period of the RPV as a result of accumulated neutron radiation from the core. The Appendix H to 10 CFR 50 provides the requirements to surveil changes in the fracture toughness properties of ferritic materials in the beltline due to exposure to neutron irradiation and thermal environment. As a result of changes made to the plant license, including power uprates, increased operating periods due to license renewal, modified fuel design, neutron fluence methodology updates, and fuel placement within the core, the physical region of the reactor vessel with fluence that exceeds this level can expand. The result is that changes in fracture toughness properties resulting from neutron embrittlement may occur in materials where the effects of radiation damage may not have been previously considered when developing the P-T limits for the vessel. It was not considered that the effects of structural discontinuities for a material with a lower reference temperature (such as a nozzle with a lower neutron fluence) may result in more restrictive allowable P-T limits than those for the vessel shell material limiting material with a higher reference temperature. Thus, according to NRC Regulatory Issue Summary (RIS) 2014-11, the development of P-T limits for the reactor vessel must consider not only the vessel shell material with the highest reference temperature but also other vessel materials with structural discontinuities. In the Spanish plants that have requested the long-term operation (Vandellós II and Almaraz), they have re-analysed the P-T curves considering the “extended beltline”, following the previous RIS mentioned.
ES-89 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | 05.1.3 Monitoring …, page 117 | 5.8 Tab 05.8: no inspection of base metal included. How did you taken into account experience from Tihange and Doel? For all your reactors generally? | expert group 2 | All available documentation about the manufacturing of the reactor, scope and results of pre-service and in service (UT) was checked with an acceptable outcomes. However, taking into account that this material could theoretically be affected by hydrogen flakes, although the manufacturing process is different to D&T, Trillo NPP has planned to inspect the base metal area during the next refueling outage in spring 2018, by UT techniques with capability to detect these flaws. For the rest of the NPPs the shells have been manufactured by material plates, specified by American Society for Testing and Materials (ASTM) SA-533 Grade B, Class 1, which are joined by means of longitudinal and circumferential welds. In case of Santa María de Garoña NPP, at the end of 2014, different samples of base material from all RPV rings were examined by UT from the inside with both straight beam and angle beam (45º), using recording and acceptance criteria, according to manufacturing code (ASME III). No remarkable indications similar to flakes were found. Currently Santa María de Garoña NPP is in the definitive shutdown situation.
ES-90 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 117 | Do you postulate under surface crack in you PTS calculation? I ask because you do not count a clading as safety relevant | expert group 2 | No. PTS is calculated with the fluence at the surface (10 CFR 50.61) and the cladding is not taken into account.
ES-91 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 122 | The calculations relating to neutron embrittlement of the vessel fulfil the definition of “Time-limited Ageing Analysis” - which kind of calculation exactly? (Fluences, Tka, others?) | expert group 2 | For PWR plants TLAA are: neutron fluence, Upper Shelf Energy, Adjusted Reference Temperature, Pressure-Temperature Limits, Low Temperature Overpressure Limits and Pressurised Thermal Shock. For BWR the plant TLAA are: Neutron Fluence, Upper Shelf Energy, Adjusted Reference Temperature, Pressure-Temperature Limits, RPV Circumferential Weld Inspection Relief, RPV Axial Weld Failure Probability and, RPV Core Reflood Thermal Shock Analysis. The surveillance programmes are based on 10 CFR 50 Appendix H, ASTM E-185 and NRC RG 1.99 rev. 2. The neutron fluence calculation is made according to NRC RG1.190.
ES-92 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 123 | 5.1.3 How were preselected class 1 components for monitoring of transients? | expert group 2 | The EPRI guide “Environmentally Assisted Fatigue (EAF) Screening: Process and Technical Basis for Identifying EAF Limiting Locations” TR-1024995 has been used for selecting class 1 componentes.
ES-93 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 123 | Do you use environemental factor in fatigue calculation? | expert group 2 | Yes. Environmentally assisted fatigue degradation should be addressed in ageing management programmes developed for license renewal. To assess the impact of the reactor coolant environment should include a sample of critical components, as a minimum those selected in NUREG/CR-6260 and others additional component locations selected by the plant. All of these locations have been named as "sentinel locations", which have been identified using the EPRI guide TR-1024995. This sample of critical components is evaluated applying environmental correction factors to the existing ASME Code fatigue analyses. NUREG/CR-6909 is used to calculate correction factors for the CUF taking into acount the environmental effect.
ES-94 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 125 | When water chemistry parameter is outside the limits accepted by the industry - do you assess possible effect of parameter value to aging of primary circuite components? | expert group 2 | Yes. A revision of any chemistry limit violation is required after such event . Depending on the inpurity, the abnormal value and the time over this limit, remedial actions are required by the applicable procedures. The actions levels, time and type of action are based on the recommendations given in: • EPRI 1014986, PWR Primary Water Chemistry Guidelines. • BWRVIP-190 (EPRI 1016579), BWR Vessel and Internals Project: BWR Water Chemistry Guidelines. • NUREG/CR-6001, Aging Assessment of BWR Standby Liquid Control Systems. • VGB-R 401 J, Richtlinie für das Wasser in Kernkraftwerken mit Leichtwasserreaktoren. Dritte Ausgabe (For Trillo NPP).
ES-95 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 126 | What was remedial action after cono-seals leakage? | expert group 2 | After detecting the accumulation of boric acid on the insulation of the vessel head, it was determined that the leakage was originated from the cono-seal. The affected surfaces were cleaned and the isolation of the reactor vessel head removed to facilitate the performance of inspections and to examine the outer surface of the reactor vessel head. As a result of these activities no degradation due to boric acid was detected. A design modification was performed in order to improve the seal capacity of the component in order to avoid future leakages. The scope of the design modification included the change of the male flange, gasket and weld to reinforce the seal.
ES-96 |  | RPV expert group | Spain | 05. Reactor Pressure Vessels | page 126 | In no case the leaks have been considered unacceptable - I do not understand sentece. So leaks were acceptable? | expert group 2 | It is a mistake. Leakages through pressure boundary are not allowed. Spanish NAR wanted to say that the leaks detected up to now have not been through pressure boundary, and after evaluation, they have been considered acceptable (i.e. leakages through a bolted joint coult be acceptable if the external surface of a component suffering the leakage is not afected by boric acid corrosion). However, all leakages have been repaired.
ES-97 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 136 | In accordance with Technical Specification for chapter 7.1.1. What are the main functions of the structures? You have described some of the structures but not all of them. | expert group 4 | It's understood that a description of the functions of all the elements included in 07.1.1. are requested. According to this assumption, the information associated with the structures has been analysed and as a conclusion the only missing function that was identified is the concrete structure of the Trillo NPP. The intended function of Trillo NPP concrete structure is to provide shelter/protection to safety-related components (in this case, the metallic containment).
ES-98 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 136 | In accordance with Technical Specification for chapter 7.1.1, can you add principle drawings? | expert group 4 | Licensee property.
ES-99 |  | Concrete containment PCPV expert group | Spain | 02. Overall Ageing Management Programme requirements and implementation | 19 | In chapter 02.3.1. the scope of the overall AMP is described. In the AMR process its described how the structures and components are grouped in two levels. Could you give an example how civil structures are grouped in both levels? | expert group 4 | First Level : Reactor building structure (except Primary Containment) Second level: Walls and Floors and bedplate (concrete) Platform, stairs (structural steel components) Masonry walls Concrete area at location of support elements Supports elements (steel)
ES-100 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 140 | In accordance with Technical Specification for chapter 7.1.2, can you describe the establishment of acceptance criteria related to ageing mechanisms? | expert group 4 | Each plant establishes its own acceptance criteria based on their applicable regualtions, basically ACI 349.3R.
ES-101 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 140 | Has results from the R&D-program been implemented in the your ageing assessments of concrete structures? If yes, how has results been implemented? | expert group 4 | R&D programmes have not been implemented yet in the ageing assessment for concrete structures. TLAA for pre stressing systems will be implemented in the future.
ES-102 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 140 | Do the AMPs in chapter 07.1.2 refer to the inspection activities and acceptance criteria mentioned in chapter 07.1.3? | expert group 4 | Yes.
ES-103 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 159 | On page 159 follows “Also relating to the surveillance exercises performed at Ascó NPP, in response to the detection in certain cases during the first surveillances of a significant loss of protective grease from the tendons, the performance of a study was required in order to analyse the impact of the grease filtering via the fissures on the structural performance of the concrete. This study was performed by the Polytechnic University of Catalonia in 1993. Subsequently, in the year 2000, a non-destructive testing campaign was performed using georadar techniques on the outer containment wall at Ascó 1 NPP to detect and locate possible grease accumulation from the pre-stressing system.“ What did the results show? | expert group 4 | The report ordered by the licensee concluded the following: -The vertical cracks were caused by the concrete retraction in the outer wall. -The grease leaked due to the fact that tendon ducts were not perfectly watertight and other paths which were more permeable were sealed (e.g. concrete hollows, concrete joint…). -The grease has no impact on the chemical characteristics of the concrete and very low incidence on the physical properties. -The grease flux is limited through the cracks and not through the sound concrete. -The presence of water in the grease does not produce the corrosion of the rebars and do not modify the steel properties. -The presence of grease has not influence in the steel-concrete bond.
ES-104 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | Table 7.1 | Table 7.1 - Table 7.1 does not include steel reinforcement. Please clarify. | expert group 4 | The rebars of the reinforcement are included in the concrete components item of Table 07.1.
ES-105 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 140 | Ageing assessment of concrete structures - On top of the inspections stated in Section 7, do the Licensees carry out plant walk downs and monitoring on a frequent basis? | expert group 4 | Walkdown inspections are also performed under the seismic margin assessment methodology.
ES-106 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 140 | Ageing assessment of concrete structures - Please provide more information on the the liner inspections and leak detection tests for the BWR primary containment. | expert group 4 | Cofrentes NPP has a metal primary Containment. According to 10CFR50 Appendix J, at Cofrentes NPP containment leak rate tests are performed periodically, in order to “assure that leakage through these containments or systems and components penetrating these containments does not exceed allowable leakage rates specified in the technical specifications and; to assure that the integrity of the containment structure is maintained during its service life." Three types of tests are performed: Type A tests for determining the overall primary containment integrated leakage rate at the loss of coolant accident peak containment pressure. Type B tests are intended to detect local leaks and to measure leakage across each pressure-containing or leakage-limiting boundary of containment penetrations. Type C tests are intended to detect local leaks and to measure leakage across containment isolation valves installed in containment penetrations or lines penetrating containment. Appendix also requires a general inspection of the accessible interior and exterior surfaces of the containment structure and components be performed prior to any Type A test. General Visual examinations are performed in accordance with the ASME Section XI, Subsection IWE for the Metal Containment and, in accordance with the ASME Section XI, Subsection IWL, for the case of concrete accessible surfaces of concrete around the suppression pool, as primary containment, and the concrete shield building and dome as the secondary containment.
ES-107 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 145 | Ground Movement Surveillance Manual - Are there any electronic monitoring points or is the data adquired by scheduled surveys? If so, how often these surveys take place? | expert group 4 | There are not any electronic monitoring devices. The data is adquired via topographic levelling of the control points every six months.
ES-108 |  | Concrete containment PCPV expert group | Spain | 07. Concrete containment structures | 157 | Cofrentes nuclear power plant - Regarding the alkali-silica reactions, could you provide more information on the new monitoring activities? | expert group 4 | In 2012 Cofrentes NPP carried out some investigations in order to verify if the surface cracking that exist in some small areas of the structure surface in contact with the environment could be due to the Alcali-Silica reaction (ASR). The initial investigation did not provide a clear assessment regarding the degradation of the concrete, recommending some additional investigation to be performed. The initial investigation was performed by AIDICO Institute. AIDICO was closed later on and it was not possible to continue with the second phase of the investigation. During 2017, CIMNE was contracted to continue with the AIDICO recommendations and to finish the pending investigation. A national specialist in the area, is leading this project. The status of the project is the following: • The AIDICO report has been revised and some gaps have been found regarding the record details of the test performed. There is no detailed information regarding the process or protocol used for the test. In the pictures included in the report, it is no clear evidence of presence of silica gel, as it is stated in the conclusion. • Cofrentes NPP life management structure database has been revised to check the photography of the surface cracking pattern found in the some NPP structures, and made a plan for in-situ inspection. The cracking pattern found in the existing photos is smaller than the one produced by ASR and it is probably due to shrinkage of the surface cement. Nowadays licensees are preparing in-situ inspection to define the location where additional testing proposed by AIDICO will be performed and to prepare a complementary testing to produce an assessment regarding the existence of ASR degradation in Cofrentes NPP structures. It is foreseen to finish this analysis by mid of 2018.
ES-109 |  | Concealed pipework expert group | Spain | 04. Concealed pipework | General | Are methods of contactless diagnostics that allow assessment of inaccessible sections used at Spanish NPPs (methods of contactless diagnostics for underground piping: contactless magnetometric diagnostics method; acoustic tomography method. These methods reveal loss of integrity of piping and do not require direct access to piping external surface. Diagnostics is carried out from ground surface above the piping. 100% of piping from all observation groups is inspectable). This information should be added to the Report or corresponding clarifications might be provided as an answer. | expert group 5 | No. Currently no contactless diagnostic assessment is carried out in any Spanish NPP for concealed piping systems. Some methods such as Guided Waves have been tested at some Spanish plants, however, there is no practical experience with the techniques mentioned in the question. According to the information gathered in the last inspections of the CSN, the CSN has no constancy of performing magnetometric diagnosis without contact or acoustic tomography in the Spanish NPP. Inspection is only carried out as an indirect method for piping run indications at the Almaraz and Trillo plants. In any case, the LR-ISG-2015-01 indicates in its discussion section on the inspections in table XI.M41-2 that the NRC does not give credit to non-direct inspections as the NEI-09-14 does, and mentions the example of guided wave exams. The guided ultrasonic waves have limitations such as the interpretation of the data that depends on the examiner, the difficulty of detecting small defects (pitting) and the validation of the procedure. The diagnostic methods are used for both detection and monitoring. In the section of the model program on detection it only indicates direct visual inspections, and in the monitoring and trends section it only indicates that trends of the potential and amperage measurements will be made to identify changes in the effectiveness of the cathodic protection system or coatings; also that the activity of the jockey pump will be monitored, the leakage rates in case of leakage tests, and the thickness measurement. TABLE 04.05 CORRECTED. There is a mistake in table 04.5 regarding to Trillo NPP (TRI) that also performs the inspection by run indications and inspection of accessible sections (manholes and others). So there have to be two Xs in Trillo NPP in the line "e) Visual inspections of accessible sections" and in the line "h) Inspection for piping run indications".
ES-110 |  | Cables expert group | Spain | 03. Electrical cables | 68 | Who are the third-party certification organisations and what are their responsibility and duties in relation with AMP on cables | expert group 3 | As we explain in NAR chapter 02, pages 35-36, in Spain there are not any third-part certification organization acting in relation with ageing management activities. Referring to cables AMP, licensees are responsible for developing and implementing de AMP activities. Anyway, external organizations (ie: Tecnatom) are normally subcontracted for implementing the tests and inspections on the cables.
ES-111 |  | Cables expert group | Spain | 03. Electrical cables | 60, 76, 78 | Among the methods for the inspection of inaccessible cables, is the boroscopic method used in practice? | expert group 3 | No. Spanish cable AMPs do not include presently the iluminated boroscopic method for inspecting inaccesible cables.
ES-112 |  | Cables expert group | Spain | 03. Electrical cables | 56 | For the cables and connections that are under the AMR but without environmental qualification (non EQ cables), the "Plant Spaces Approach" is used. To which extent this is different than for the EQ qualified cables? | expert group 3 | EQ cables are identified inside the Equipment Environmental Qualification Program, and not inside the OAMP. Scope of EQ cables is defined in 10 CFR 50.49 and its ageing is managed by the environmental qualification maintenance activities. During the design service life they do not need an AMR process as defined in the OAMP for the NON- EQ cables. Independently of the afforementioned statement and as it is explained in NAR page 59, Spanish plants have included the EQ cables inside its AMPs to face the uncertainties in their qualified life highlighted in recent international R&D programmes.
ES-113 |  | Cables expert group | Spain | 03. Electrical cables | 57 | Could you please provide examples of the types of cables (power and instruments) are subject to containment atmosphere that are considered useable for 60 years? | expert group 3 | As a result of the plant spaces approach, and depending on each Spanish NPP, some NON-EQ power, control and instrumentation cables inside containment, with different insulation materials as EPR, XLPE, ETFE or Kapon have been considered useable for 60 years. EQ cables subject to containment atmosphere in the scope for LTO must be analysed by a TLAA. Results of such analysis could show, for some cables, a life over 60 years.
ES-114 |  | General AMP expert group | Spain | 02. Overall Ageing Management Programme requirements and implementation |  | Regarding chapter 02 the Spanish report is very well structured containing good amount information about country's Overall AMP and is following the technical specifications. | expert group 3 on other topics / expert group 1 | Ok.
ES-115 |  | General AMP expert group | Spain | 02. Overall Ageing Management Programme requirements and implementation | 13 | Status of the Ageing management organisation is not clear. Is it a Committee or a permanent part of the organisation (e.g. section, division, etc.) or a matrix type organisation, i.e. composed from experts of other sections, divisions? Please clarify. | expert group 3 on other topics / expert group 1 | The Ageing Management Committee is a matrix type organisation, composed from experts of other sections (I&C maintenance, electric maintenance, mechanical maintenance, etc) that have also responsibilities on ageing management.
ES-116 |  | General AMP expert group | Spain | 02. Overall Ageing Management Programme requirements and implementation | 22 | In the figure, does the text of the box "Identification of S&C environment(s)" include loading as well or does it refer only to'environmental' conditions such as temperature, humidity, radiation field? It the latter is the case where are the loading conditions taken into account? | expert group 3 on other topics / expert group 1 | In that figure 02.2, "identification of S&C environment" means that it has to be defined what environment is in contact with the S&C materials: temperature, humidity and/or radiation. For example, in the case of the containment structure, the inner part of the building is in contact with "Air – indoor controlled" and the outer part of the building is in contact with "Air – outdoor ". And in the case of a mechanical system, the inner part of a piping (for example) is in contact with "Treated water" and the outer part is in contact with "Air – indoor controlled" (if the atmosphere of the building is treated with a HVAC system). Additionaly, in the case of cranes, loading can be considered a environmental parameter, because the number of cycles of maximum load is crucial to determine the crane residual life.
ES-117 |  | General AMP expert group | Spain | 02. Overall Ageing Management Programme requirements and implementation | 34 | Erosion-corrosion program: even thouigh UT is a volumetric examination when looking for flaws, the wall-thickness measurement with UT is just a simple distance (precisely time of flight) measurement only. I would not call it volumetric type examination. | expert group 3 on other topics / expert group 1 | From Spanish point of view, UT are always considered as volumetric examinations.
ES-118 |  | General AMP expert group | Spain | 02. Overall Ageing Management Programme requirements and implementation | 38 | Assessment of TLAAs: third bullet says that it is possible that a former TLAA is not necessary for the extended service life? Is the meaning of this bullet? | expert group 3 on other topics / expert group 1 | The meaning of this third bullet is that, one possible method to solve a TLAA is that a specific AMP manages the potential ageing mechanisms and effects that there could be during the LTO period. For example: An electric cable qualification report (former TLAA) that results in a qualified life bigger than the LTO period
ES-119 |  | General AMP expert group | Spain | 02. Overall Ageing Management Programme requirements and implementation | 45-46 | CSN gives a list of positive aspects (strengths) of the LMP development process (I guess it should be AMP) and concludes that it is adequate. However no weaknesses are shown here. Is there any weakness in implementing AMP in Spanish plants? | expert group 3 on other topics / expert group 1 | After comparing with other countries reports, we could consider more research related to Ageing Management topics could be mentioned as a challenge or area for improvement.
ES-120 |  | EC | Spain | 09. Overall assessment and general conclusions | - | The report's second chapter follows the structure of WENRA technical specifications. Sub-topics are not clearly marked, but given the added complexity of the number of different entities involved this is understandable. The substance of the report is meaningful and coherent. A number of good practices can be pointed out. Given the comparatively long period for which aging management requirements have been in place, it would be appreciated if the regulator could provide more plant specific feedback resulting from CSN's assessment activities. |  | From CSN's assessment activities it could be mentioned the following: - Scoping updating: EQ cables have been included within the scope of AMPs as a consequence of R&D programmes results. - AMP activities improvements: Environmental conditions surveillance programmes have been implemented in each plant to verify the actual conditions to be used for service life management (TLAA on environmental qualification). - AMP activities implementation: During the CSN inspections performed every two years, the evolution of the implementation of activities and their results have been reviewed. - AMP updating: CSN has required the Spanish plants the implementation of new standards requirements, for example, new requirements in GALL revision 2 (2010) and the subsequent LR-ISG developed by NRC.
ES-121 |  | EC | Spain | 02. Overall Ageing Management Programme requirements and implementation | 14 | What is the typical period between meetings of the Ageing Management Committee for each of the NPPs? |  | The typical period between meetings varies from plant to plant but, in any case, it is between 3 to 6 months. Usually in June, an Ageing Management Committee meeting is called in order to approve the “Annual Ageing Management Activities Report” that must be sent to the CSN.
ES-122 |  | EC | Spain | 02. Overall Ageing Management Programme requirements and implementation | 19 | Sub-section e) of 2.3.1 'Scope of the overall AMP' is not adequately addressed. References to the applicable quality assurance manuals as well as examples relevant to the AMP application would be appreciated. |  | The ageing management for the SSC included in the overall screening and the activities of engineering analyses are safety related, thus the Nuclear Quality Assurance Requirements apply. As it is stated in the text, the OAMP activities are subject to the plant's quality assurance manuals. The specific activities for quality assurance regarding the OAMP are settled on periodic inspections, audits and procedure revisions, covering any activity of the programme.
ES-123 |  | EC | Spain | 02. Overall Ageing Management Programme requirements and implementation | 37 | Is the AMR process triggered for each incorporation of a new S&C in the scope of OAMP or the modification is taken into account when the AMR is periodically run? |  | In general, a modification is taken into account when the OAMP (and therefore the AMR) is updated as a consequence of all design modifications implemented in a period of time. Additionally, Cofrentes, Ascó and Vandellós II analyse during the design stage, if the design modification impact or not on the OAMP.
ES-124 |  | EC | Spain | 02. Overall Ageing Management Programme requirements and implementation | 37 | What is the period between routine AMR processes for each of the NPPs? |  | The AMR process is updated in the following four situations: 1. Changes in the scope of the AMPs as a consequence of plant design modifications. 2. Operative experience analyses results, that conclude in new ageing mechanisms and/or effects not considered previously. 3. Changes in rules and standards taken into account in the AMR process. 4. R&D programmes results related to ageing management. In the last edition of the Spanish ageing management rule IS-22, establishes a maximum of 4 years to update all the ageing management process as a consequence of the aforementioned situations.
ES-125 |  | EC | Spain | 02. Overall Ageing Management Programme requirements and implementation | 42 | The list of tasks performed within the framework of OAMP in Almaraz and Trillo does not provide clarity on which operator(s) performed which of the tasks. |  | Almaraz and Trillo are managed by the same electric company. So they started their Overall Ageing Management Programmes more or less at the same time, and they have been developing their activities at the same time. That is the reason why the tasks are mentioned together to Almaraz and Trillo. However, in the last paragraph where the activities of updating and reviewing are explained, they have been done in different dates for each NPP, since Almaraz finished a little bit earlier.
ES-126 |  | EC | Spain | 02. Overall Ageing Management Programme requirements and implementation | 46 | How did CSN evaluate the OAMP effectiveness indicators created by the operators? If those indicators vary between NPPs does CSN plan on issuing guidance on unifying the practice? |  | In each inspection performed by the CSN to each licensee every two years, effectiveness indicators and their evolution are observed. The reasons of those AMP having the lower indicators are discussed with licensees. Up to date, CSN does not have thought about requiring to licensees to have the same indicators.
ES-127 |  | EC | Spain | 02. Overall Ageing Management Programme requirements and implementation | 10,11 | How does the regulator's assessment of LT-OAMP implementation affect the decision for LTO operating permit? |  | As it is said in the pages to which the question is refering, before starting the LTO period licensees have to develop an Integrated Plant Assessment (IPA) that has to be evaluated by the CSN, so all the conclusions, deviations and assessments achieved could be subjected to be a condition to the permit for the LTO. In the evaluation performed by the CSN, both scope, screening, ageing management review, materials, environments, ageing effects and mechanisms and the TLAA are evaluated to check the completeness and the results of the evaluations.
ES-128 |  | EC | Spain | 02. Overall Ageing Management Programme requirements and implementation | 39,40 | References and examples of specific indicators for the effectiveness of the OAMP at each NPP would be appreciated. Also the link between activities defined in AMPs and the OAMP effectiveness assessment needs to be elaborated on. |  | For each Ageing Management Programme an "AMP tracking report" is prepared periodically. The "AMP tracking report" summarizes the results of AMP activities and includes the AMP effectiveness indicator that assesses its effectiveness taking into account the three following aspects: 1) Activities results: If all foreseen activities have been performed and no significant ageing effects have been detected, the maximum indicator value is achieved, otherwise postponed activities and/or detected ageing effects will reduce the indicator value. 2) Operating Experience: Any internal or external experience that affect the AMP could reduce the indicator value. 3) Commitments: When the implementation of an enhancement proposal or other commitment that affects the AMP is delayed, the indicator value is reduced. The indicator trend is also evaluated every year. Almaraz and Trillo NPPs measure AMP effectiveness on a qualitative basis.
ES-129 |  | EC | Spain | 03. Electrical cables | 66 | Are there cable deposits at any plant, or is sampling for laboratory ageing follow-up tests taken only from cables that have been in operation? |  | Only one of the Spanish NPPs has cable deposits that can be used; for the rest of the plants the samples have been taken from cables that have been in operation.
ES-130 |  | EC | Spain | 03. Electrical cables | 66 | Can you describe in more detail the taking of samples from naturally aged cables? (How long samples, their replacement.) |  | The samples have been selected according to different criteria in order to collect a representative population. Once that these criteria have been established, the NPPs have investigated, through the routing cable DB, all of the cables in compliance with those criteria and have selected them to be taken from the plant. The most accesible cables were selected to be recovered through proper identification close to the access point of cables in trays. Cables taken from the plants, to be used in the PCI Programme ES-27 (see Spanish NAR page 66) have lenghts varying from 4 to 30 meters.
ES-131 |  | EC | Spain | 03. Electrical cables | 81-82 | Please add text to the table captions 03.2 and 03.3 |  | Tables 03.2 and 03.3 of the NAR identify the specific insulation material of the power (MV, LV), instrumentation and control and COAX/TRIAX cables included in the scope of the cable AMP,s for each one of the Spanish NPP.
ES-132 |  | EC | Spain | 05. Reactor Pressure Vessels | Chapter 05.1.3, page 123 | Correct the text "At the date of editing this chapter, the calculations depending on an estimation of creep over time have been solved for the Vandellós II and Almaraz plants, the fundamental conclusions being as follows:". It should be "At the date of editing this chapter, the calculations depending on an estimation of neutron fluence over time have been solved for the Vandellós II and Almaraz plants, the fundamental conclusions being as follows:". The Spanish version of the national report is correct. Only the English version needs to be corrected. |  | Yes, it is a translation mistake.
ES-133 |  | EC | Spain | 07. Concrete containment structures | 157 | At Cofrentes NPP, in 2012 traces of ASR in the early stages of development were detected. It is stated that new monitoring and assessment activities are foreseen. Has any further inspection, monitoring or assessment been performed in follow-up to these findings in the 5-6 years since the discovery? |  | In 2012 Cofrentes NPP carried out some investigations in order to verify if the surface cracking that exist in some small areas of the structure surface in contact with the environment could be due to the Alcali-Silica reaction (ASR). The initial investigation did not provide a clear assessment regarding the degradation of the concrete, recommending some additional investigation to be performed. The initial investigation was performed by AIDICO Institute. AIDICO was closed later on and it was not possible to continue with the second phase of the investigation. During 2017, CIMNE was contracted to continue with the AIDICO recommendations and to finish the pending investigation. A national specialist in the area, is leading this project. The status of the project is the following: • The AIDICO report has been revised and some gaps have been found regarding the record details of the test performed. There is no detailed information regarding the process or protocol used for the test. In the pictures included in the report, it is no clear evidence of presence of silica gel, as it is stated in the conclusion. • Cofrentes NPP life management structure database has been revised to check the photography of the surface cracking pattern found in the some NPP structures, and made a plan for in-situ inspection. The cracking pattern found in the existing photos is smaller than the one produced by ASR and it is probably due to shrinkage of the surface cement. Nowadays licensees are preparing in-situ inspection to define the location where additional testing proposed by AIDICO will be performed and to prepare a complementary testing to produce an assessment regarding the existence of ASR degradation in Cofrentes NPP structures. It is foreseen to finish this analysis by mid of 2018.
ES-134 |  | EC | Spain | 07. Concrete containment structures | 148, 150, 151, 153 (154) | On pages 148, 150 and 151, there is a description of the procedure related to the consideration of areas that are inaccessible for inspection. In case conditions of degradation are detected in accessible areas that may indicate the presence or result of degradation in inaccessible areas, an acceptability assessment shall be performed. i) Have there been cases in which this procedure has had to be put into practice? ii) In case the assessment cannot rule out the possibility of degradation in the inaccessible area, what are the possible actions? Is there any experience of such cases? iii) The experience described on page 153 related to the refuelling outage R21 at Asco NPP unit 1 where the perimeter joint of the containment building was found to be degraded would seem to be a case in point (the experience at Vendellos II in outage R14 on p154 may be another case). Since liner material loss was detected at several places accessible to inspection and which required repair, how could it be assured that no similar or worse material loss has occurred at the inaccessible lower elevations of the liner where water could have entered? |  | i) Yes. It is usually used in the case of cubicles with no access due to radiological reasons or in pump pits full of water. ii) Opportunistic direct inspections. iii) In that case when lower elevations were degraded, there were indications at higher elevations.
FI-1 |  | Poland | Finland | 08. Pre-stressed concrete pressure vessels (AGR) | 91 | 1. Have you had a special registration tool or law requirements for reporting non-conformances and safety concerns issues during construction period before those construction errors have happened? If so please give details what kind of requirements were used. What was the role of RB in decision making after events? | Website | Question concerns chapter 7.1.4, page 88 (preventive and remedial actions for concrete structures) and especially construction period of Olkiluoto 1 and 2 (1974 - 1980). According to guide YVL 1.4, in force during the construction, it was required that non-comformancies must be recorded and followed during construction and STUK (regulatory body) was then and is still responsible for the oversight of the construction works from radiation and nuclear safety point of view.
FI-2 |  | Bulgaria | Finland | 07. Concrete containment structures | chapter 7.1.2 | In conjunction with chapter 7.1.2 ASSESSMENT OF AGEING OF CONCRETE CONTAINMENTS, please, clarify the acceptance criteria related to the different ageing mechanisms. | Website | OL1/OL2/OL3: Ageing mechanisms and circumstances are followed periodically and corrective measures are assessed case by case. Some ageing mechanisms have specific acceptance criteria, for example loss of prestressing forces and leak tightness of the containment. Loviisa: There are no clear acceptance criterias defined for every different ageing machanisms. The inspection guideline Y-05-00005 defines criterias for reporting and decision making for repair is based on engineering judgement.
FI-3 |  | Bulgaria | Finland | 07. Concrete containment structures | chapter 7.1.2 | In conjunction with chapter 7.1.2 ASSESSMENT OF AGEING OF CONCRETE CONTAINMENTS please, clarify the key standards and guidance used to prepare SSC Aging Management Program. | Website | OL1/OL2/OL3: Standards are ASME XI, ASME III div 2, IAEA-TECDOC-1025, IAEA guide series, for OL1 and OL2 also US nuclear regulatory guides. Fortum: National regulatory guidelines (STUK YVL-guidelines, especially YVL A.8 and YVL E.6).
FI-4 |  | Bulgaria | Finland | 02. Overall Ageing Management Programme requirements and implementation | p. 13 | In chapter “2.3.3 Monitoring, testing, sampling and inspection activities”, subchapter “Inspection programme (ISI‐program)” is stated that “Loviisa plant has ISI‐programmes for both pipelines and components. They are both based on ASME XI requirements and are prepared for ten year periods.” Would you give more information about the reasons (or benefits) for using the ASME code instead of the codes used for manufacturing (design) of the equipment? | Website | Fortum: Using the ASME is the basic authority requirement in Finland. (YVL-E.5 req. 302: The basic requirement level of in-service inspections shall be the standard ASME Boiler and Pressure Vessel Code, Section XI, Rules for In-service Inspection of Nuclear Power Plant Components, Division 1, (ASME Code, Section XI) [ 4]. Deviations from the Code shall be justified and it shall be demonstrated that a corresponding level of safety and reliability can be achieved.)
FI-5 |  | United Kingdom | Finland | 05. Reactor Pressure Vessels | General | Throughout – Some RPV nozzles have repair zones with Inconel. What is the typical extent of these repairs? What inspection is performed to confirm lack of degradation? | Website | TVO: Cover the internal circumference with material that is resistant to IGSCC. Normal inspections were performed to determine surface breaking and internal inspections. Fortum: In Loviisa RPVs there is no inconel material used.
FI-6 |  | Slovak Republic | Finland | 02. Overall Ageing Management Programme requirements and implementation | Pages 16 and 99 | Chapter 2.7 last section and chapter 9.1 last section suggest postponed decision of licensee to renew I&C and electrical equipment which can lead to a situation that the licensee will not be capable to demonstrate the safety of continued operations to the regulator or can lead to different understanding of required scope between them. Could Finland explain this statement in more detail? | Website | STUK: If an unavoidable modernisation or renewal project is delayed for a SSC which has a bad operability history, it is very likely that physical ageing will continue. Sometimes obsolescence may become apparent, too. In such cases it will be more open to interpretations how to demonstrate the operability of the SSC.
FI-7 |  | Slovak Republic | Finland | 05. Reactor Pressure Vessels | Pages 63, 64 | There are some pending issues concerning indications: - Loviisa 1 RPV low pressure safety injection (TH) nozzle - Olkiluouto 1 and 2 safe-end welds of systems 312 (feed water), 323 (reactor core spray) and 321 (shut down cooling) What is the timetable for inspection of all possible indications and is a repair technology prepared for these indications? | Website | TVO: The time schedule depends on the inspection results. For the time being inspections are performed every second year. A propriety internal repair has been applied and is available for future repairs. Fortum: TH-nozzle inspections will be continued in 2018, no repairs have been considered yet.
FI-8 |  | Slovak Republic | Finland | 02. Overall Ageing Management Programme requirements and implementation | Pages - general | According to STUK Guide YVL A.8 Ageing Management of Nuclear Facility item 503 a 504 licensee shall establish baseline data from fabrication, pre-service inspections and sampling. Could Finland give short information on how was this requirement managed by Olkiluouto 3 staff and who is in possession of this kind of data? | Website | STUK: Baseline inspections and tests are to provide comparative data about the original condition of the SSCs inspected within the scope of inspections and tests during operation. In OL3, for example baseline data of piping NDT, performance of valves and pumps have been recorded for later reference. In Finland it is the licensee who is in charge of managing the recorded data and reporting to STUK any significant changes from the baseline.
FI-9 |  | Slovak Republic | Finland | 01. General information | Pages - general | The National Assessment Report indicates a lot of collected data and information in the field of ageing management. Is there licensee´s ageing management database in place? How is it structured? Does it include acceptance criteria and trending to decide on the required steps for corrective actions? | Website | TVO does not have only one database for ageing. Most important active component ageing management information is in maintenence system and all ageing related failure information is in maintenance system. RPV and pipelines material and possible degradation mechanisms are in a separate database. Trending has done case by case. Fortum: Database is in place, but acceptance criteria and trending is not fully comprehensive. Process for corrective action exists.
FI-10 |  | United Kingdom | Finland | 04. Concealed pipework | 30-31 | Section 4 explains there is not much buried pipework, and that where it is fully concealed, it is embedded in concrete and covered by an ageing management programme. Compairing Loviisa 1 and 2 with a similar VVER design plant at Bohunice V2 NPP, as described in the Slovak Republic NAR, shows that the latter has much more buried pipework. Please explain why the two similar plants have different extents of buried pipework. | Website | Fortum: Loviisa and Bohunice plants are not completely identical, for example there are differencies in the design of the plant and piping lay-out.
FI-11 |  | United Kingdom | Finland | 02. Overall Ageing Management Programme requirements and implementation | 7 & 8 | Section 2.3.2 explains the ageing assessment at TVO and Fortum. How are changes or challenges to the design basis and to national or international standards incorporated into the ageing assessments? | Website | In TVO Practical challengies are, how to apply international standards and procedures, what terms AMP, TLAA and LTO really means. Do they change real processis. Fortum: This is evaluated as a part of PSR.
FI-12 |  | United Kingdom | Finland | 02. Overall Ageing Management Programme requirements and implementation | 11 | The sub-section describing on-line monitoring notes that on-line fatigue monitoring will be in place for Olkiluoto 3. This is regarded as a good practice. What plant will be monitored and how will this work? | Website | The fatigue monitoring system of OL3 measures and to stores the original temperature and pressure which characterize the variable load of the primary circuit piping and certain associated nozzles during operation. Temperature sensors are installed directly on the loaded parts. This information is then analysed by means of custom made computer software to assess the fatigue life.
FI-13 |  | United Kingdom | Finland | 02. Overall Ageing Management Programme requirements and implementation | 14 | Section 2.4 discusses review and updating of the process. How does the licensee's senior management maintain oversight of the ageing management programme? What reports or key performance indicators are provided to senior management? | Website | TVO: Plats chef engineerings are checking component and system level annual reports and plant system health report. Plant system healt report is accepted by 3 directors (technical, oper.,safety) Fortum: Plant Health Committee evaluates regurlarly System health/Plant Health and Equipment Reliability Index (ER-index) and reports the results to senior management.
FI-14 |  | United Kingdom | Finland | 02. Overall Ageing Management Programme requirements and implementation | 14 | Section 2.4 states that the assessment of ageing management is integrated into the Periodic Safety Review. Please explain what the high level scope of the the Periodic Safety Review ageing management activities are. | Website | TVO: By section 36: 5) the Technical Specifications, which shall at least define limits for the process quantities that affect the safety of the facility in various operating states, provide regulations on operating restrictions that result from component failures, and set forth requirements for the testing of components important to safety; 6) a summary programme for periodic inspections 12) a programme for the management of ageing. AND Report of EQ, Plant improvements, FSAR-structural analysis Fortum: There are ageing summary reports of each technical discipline; mechanical, electrical, I&C, Cables and Civil Structures
FI-15 |  | United Kingdom | Finland | 02. Overall Ageing Management Programme requirements and implementation | 14 | Section 2.5 states 'sometimes a more detailed AMP is necessary. TVO will produce some more detailed AMPs in 2018, partly due to start-up of Olkiluoto 3. Please explain what the increased detail is covering and why the start up of the new reactor has influenced this. | Website | TVO has one organization for OL1/2/3. TVO will produce more detailed AMP's because of OL3 needs them and same AMP's are usefull for OL1/2. We try to use most of our AMP's all our units, scope and assessmets will be done separately.
FI-16 |  | United Kingdom | Finland | 03. Electrical cables | 22 | Section 3.1.3 notes that at Loviisa 1 and 2 most inspections are visual but some actions e.g. forcing a load onto a cable tray might be done. Please elaborate on what are the benefits and drawbacks of applying a load onto the cable tray are. | Website | Fortum: By forcing a load (by hand) to a cable tray might help to detect loose attachments of the tray. Unlikely drawback might be that the whole tray (or big part of it) loosens and the cables have to hang on the air until the broken attachments are repaired.
FI-17 |  | United Kingdom | Finland | 03. Electrical cables | General | Do the Finish NPP's routinely carry out Time Domain Reflectometery (TDR) test? | Website | OL1/OL2: TDR tests have not been used routinely in OL1/OL2, but e.g. for fault localization in neutron flux measurement circuits. OL3: TDR test has not been used. Preliminary plans to perform TDR measurements for special cables (e.g. nuclear instrumentation) have been made. Loviisa : No
FI-18 |  | United Kingdom | Finland | 07. Concrete containment structures | 76 | Section 7.1.3 Monitoring, testing, sampling and inspection activities for concrete structures - various references to monitoring of strain gauges across the Finland fleet are discussed in this section. Please provide more information on the AMP adopted to optimise the on-going availability of functioning gauges and any techniques for installing new monitoring instrumentation. | Website | OL1/OL2 /OL3 units have different kind of strain gauges. Main function is to show that the containment structure deformations are elastic during pressure test. New monitoring is possible to install, but it needs a lot of design work. Fortum applicable in Loviisa.
FI-19 |  | United Kingdom | Finland | 07. Concrete containment structures | 97 | Section 7.3 STUK has required that the containment of Olkiluoto 3 NPP has to be equipped with strain measurement system of the steel liner. The reason for this requirement was large initial imperfections caused by the large module fabrication technique. After required changes to the programmes STUK approved the ISI‐plan. Please provide more information to clarify the large module fabrication technique. | Website | OL3: ''The large module fabrication technique'' meant in this case the erection system where the liner was fabricated in the large modules (approximately 5 m high full rings/cups) which were shipped to Olkiluoto and then connceted by welding on site/final place. Some imperfections (exceeding of installation tolerance criteria) were observed after installation. They were repaired, however.
FI-20 |  | United Kingdom | Finland | 03. Electrical cables | General | The report identifies the position on ageing at two NPP Sites and appears confined to those Sites. Is best practice and findings shared between them and with other NPP operators? Little information is given for new build. Have lessons learned in terms of routing on new build (Olkiluoto 3) been factored into the design to minimise the known ageing effects in some locations? Have environmental conditions been adjusted to reduce their effects? Finally has additional environmental monitoring been installed in known problem areas to help predict future cable condition over and above general monitoring? | Website | OL1/OL2: OL1/OL2 cable system related findings, experiences, condition monitoring and qualification results etc. are handled most detailed in cooperation groups of Asea-Atom based NPPs (for cables namely "EKG Kabelgruppen"). Also Loviisa NPP representatives are invited in this cooperation. In OL1/OL2 additional environmental monitoring was installed as part of a project for lifetime management of in-containment electrical and I/C components to further investigate the actual radiation and temperature conditions e.g. in areas specified as most demanding in terms of design basis requirements. OL3: In terms of routing lessons learned from other plants have been taken into account already in basic design phase as far as applicable. Due to different regulations and most of all different plant type, the most important experience and knowledge is from reference plants (e.g. GKN 2) and other EPR's. Information is shared between other EPR owner's in EPROOG program. Design review and qualification tasks have led also to changes in cable routing and cable types in known problem areas. In OL3 environmental conditions will be monitored in locations of sample cable deposits and in addition on selected cable routes. Cable routes that are selected to be monitored are mainly in areas known to be problematic and some routes contain cables with e.g. lifetime restrictions. Environmental monitoring will be installed also for some I&C equipment for on-going qualification purposes and these results can be used also to predict cable conditions in these areas.
FI-21 |  | United Kingdom | Finland | 07. Concrete containment structures | 76 | It is stated for NPP units Loviisa 1 and 2 that the reactor building outer shell cylinder wall has rock anchors. To what extent are the heads of the rock anchors visible for visual inspection and how is the continued performance of the anchors demonstrated? | Website | Fortum: Rock anchors' ends are not visible, so visual inspection is not possible. STUK added: According to research report VTT-R-02323-08, 5.3.2008 "Degradation and service life of concrete structures in nuclear power plants", it is recommended to do special studies in which the risk of such degradation is evaluated specifically.
FI-22 |  | United Kingdom | Finland | 07. Concrete containment structures | 101 | There is no mention of settlement/tilt monitoring in the report. Is this carried out for the Finnish reactors? If not, how is it argued that any settlement will not adversely impact the NPP? | Website | OL1/OL2/OL3: Finnish nuclear power plants are founded on hard rock. Settlement monitoring is not necessary. Fortum: No, the plant is on the bedrock.
FI-23 |  | Switzerland | Finland | 02. Overall Ageing Management Programme requirements and implementation | 4 | Did you compare the new regulatory guide YVL A.8 with the new IAEA (draft) safety guide DS485? If yes, what are the results of this comparison concerning physical ageing? If no, do you intend to perform such a comparison? | Website | The guide YVL A.8 has not been compared in detail with the DS485 but their frameworks have been found quite similar. No systematic comparison is expected in near future.
FI-24 |  | Switzerland | Finland | 02. Overall Ageing Management Programme requirements and implementation | 5 | What kind of non-nuclear safety classified components are part of the overall AMP? Are fire protection components like piping and dampers included? | Website | TVO: We have in Finland class STUK/EYT it is safety class for component non safety but related safety e.g. fire protection components. Pipeline are in AMP and electrical grid component, main generator, generator protection etc. Fortum: Systems and components which are credited in the PRA model, like fire protection systems, and systems which will be used after DEC event to bring the plant in the controlled state.
FI-25 |  | Switzerland | Finland | 02. Overall Ageing Management Programme requirements and implementation | 5,6 | Based on PSA insights the SSCs are assigned to different maintenance categories (TVO) or groups (Fortum) having graded procedures and scope of AM. What are the main differences between the categories with respect to the generic attributes of an effective AMP as illustrated in IAEA NS-G-2.12? | Website | TVO maintenance classes are based on safety and economical assessment and NS-G-2.12 is based only on safety aspect. It is biggest difference. Fortum: No systematic evaluation has been made/documented regarding the generic attributes as per IAEA guideline.
FI-26 |  | Switzerland | Finland | 02. Overall Ageing Management Programme requirements and implementation | 14 | Were the AMPs in the Finish NPP subject to an independent review (e.g. Salto Peer Review mission)? If not, is such a mission planned in the next future? | Website | TVO's plants OL1 and OL2 have not been subject to an independent review so far. Fortum: There was a LTO-module in the recent Osart-mission, no decision made for SALTO-review.
FI-27 |  | Switzerland | Finland | 02. Overall Ageing Management Programme requirements and implementation | 15 | Are the licences requested to report annually to STUK about the status of the AMP and the insights gained from? | Website | The licensees are obliged to report about the status of their ageing management. From the SSCs important to safety such topics as long-term defect and failure trends, present operability, and validity of qualifications and time limited ageing analyses are summarized in the annual report.
FI-28 |  | Switzerland | Finland | 03. Electrical cables | 20 | Textline17-NPP-OK3: What type of cables are foreseen for in-containment with LOCA-requirement (=red rooms?)? | Website | OL3: For main part of the cabling inside containment with LOCA requirements following cable types are used: Power Cables (Prysmian) NHXCHX FRNC-BX (N)HXSCHXOE-J FRNC-BX I&C Cables (Leoni, EUPEN) JE-LiHXCHX FRNC-BX JE-HXCHX FRNC-BX In addition to these few other special cable types are used mainly for nuclear instrumentation.
FI-29 |  | Switzerland | Finland | 03. Electrical cables | 20 | Textline24-NPP-OK3: What are the criterias for these many different cable type groups (61)? | Website | OL3: Number of cable types (61) refers to total number of cable types, not different type groups. Described procedure was used to define preliminary selection of cable types to be installed in deposits. Number contains also the ones in the same type group but with different cross section or number of wires. Number of type groups with the described procedure would be somewhere around 20-30. Please note that this procedure doesn't show only the cable types in harsh environment (i.e. with accident requirements such as LOCA/SA) but also the ones without accident requirements but ending in or passing through the rooms with high radiation (red rooms).
FI-30 |  | Switzerland | Finland | 04. Concealed pipework | 30 | According to the cases described in chapter 4 no fire extinguishing pipework is embedded or buried in the Finnish NPP. Is fire extinguishing pipework not part of the AMP (see question 2) or is it routed in concrete channels exclusively? | Website | TVO: Fire extinguishing piping is not embedded or buried but housed inside concrete tunnels as well as inside technical rings. AMP is based on the analysis of piping degradation mechanisms. Fortum: Fire extinguishing pipes are in the scope of AMP and also in the RI-ISI program for pipelines.
FI-31 |  | Switzerland | Finland | 04. Concealed pipework | 30 | As pointed out for NPP units Loviisa 1 and 2 a few meters of piping embedded in concrete exist. Are these piping segments addressed explicitly in the AMP and what kind of surveillance methods are applied? | Website | Fortum: Internal visual inspections acc. to RI-ISI program for pipelines.
FI-32 |  | Switzerland | Finland | 07. Concrete containment structures | 77 ff. | How are the structures and the structural elements assessed which are inaccessible for visual inspections (indirect / indicative methods)? | Website | OL1/OL2/OL3: Preventative measures have been done during construction work. Containment leak tightness is verified by pressure tests periodically. NTD and material destructive methods are used case by case. Loviisa: For example liner plate inside concrete structures is not accessible for inspection, containment leak test every 8 years reveals possible leaks of the liner. One time visual inspection sample has been done for the bottom liner plate by drilling hole in the concrete. R&D has been done for drill hole samples e.g. embrittlement research of the concrete.
FI-33 |  | Switzerland | Finland | 07. Concrete containment structures | 83 | How the results of the tests on the 3 m long test beams are transferred or compared to the assessment of the pre-stressing in the containment? | Website | Short beams have been stored in units and in same circumstances compared to containment structure. Corrosion rate has been investigated. Loss of prestress differs to because short beam anchorage device influence is bigger.
FI-34 |  | Switzerland | Finland | 07. Concrete containment structures | 88 | Which are the reasons that many drilled anchor bolts had to be repaired? How were they inspected and how the deficiencies were detected? What are the conclusions of the large study and could there be a general problem with some types of anchor bolts? Are there further specific testing and inspection requirements for anchor elements? | Website | STUK: The original anchorage technique of post-installed anchors was from late 1970`s. Afterwards it was found that these post-installed anchors could not sustain the anchorage capacity. Utility made a large testing and replacement works concerning pipeline supports. The work has been completed in the 1980`s and it has been approved by STUK. No further actions has been required after.
FI-35 |  | Czech Republic | Finland | 02. Overall Ageing Management Programme requirements and implementation | 5 | "Ageing management is coordinated by a dedicated “Age” working group which consists of representatives of all technical disciplines and relevant plants’ functions such as nuclear safety, operation, maintenance and asset management." Does it mean that this group has responsibility to ensure that an overall AMP is developed and implemented? | Website | The “AGE” group is in charge of developing overall and specific ageing management programmes. The members of the group gather and process information from their discipline to support this work.
FI-36 |  | Czech Republic | Finland | 02. Overall Ageing Management Programme requirements and implementation | 7 | From the document it is not clear if any indicators are used to assess the effectiveness of the ageing management process in Fortum. Could you please clarify how do you assess the effectivness of this proces? | Website | Fortum: At the moment no clear indicator exists, to assess effectiveness we utilize e.g. maintenance KPI's and failure trends,
FI-37 |  | Czech Republic | Finland | 02. Overall Ageing Management Programme requirements and implementation | Chapter 2.3.2 | From the document it is not clear if the ageing management review was performed to identify relevant ageing and wear-out mechanisms and potential age re-lated degradations for all SCCs in the scope of ageing management. Could you please clarify it? | Website | TVO: An extensive literature study was performed for all possible damage mechanisms. Insignificant damage mechanisms were screened out. For the signifigant damage mechanisms subsecuent analysis was performed and documented in TVO report 170462. Fortum: Ageing management review has been performed for SSCs to identify relevant ageing machanisms.
FI-38 |  | Czech Republic | Finland | 02. Overall Ageing Management Programme requirements and implementation | 12 | "Fortum’s programmes for monitoring, testing, sampling and inspection activities are described in the following. …" In Fortum there is no ageing management programme (or monitoring programme) for managment of flow accelerated corrosion in secondary feedwater pipelines and steam pipelines? | Website | Fortum: Yes, there is comprehensive monitoring program for FAC.
FI-39 |  | Czech Republic | Finland | 04. Concealed pipework | 30 | You have mentioned that TG‐piping in Loviisa NPP has been handled in RI‐ISI aging management program and there is only a few metres of piping that is embedded in concrete. What are the results of RI‐ISI aging management program ? What time period is set up between two inspections? What NDT method is used? How do you assess residual lifetime of these concealed pipings embeded in concrete? | Website | Fortum: No degradation is indentified based on the visual inspections carried out according to RI-ISI program for pipelines.
FI-40 |  | Czech Republic | Finland | 04. Concealed pipework | 30 | You have mentioned that you have set up AMPs for concealed piping of Olikuloto 1 and 2. What is the basis of these AMPs? How do you assess residual lifetime of these pipings? | Website | This is not stated in the country report of Finland. The concrete tunnel housing the cooling water piping have their own AMPs which do not belong in the scope of the requested reporting. (STUK has clarified the answer further)
FI-41 |  | Czech Republic | Finland | 05. Reactor Pressure Vessels | 37 | You have mentioned that the fatigue analyses of the RPVs of NPP units Olkiluoto 1 and 2 have been updated for 60 years of service life. Do these analyses contain also analyses of environmentally assisted fatigue? | Website | Yes, in the updated analyses environmentally assissted fatigue has been considered for Olkiluoto 1 and 2.
FI-42 |  | Czech Republic | Finland | 05. Reactor Pressure Vessels | 38 | You have mentioned enviromentally assisted fatigue only in table 5.5 which defines relevant degradation mechanisms for Olkiluoto 3. Have you performed analyses of enviromentally assisted fatigue for Loviisa 1, 2 or for Olkiluoto 3. If not, what is the reason? You have mentioned that the U.S. NRC requires the consideration of environmental factors for Fatigue assessment during the design phase of new plants and long‐term operation in the U.S. [US NRC Regulatory Guide 1.207], as well as during the evaluation phase supporting the Long‐Term Operation for existing plants [NUREG‐1801]. | Website | Environmentally assissted fatigue has been considered for Olkiluoto 3. For Loviisa 1 and 2 it was not considered in the original strength analyses but the analyses have been updated later on and environmentally assissted fatigue is now considered.
FI-43 |  | Czech Republic | Finland | 05. Reactor Pressure Vessels | 46 | Have you used FEN factor (FEN = Nair / Nwatter) which is defined in NUREG/CR 5704 and 6583 in the case of Olkiluoto 3? | Website | Yes, we have applied those ones and NUREG/CR-6717, NUREG/CR-6815 and NUREG/CR-6909 as well.
FI-44 |  | Bulgaria | Finland | 02. Overall Ageing Management Programme requirements and implementation | p. 16 | Information, related to the STUK conclusions about “further development to some extent” of ageing management programs for both companies TVO and Fortum is presented. Would you please provide more information about this conclusion of STUK concerning the scope of further development? | Website | The topics of further development are related to grouping of SSCs. The target is that the same grouping should apply to both AMPs and annual ageing follow-up reports. The AMPs include SSC-specific information on design basis, ageing mechanisms, condition monitoring/maintenance programs, qualifications and time limited ageing. The status of ageing such as SSC failure trends and major service works should be reported with a similar SSC-specific breakdown. In addition, organizational description should be completed. Responsibilities, tasks and interaction of involved parties should be described so that implementation of overall ageing management is well-defined.
FI-45 |  | Bulgaria | Finland | 02. Overall Ageing Management Programme requirements and implementation | p.4 | Would you please clarify whether the following IAEA safety standards, reports and guides had been used too: 1.IAEA, Safe Long Term Operation of Nuclear Power Plants, Safety Reports Series No. 57, IAEA, Vienna (2008) 2.IAEA, Periodic Safety Review of Nuclear Power Plants, Safety Standards Series No. SSG-25, IAEA, Vienna (2013) 3.IAEA, Methodology for the Management of Ageing of Nuclear Power Plants Components Important to Safety, Technical Reports Series No. 338, IAEA, Vienna (1992) 4. IAEA, A system for the Feedback of Experience from Events in Nuclear Installations, Safety Guide No. NS-G-2.11, IAEA, Vienna (2006) 5.IAEA, Data Collection and Record Keeping for the Management of Nuclear Power Plants Ageing, Safety Reports Series No. 50-P-3, IAEA, Vienna (1991) 6.IAEA, Implementation and Review of a Nuclear Power Plant Ageing Management Programme, Safety Reports Series No. 15, IAEA, IAEA, Vienna (1999) 7.IAEA, Equipment Qualification in Operational Nuclear Power Plants: Upgrading, Preserving and Reviewing, Safety Report Series No. 3, IAEA, Vienna (1998) 8.IAEA, Maintenance, Surveillance and In-service Inspection of Nuclear Power Plants, Safety Standards Series Safety Guide No. NS-G-2.6, IAEA, Vienna (2002) | Website | TVO is not following stricly these IAEA documents but they try to fullfil ideas of these documents. Fortum: No IAEA guidelines have been exactly used in Loviisa, but national STUK YVL-guidelines are based in many cases IAEA guidelines and safety standards.
FI-46 |  | Bulgaria | Finland | 04. Concealed pipework | p.30 | For NPP units Olkiluoto 1 and 2, in the first paragraph was written “There are also some safety classified pipes, which have penetration through thick concrete structures.” Would you please clarify to which safety systems belong those pipes? | Website | These pipes belong to safety class 1 systems. These pipes penetrate through the containment wall.
FI-47 |  | Czech Republic | Finland | 04. Concealed pipework | 30 | "Seawater cooling system in NPP unit Olkiluoto 3 is mainly using cast‐in‐situ concrete channels or piping installed in rock or concrete channels. Concrete seawater channels have their own AMP FIN005‐CEC‐6350‐690132 “In service inspection plan of cooling water structures”." Experience in the Czech and Slovak Republics show that the piping embedded in the concrete, even if it is not provided with an external surface of the groundwater insulation, is not degraded from the outside even after decades of operation. Can this be confirmed by the experience of Finnish power plants? | Website | No, because there is not yet enough practical experience from Olkiluoto 3. Fortum: No experience on that.
FI-48 |  | United Kingdom | Finland | 04. Concealed pipework | 30-31 | Section 4 makes reference to 'existing AMPs'. Please provide information on the scope of these AMPs for checking the integrity of these embedded systems (frequency of inspection, percentage covered, susceptibility to degradation and consequences of failure). What is STUKs opinion on the adequacy of these existing AMPs? | Website | STUK: As stated in the country report of Finland these type of structures are very rare. Therefore AMP of these structures is defined within the corresponding system level AMP. This includes the maintenance plans and works of embedded pipeworks within internal visual inspections acc. to RI-ISI program for pipelines. These procedures have been found adequate in STUK`s opinion.
FI-49 |  | United Kingdom | Finland | 05. Reactor Pressure Vessels | 30-31 | It is claimed that pipework is in concrete channels and hence is not concealed. Please clarify what concrete channels are in the context of a how they differ to a concealed system. | Website | STUK: The question is referring to chapter 4. The concrete channels relating to this question are tunnel structures which house the pipeworks in order to be fully approachable by walking.
FI-50 |  | Belgium | Finland | 05. Reactor Pressure Vessels | 48 | The Loviisa 1 RPV has been heat treated in 1996 and new surveillance specimens were installed. How has the impact of the heat treatment on the embrittlement been estimated? How has the representativeness of the new surveillance specimens been assessed with respect to the actual RPV material, taking into account its irradiation and annealing history? | email | New surveillance program was carried out in 1996 – 2005. The new surveillance program included annealing and re-irradiation of the weld material 501 manufactured by Izhora factory. 12 surveillance chains were installed in Lo1 reactor and re-embrittlement of the material was investigated by the Charpy-V and fracture toughness measurements. Representativeness of the tailored weld material 501 has been assessed by investigating the re-embrittlement of the weld also with the initial surveillance specimen material.
FI-51 |  | Belgium | Finland | 02. Overall Ageing Management Programme requirements and implementation | 4 | What are the main differences between the regulatory guide YVL A.8 from STUK and other 'classic' IAEA standards in terms of ageing management program? | email | The guide YVL A.8 has not been compared in detail with the IAEA ageing management standards. It is understood that the guidelines are similar and there are no fundamental conflicts.
FI-52 |  | Belgium | Finland | 02. Overall Ageing Management Programme requirements and implementation | 9, 10, 13 | Which edition of the ASME Code Section XI is currently used in OL1, OL2, OL3 and Loviisa? Which code is used for the periodic testing of safety-class pumps, valves, snubbers, etc.? Is it the ASME OM or another specific code? | email | TVO: In Finland the NPP's are obliged to use the latest ASME. Fortum: "ASME XI Edition 15, ASME OM is used only partially, e.g. pump curves acceptance criterias.
FI-53 |  | Belgium | Finland | 02. Overall Ageing Management Programme requirements and implementation | 10 | What kind of periodic inspections are performed on the hoisting equipments? What is the scope of these inspections? Is it specifically required by the STUK? | email | TVO: Yearly check and according to standard 10 years fatique analyses and yearly update if nessessary. Fortum: According Government Decree VnA 403/2008 section 34 and section 35 1. Periodic inspections must be carried out at one-year intervals after the first initial inspection. However, when no initial inspection of the equipment is required, periodic inspections must be carried out at one-year intervals from the date when the employer took the work equipment into use. 2. Lifting machinery must be given a necessary test run once every year in connection with an inspection, including a testing with the permissible maximum load every four years. 3. In addition to the periodic inspection meant above in section 34, lifting machinery must be subject to a thorough periodic inspection when the designed limits defined for the lifting machinery by the manufacturer are drawing close. If those limits are not known, a thorough periodic inspection must be carried out within 10 years after the device was put into use for the first time. What is the scope of these inspections? According Government Decree Vna 403/2008 section 34 1. During a periodic inspection, the working condition of the work equipment is ensured by especially checking that no danger is caused because of ageing, fatigue, wear, corrosion or damage. When necessary, non-destructive inspection methods must be used. 2. Lifting machinery must be given a necessary test run once every year in connection with an inspection, including a testing with the permissible maximum load every four years. 3. During a thorough inspection such assembly parts must be disassembled which are important for safety and which cannot otherwise be inspected in a reliable way. Non-destructive testing methods must be used when carrying out the inspection. Is it specifically required by the STUK? Yes, STUK YVL E.11 Requirements 1108 and 1109 1108. In-service inspections shall be performed on the hoisting device unit in accordance with the Government Decree on the Safe Use and Inspection of Work Equipment (403/2008). 1109. In defining the intervals and scope of in-service inspections, the requirements for operation and reliability, ageing monitoring and Government Decree (403/2008) shall be taken into consideration.
FI-54 |  | Belgium | Finland | 02. Overall Ageing Management Programme requirements and implementation | 5 | What is the general documentation developed by the licensees in the framework of their ageing management programs (specific AMPs, inspection programs, etc.)? | email | TVO: General documentation is "umbrella" documet for frame of ageing management. Lot of specific AMPs. Fortum: General ageing management program according to YVL A.8, and system or component spesific inspection and maintenance programs, also degradation spesific programs eg. FAC-program
FI-55 |  | Belgium | Finland | 03. Electrical cables | 22 | Could you clarify wat are the specific (if any) monitoring, testing and inspection activities related to burried cables and neutron flux cables at the Loviisa and Olkiluoto NPPs ? | email | OL1/OL2: At the moment there are no safety classified buried cables in OL1/OL2. There are no condition monitoring activities specific only for the netron flux monitoring cables in OL1/OL2. Fortum puuttuu. OL3: There is no safety classified buried cables in OL3. Plans have been made to perform TDR measurements for special cables such as neutron flux measurement cables and other nuclear instrumentation cables. Loviisa 1 and 2: Most of the buried cables are non-safety cables and no spesific monitoring testing and inspections are therefore performed. Neutron flux detectors are tested every month and calibrated if needed. The whole neutron flux system is inspected and tested on every outage.
FI-56 |  | Belgium | Finland | 03. Electrical cables | 18 | At Olkiluoto 1 and 2 : some cables were selected outside the containment to be subject to a condition monitoring programme. On what basis were they selected ? | email | OL1/OL2: The outside containment cable types were selected to represent regular PVC cable types used outside containment, but the condition monitoring samples are exposed to in-containment environment.
FI-57 |  | Belgium | Finland | 07. Concrete containment structures | 75 | What are the acceptance criteria related to the ageing mechanisms listed? | email | OL3: Accpetance criteria for loss of prestressing force due to creep and shrinkage of the concrete and relaxation of the prestressing steel: Further investigations are taken if the measured losses would be higher than the calculated ones (Cf. page 95). Calculated values fulfill with margins the design criteria that average stress of cross section in current parts of containment structure remains compression under design pressure until end of the life time. Effects of other aging mechanisms (pages 75-76) are limited by good circumstances and design solutions. Regular visual inspections will be performed. In case of observed degradation, corrective measures are assessed case by case.
FI-58 |  | Belgium | Finland | 07. Concrete containment structures | 75 | Can one example of R&D programmes concerning ageing degradations mechanisms be given? | email | OL3: Monitoring of the loss of concrete compression stress, Cf. Page 95-96 .
FI-59 |  | Belgium | Finland | 02. Overall Ageing Management Programme requirements and implementation | 5 | Could you detail if the overall AMP applies to all SSCs, whether they are passive or active SSCs? | email | The AMP applies to all safety classified SSCs, irrespective of whether it is active or passive.
FI-60 |  | Belgium | Finland | 02. Overall Ageing Management Programme requirements and implementation | 6 | As the main income for the ageing assessments seem to be the scheduled maintenance and follow-up programs, could you elaborate on the ageing management for passive components? | email | TVO: The water chemistry is continuously monitored and has been improved to mitigate possible stress corrosion of piping components. Fortum: Critical components and their degradaton mechanismns have been indentified and inspection programs are allocated especially on those.
FI-61 |  | Belgium | Finland | 02. Overall Ageing Management Programme requirements and implementation | 6 | The overall ageing management program does not seem to rely on an AMR process identifying all the potentially applicable degradation mechanisms for groups of SSCs and evaluating their impact. Can you elaborate on the process for identifying the applicable degradation mechanisms in order to demonstrate that the ageing effects are adequately managed and that the maintenance and surveillance programs are adequately updated? | email | TVO: For the OL1/OL2 RPV and internals these issues are covered in TVO report 170462. In that report the component specific susceptibility to the significant degradation mechanisms is based on material type, magnitude of load, fabrication characteristics and environment. Fortum: AMR-like assessment/review is done during PSR
FI-62 |  | Belgium | Finland | 02. Overall Ageing Management Programme requirements and implementation | 14 | Can you elaborate on the frequency for updating the overall AMP ("on a regular basis")? How is this fixed? | email | TVO: Yearly, if there are needs. We have requirement for yearly updating. Fortum: At least every 4 years.
FI-63 |  | Netherlands | Finland | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2/p8 | Is IAEA IGALL/ NRC GALL and EPRI information used as input for the AMPs in Finland? | email | TVO: For the OL1/OL2 RPV and internals IAEA and information has been applied, see TVO report 170462. Fortum: Loviisa is not an EPRI member, for some cases IGALL has been used, but not systematically.
FI-64 |  | Netherlands | Finland | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2/p9 | How is other R&D than from Finnish and Swedish programmes used? | email | TVO: For the OL1/OL2 RPV and internals as much as possible international signifigant R&D data has been applied, see TVO report 170462. Fortum: There has been some common R&D together with other VVER utilities.
FI-65 |  | Netherlands | Finland | 02. Overall Ageing Management Programme requirements and implementation | 2.4/p14 | Since the existing NPPs have ages approaching 35-41 years, has it been considered to invite external review by IAEA (SALTO)? | email | TVO: No, maybe later. SALTO workshop has been done 2016. Fortum: There was a LTO-module in the recent Osart-mission, no decision made for SALTO-review
FI-66 |  | Netherlands | Finland | 02. Overall Ageing Management Programme requirements and implementation | 2.7/p16 | What are the main areas for improvement of the Finnish AMPs? | email | The topics of further development are related to grouping of SSCs. The target is that the same grouping should apply to both AMPs and annual ageing follow-up reports. The AMPs include SSC-specific information on design basis, ageing mechanisms, condition monitoring/maintenance programs, qualifications and time limited ageing. The status of ageing such as SSC failure trends and major service works should be reported with a similar SSC-specific breakdown. In addition, organizational description should be completed. Responsibilities, tasks and interaction of involved parties should be described so that implementation of overall ageing management is well-defined.
FI-67 |  | Netherlands | Finland | 03. Electrical cables | 3.1.1, p.18 | The identified ageing mechanisms are stated as: 'high temperature, short circuit or overcurrent, voltage load, ionization and UV radiation, lack of cooling and/or ventilation, mechanical damages and inappropriate substances getting involved with cable.' A few of these are actually typical examples of ageing drivers. Mechanisms for example ar typically cable cracking, water treeing, embrittlement etc. Which processes/procedures were used for the identification of ageing mechanisms? | email | Fortum: Procesesses from IAEA documents TecDoc 1188 and NP-T-3.6. Some of the Mechanical and electrical identification procedures presented in IAEA TecDoc 1188 are in use.
FI-68 |  | Netherlands | Finland | 03. Electrical cables | ch 3.1.3 | Related to chapter 3.1.3, how is the inspection history taken into account for identifying trends and progressive deterioration? | email | OL1/OL2: All the measurement trends are included when reporting the latest results every five years and in the report the results are compared to the measurement history. OL3: There is no specific inspection history from OL3. Reporting will be done in a same way with running plants in accordance with the regulatory guides every five years. Fortum: The inspection history is evaluated in the cable ageing management report done every four years. E.g. the EAB values of the measurements done every four years are plotted on a same graph to observe the trend in ageing of the cables.
FI-69 |  | Netherlands | Finland | 04. Concealed pipework | Ch.4 | It seems that Chapter 4 (concealed pipework) is not written in accordance with the TPR technical specification document. Only a very short description of concealed pipework is provided. It seems that the pipework AMP is not a standalone AMP, but belongs to different and specific AMPs (RI-ISI, concrete channels, etc.). Could you please provide more information about the concealed pipework AM in Chapter 4, preferably in the format of the TPR Technical Specification? Otherwise, could you please motivate why limited description of concealed pipework is included in the NAR? | email | STUK: This is not necessary because as stated in chapter 4 these type of structures are very rare. Therefore AMP of these structures is defined within the corresponding system level AMP. This includes the maintenance plans and works of embedded pipeworks within internal visual inspections acc. to RI-ISI program for pipelines. These procedures have been found adequate in STUK`s opinion.
FI-70 |  | Netherlands | Finland | 05. Reactor Pressure Vessels | Ch.5 | The information provided in this NAR in its chapter 5 on ageing management of reactor pressure vessels, is to a great extent qualitative. However in the Technical Specification for the NARs, the countries are requested to report in their NARs on the acceptance and action criteria for the various ageing phenomena. Apart from indicating those criteria, it is obvious that the NARs must discuss the compliance of the reactors with these criteria. Could you please provide this information? | email | STUK: ASME XI criteria are applied when ISI results are evaluated. Fatigue analysis results are evaluated against criteria presented in corresponding calculation code, typically ASME, RCC-M or Russian PNAE. Above all are the Finnish regulatory guides (YVL-Guides) that give mandatory requirements and criteria that have to be considered. For RPV, the most important regulations are given in YVL-Guide E.4: Strength analysis of nuclear power plant pressure equipment.
FI-71 |  | Netherlands | Finland | 07. Concrete containment structures | 7.1.1, p.64 | Is the effect of possible pool leakage to the surrounding concrete being monitored? | email | TVO: Pool leakages are monitored. Effect to the concrete can be monitored by drilling core samples. STUK added: Some drilling core samples have been taken from the wetwell of Olkiluoto 1/2. Fortum: Leakage monitoring exists and the effects of pool water leakages into the concrete have studied.
FI-72 |  | Netherlands | Finland | 07. Concrete containment structures | 7.1.3 | Is there an (NDO) inspection programme on the connections between the reinforced concrete construction and the steel liner/steel containment? | email | Fortum: No program exists, one time visual inspection has been done. STUK added: There is an inspection program of the steel containment anchorage to the base slab in Loviisa 1 and 2. Steel containment is not within the scope of the review.
FI-73 |  | Netherlands | Finland | 07. Concrete containment structures | 7.1.3 | The pool liner surface is inspected. Is there also an inspection programme on / analysis into the effect of pool water leaking through/out of the pool into the concrete? | email | TVO: Pool leakages are monitored. Effect to the concrete can be monitored by drilling core samples. Also thin section methods are taken if necessary. Fortum: The effects of pool water leakages into the concrete have been studied.
FI-74 |  | RPV expert group | Finland | 05. Reactor Pressure Vessels | 37 | 5.1.2 In NAR page 37 is mentioned that Loviisa 1 RPV had to be thermally treated in 1996 due to the high Cu and P content. However, it is not mentioned anything about heat treatment to Loviisa 2. Has been it performed?. If not, which is the reason for not doing it?. | expert group 2 | The fracture toughness of Loviisa 2 RPV weld material is higher than that of Loviisa 1.The reason for this is the unexpected high neutron fluence that was first detected at Loviisa 1. At that time Loviisa 2 had been in use much shorter time and the mitigation measures were more effective for Loviisa 2 RPV. The fracture toughness did not decrease as much at Loviisa 2 than it did at Loviisa 1. The need for thermal annealing of Loviisa 2 RPV will be discussed later especially if the utility is applying license renewal up to 60 years.
FI-75 |  | RPV expert group | Finland | 05. Reactor Pressure Vessels | - | 5.1.2 and 5.1.3 NAR Chapter 5.1.2. and 5.1.3. The information included about Olkiluoto 3 (not in operation yet) is more detailed than for the rest of the plants (in operation and near to LTO). Is OL3 information applicable to the rest of the plants?. In those chapter there is not information relating to ISI program, water chemistry monitoring, fatigue monitoring and others in OL1 &2. Could you provide information about this? | expert group 2 | TVO: ISI: A full program according to the ASME is performed with additional inspection due to the known cracks. Fatigue monitoring: A full reanalysis has been performed for a 60 year lifetime. The result of this analysis is that the fatigue usage is insignificant. Therefore this is not separately monitored.
FI-76 |  | RPV expert group | Finland | 05. Reactor Pressure Vessels | 59-61 | 5.2 NAR Chapter 5.2. OL1&2 explain in this chapter the AMP applied to RPV, but there is not any information about the licensee´s experience. Can you provide information about this?. | expert group 2 | OL1/OL2: The experience has come from ISI. Some cracks have been found from RPV internals. These cracks have been the result of high cycle thermal fatigue and were fully mitigated by thermal shields and internals replacement. Further experience has been obtained from conferences and meetings with colleagues from other sites.
FI-77 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 64 | In accordance with Technical Specification for chapter 7.1.1. What are the main functions of the structures? | expert group 4 | Fortum: Containment structures main safety function is to prevent radioactive release.
FI-78 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 64 | In accordance with Technical Specification for chapter 7.1.1, can you describe the main concrete structural elements for the reactor buildings in units Olkiluoto 1 and 2 and add principle drawings? | expert group 4 | OL1/OL2: A Schematic drawing is presented in annex 9.
FI-79 |  | Concrete containment PCPV expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | 5 | On page 5, 6 regarding scope of overall AMP. What method is used to find non‐nuclear safety classified civil structure having an consequential risk to nuclear safety? | expert group 4 | OL1 and OL2 containment is protected with reactor building. OL3 has secondary containment. Loviisa: PRA has been used to identify those SSCs.
FI-80 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 71 | In accordance with Technical Specification for chapter 7.1.2, can you describe the establishment of acceptance criteria related to ageing mechanisms? | expert group 4 | OL1/OL2/OL3: Ageing mechanisms and circumstances are followed periodically and corrective measures are assessed case by case. Some ageing mechanisms have specific acceptance criteria, for example loss of prestressing forces and leak tightness of the containment. Loviisa: There are no clear acceptance criterias defined for every different ageing machanisms. The inspection guideline Y-05-00005 defines criterias for reporting and decision making for repair is based on engineering judgement.
FI-81 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 77, 83 | What kind of NDE-methods are used for periodical inspections at Loviisa 1 and 2 and Olkiluoto 1 and 2? | expert group 4 | OL1 and OL2: IE – Impact Echo, SASW – Spectral Analysis of Surface Waves, MASW – Multichannel Analysis of Surface Waves. Loviisa: Thickness measurements and hardness measurements of concrete.
FI-82 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 77 | On page 77: “Guide Y‐05‐00005 defines those reinforced concrete structures and steel structures, which are under the scope of periodical civil engineering inspections and describes the inspection activities for each structure.” How is the identified civil structures within the scope of overall AMP joined to this guide? | expert group 4 | Fortum: In the overall AMP all the civil structures have been classified.
FI-83 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 83 | How are concrete cracks inspected during leak tightness test? | expert group 4 | TVO: Visual inspection. Some cracks are monitored by "demeg" method.
FI-84 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 80 | Some acceptance criteria are missing for periodical inspections for Loviisa 1 and 2 in chapter 7.1.3. For example what causes the expansion joint sealant to be classified either 2 or 3? | expert group 4 | Fortum: If there is no clear citeria then it is based on engineering judgement.
FI-85 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 84 | In accordance with Technical Specification for chapter 7.1.3, what are the acceptance criteria for Olkiluoto 3? | expert group 4 | OL3: Accpetance criteria for loss of prestressing force due to creep and shrinkage of the concrete and relaxation of the prestressing steel: Further investigations are taken if the measured losses would be higher than the calculated ones (Cf. page 95). Calculated values fulfill with margins the design criteria that average stress of cross section in current parts of containment structure remains compression even under design pressure until end of the life time. Effects of other aging mechanisms (pages 75-76) are limited by good circumstances and design solutions. Regular visual inspections will be performed. In case of observed degradation, corrective measures are assessed case by case. There is also an accurate acceptance criteria for periodically tested containment leak tightness. This criteria might be not achieved in case of significant corrosion defects of containment liner (inaccessible areas).
FI-86 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | 88 | In accordance with Technical Specification for chapter 7.1.4, what are the preventive actions for Olkiluoto 1, 2 and 3? | expert group 4 | OL1/OL2/OL3: During construction work several work method tests (mock-ups) have been made widely in order to prevent inadequate work quality. Ageing has been considered also in design process (e.g. concrete cover, coating systems, concrete quality).
FI-87 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | Section 7.1.3 | With reference to Section 7.1.3 Monitoring, testing, sampling and inspection activities for concrete structures, have there been any cases identified in which there are differences between the design assumptions and the actual operating conditions for parameters that may affect the performance of the 07. Concrete containment structures? | expert group 4 | TVO: No. But because orginal design life time is shorter than real, ageing phenomena and mechanisms are important. Fortum: No such cases indentified.
FI-88 |  | Concrete containment PCPV expert group | Finland | 07. Concrete containment structures | Section 7.2 | With reference to Section 7.2 Licensee’s experience of the application of AMPs for concrete structures, what external operating experience events involving ageing-related degradation of 07. Concrete containment structures have been evaluated for applicability to Finish NPPs OL1 and OL2? | expert group 4 | Question is not understandable. STUK added: There is ongoing exhange of opearational experiences between BWR utilities in Finland and Sweden.
FI-89 |  | Concealed pipework expert group | Finland | 04. Concealed pipework | 30 - 31 | According to WENRA TS, the NAR don't describe: the ageing management programme, the outputs of the ageing assessment (including the key standards, operating experience…), the monitoring, testing, sampling and inspection activities, the preventive and remedial actions, the licensee's experience of the application of the AMPs and the regulator's assessment and conclusions on ageing management of concealed pipewotk. Infact the topic 4 (concealed pipework) of this NAR is made of only two pages. It is necessary to integrate it according to the items described in WENRA TS. | expert group 5 | STUK: We acknowledge that this information should be shared if there were reasonable amount of corresponding structures and related extensive AMP for concealed pipework. This is not necessary because as stated in chapter 4 these type of structures are very rare. Therefore AMP of these structures is defined within the corresponding system level AMP. This includes the maintenance plans and works of embedded pipeworks within internal visual inspections acc. to RI-ISI program for pipelines. These procedures have been found adequate in STUK`s opinion.
FI-90 |  | Concealed pipework expert group | Finland | 04. Concealed pipework | General | Section 4 “Concealed piping” of Finland NAR provides information that “There is actually not much of concealed pipework in the Finnish nuclear power plant units”. In addition, brief information is given on several types of inaccessible pipelines and it is said, for example, that “Seawater cooling system in Olkiluoto NPP unit 3” is controlled within a separate program MP FIN005‐CEC‐6350‐690132 “In service inspection plan of cooling water structures”. Other information on inaccessible pipelines is not available. Therefore, it is impossible to perform “Assessment of the adequacy to WENRA TS” for inaccessible pipelines. Question: Are there extended pipeline systems with inaccessible sections, for example, fire extinguishing systems, emergency/backup cooling water supply systems, ventilation lines at Finnish NPPs other than pipeline types presented in the report? If there are such pipelines, it is necessary to extend the report with the data on the technological systems they are referred to and within which ageing management programs these pipelines are controlled? If there are such pipelines and they are not considered within separate ageing management programs, the report should be extended with the data in accordance with WENRA TS requirements. | expert group 5 | TVO has evaluated all pipelines related to risk for inspection actions. Fortum: There are only short sections of pipelines which are inaccessible in Loviisa NPP and these pipelines belong to the scope of RI-ISI program for pipings.
FI-91 |  | Concealed pipework expert group | Finland | 04. Concealed pipework | 30 | What inspections are performed for sea-water piping installed in concrete channels in Loviisa? | expert group 5 | Loviisa: Inspections defined in the RI-ISI program; mainly internal and external visual inspection
FI-92 |  | Concealed pipework expert group | Finland | 04. Concealed pipework | 30 | Are there any other triggers for maintenance other than leaks? | expert group 5 | TVO: For instance operational experience. Fortum: Inspection results, e.g. damages of the internal coatings.
FI-93 |  | Concealed pipework expert group | Finland | 04. Concealed pipework | 30 | Is sea-water used for all ESW, non-ESW and main condenser cooling at all Finnish units? | expert group 5 | STUK: The answer is based on the assumption that ESW = Essential Service Water. Sea water is used as ESW in NPP Units OL1, OL2 and OL3. In Loviisa NPP also air is used for cooling but only in cooling towers that are for emergency purposes. Sea water is used as ESW in all other purposes in Loviisa NPP as well.
FI-94 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | from 4 to 16 | Nevertheless the report follows the technical specifications it is too general and doesn't give enough information as it is requested in the technical specifications and that raises diffculties for the reader to understand the AMP especially when comparing this report with other countries' reports. (It is expected that this chapter will be 20 to 80 pages but it is only 12) | expert group 3 on other topics / expert group 1 | ???
FI-95 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | 4 | From the next sections of the report the Guide YVL A.8 seems main document regulating the ageing management of NPPs in Finland. It would be good to have broader description of the contents and requirements written there (even some quotes form it) in order to have better understanding of the national legal requirements regarding the ageing management. | expert group 3 on other topics / expert group 1 | YVL Guides, including YVL A.8, are available in English https://www.stuklex.fi/en/yvl-ohje
FI-96 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | from 5 to 7 | The Overall AMP for both licensees is not described as a whole integral program as per WENRA I1.1. Items a) to e) from technical specifications are only briefly mentioned or even missing. | expert group 3 on other topics / expert group 1 | ???
FI-97 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | from 7 to 9 | Item 2.3.2 Agein Assessment of the report doesn't clearly describe how WENRA I2.1 is fulfilled. For example only YVL A.8 is quoted as guiding document for overall AMP. What about design, manufacturing and oprations documents - are they used in preparation of the overall AMP? | expert group 3 on other topics / expert group 1 | ???
FI-98 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | 16 | "A generic lesson learned in Finland is that the closer nuclear power plants get to the end of their design lifetime, the more challenging it is for the licensees to start large and expensive investments to modernise or modify the NPPs. Instead of renewing a system or a component, modernisation may be postponed or realized only partially. A postponed decision to renew for instance an I&C system or an electrical system may result in an obsolescence of systems, i.e., spare parts or technical support are no longer available. This may lead to situations where the licensee may not be able to demonstrate the safety of operations to the regulator, or as far as the scope or adequacy of demonstration is concerned, opinions may differ between the licensee and the regulator." Has the regulator (STUK) had so far experience with such postponed/partially realised modernisations? What were the licensee's arguments and were they accepted by the regulator? | expert group 3 on other topics / expert group 1 | If a SSC is out of service regularly for repair works, licensees may prefer to replace defective parts instead of replacing the whole SSC. Typically there are financial reasons, and in some cases it is acceptable, too, when only limited number of parts are degraded and replaced parts completely restore the operability of the SSC. However, if it is obvious that a SSC is reaching the end of its lifetime and part replacements are no more justified for safety, STUK is in position to require more extensive modernizations.
FI-99 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | 7 | In TVO's ageing assessment, scheduled maintenance seems to receive the same attention as the follow-up programs. Maintenance is the tool for ensuring functional integrity of active components. In the case of SSCs (passive SSCs) the follow-up programs ensuring their structural integrity play a much more important role. The list of follow-up programs in the Report is correct. | expert group 3 on other topics / expert group 1 | Correct.
FI-100 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | 10 | Why pitting corrosion is included into erosion inspection program? Please clarify. | expert group 3 on other topics / expert group 1 | Any degradation mechanism that may reduce wall thickness or otherwise weaken integrity is addressed in the erosion inspection program.
FI-101 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | 16 | Some examples (say performance indicators) for ageing management effectiveness measurement would be worth mentioning. | expert group 3 on other topics / expert group 1 | TVO: Number of failures, lack of spareparts. Fortum: System health indicator and ER-index (=Equipment Reliability index).
FI-102 |  | General AMP expert group | Finland | 02. Overall Ageing Management Programme requirements and implementation | 16 | STUK conclusion that AMP of both plants need further development should be illustrated by examples. | expert group 3 on other topics / expert group 1 | The topics of further development are related to grouping of SSCs. The target is that the same grouping should apply to both AMPs and annual ageing follow-up reports. The AMPs include SSC-specific information on design basis, ageing mechanisms, condition monitoring/maintenance programs, qualifications and time limited ageing. The status of ageing such as SSC failure trends and major service works should be reported with a similar SSC-specific breakdown. In addition, organizational description should be completed. Responsibilities, tasks and interaction of involved parties should be described so that implementation of overall ageing management is well-defined.
FI-103 |  | Cables expert group | Finland | 03. Electrical cables | 24 | (The TPR report states that Habia is LOCA qualified but doesn’t function when sunk in water. Could you provide more details. Which cables are currently fully LOCA/HELB qualified ? | expert group 3 | OL1/OL2: The following cable types are fully qualified for OL1/OL2 LOCA requirements: Habia HFI 260 / HFS 105 XL Type B, Rockbestos Firewall III, Asea-Kabel/Liljeholmens Kabelfabrik Lipalon cables and Habia PI/PFA insulated / ETFE sheathed supescreened coaxial cables ("NIM-054"). (Please note that in OL1/OL2 LOCA conditions do not include submergence.)
FI-104 |  | Cables expert group | Finland | 03. Electrical cables | 3,1,3 | For both Loviisa and Olkiluoto , under which environmental conditions (temperature/irradiation) are cables in deposit? | expert group 3 | OL1/OL2: Based on environmental monitoring results the sample cables in the deposits of OL1/OL2 are exposed to temperatures ranging from 30 °C to 50 °C and dose rates ranging from < 10 Gy/a to 110 Gy/a. OL3: Cable deposits for accident proofed cables will be mounted adjacent to a main cooling pipe. Deposits for other samples will be located in upper levels of containment under representative environmental conditions of these cable types. Since the plant hasn't started there is no results from condition monitoring available. Results from the deposits of the reference plant are comparable with OL3 deposits for accident proofed cables. In the reference plant results have shown temperatures around 40 °C to 50 °C and radiation dose rates of <0,5 Sv/h. Loviisa: The deposits are located in the steam generator room. One deposit in a harsh conditions (ca. 70 °C) and other two in milder conditions (ca. 60 °C and 55 °C). During the operation all the deposits are exposed to ionizing radiation and the humidity is ~90%.
FI-105 |  | Cables expert group | Finland | 03. Electrical cables |  | Comparison of characteristic seems to have been done between cables coming from different deposit (submitted to both to harsh and mild environment). What are the main insights obtained ? | expert group 3 | OL1/OL2: The condition monitoring cables from mild and harsh environment are different types, because of which direct comparison of characteristics is not possible. However, standard PVC cables which have been in use in harsh environment since the start-ups and taken for sample cable use just lately, seem to have withstood the harsh environment very well. Loviisa: The ageing is faster in harsh conditions but not significantly.
FI-106 |  | Cables expert group | Finland | 03. Electrical cables |  | Is the Condition monitoring-method for insulation of low voltage cables (< 1 kV) based on mechanical characteristic (elongation at break) or does it also considers e.g. physic-chemical indicators, such as OIT? | expert group 3 | OL1/OL2: The condition indicator which represents the aging conditioning of the cables best is elongation at break. OL3: Method will be based on same priciples than in OL1/OL2. Experience from the reference plant and qualification also shows that mechanical parameters such as elongation at break are sensitive to thermal and radiological aging. Loviisa: The CM is based on mechanical characteristics (elongation at break and tensile strenght).
FI-107 |  | Cables expert group | Finland | 03. Electrical cables | 27 | The Sienopyre cables have been requalified for extended operation. Was the qualification (ageing + LOCA test) performed on actual cable samples from the plant i.e. aged under realistic conditions)? If yes, what environmental conditions and age were those subject to before the LOCA test was implemented? | expert group 3 | Loviisa: Yes. The cables had been in use in the steam generator room; Power cable for 22 years and I&C cable for 21 years. The estimated conditions was an average temperature of 60 °C and radiation dose 6,66 kGy/a. Before the LOCA-tests cables were artificially aged to the years 2030 and 2040.
FI-108 |  | Cables expert group | Finland | 03. Electrical cables | 17 | Are the ( cable) penetrations part of the AMP for cables , or are those covered somewhere else? | expert group 3 | OL1/OL2/OL3: Cable penetrations are not part of the cable AMP. Tightness of Containment Electric Penetrations is monitored by reading the pressure gauges at certain intervals. Loviisa: Yes they are, except the penetrations of the containment which are covered in the AMP of the containment
FI-109 |  | Cables expert group | Finland | 03. Electrical cables | 17 | The TRP report seems to suggest that the AMP is prioritizes on cables that are "n the most harsh environment and unreachable during the operation, i.e. only reachable during outages, mainly the steam generator room in the containment". Does it means that theer might be safefy related cables NOT subject to the AMP? | expert group 3 | OL1/OL2: The condition monitoring sample cables are located mostly in the upper drywell of the reactor containment, where general temperature and radiation conditions are most demanding. Also the standard PVC cable samples representing the outside containment cable types are situated in the upper drywell to expose the samples for harsher environment than in actual applications. OL3: AMP for cables in OL3 conciders all safety related cables. Condition monitoring, sample cables and regular inspections focuses mainly on the cables inside the containment and other cables in harsh evironment. Loviisa: No. Every building and their cable's and cable ways are in the AMP of cables.
FI-110 |  | Cables expert group | Finland | 03. Electrical cables | 17 | Lovisa NPP is obliged to report to STUK on teh AMP every 4 yerrass. Could you plese detail of this mandfatory repporruion(content)? | expert group 3 | Loviisa: Finnish NPPs are obliged to report STUK every 5 years. It's Loviisa NPPs decision to report every 4 years. The reports mandatory content can be found on STUK's YVL-guide A.8
FI-111 |  | Cables expert group | Finland | 03. Electrical cables |  | It seesm that Olkiliuto does nto report on AMP to STUK every four years as Loviisa does. Why? | expert group 3 | OL1/OL2/OL3: TVO reports the condition monitoring results to STUK every five years, which is the reporting interval allowed by YVL Guide E.7, requirement 805.
FI-112 |  | Cables expert group | Finland | 03. Electrical cables |  | Are there any continuous monitoring inside the containment in Olkiluoto NPP to detect hot spots? If not why? | expert group 3 | OL1/OL2: It is not possible to perform environmental condition monitoring in OL1/OL2 containments e.g. with thermographic camera during operation, because the containments are filled with nitrogen. During 1990s there were campaigns in which radiation and temperature conditions of the sample cable deposits were investigated with dosimeters during operation and with thermographic camera directly after shutting down for outage. Recently the in-containment radiation and temperature conditions have been further investigated with data loggers and dosimeters during operating cycles 2013-2014 and 2014-2015. OL3: Environmental conditions will be monitored in locations of sample cable deposits and in addition on selected cable routes. Cable routes that are selected to be monitored are mainly in areas known to be problematic and some routes contain cables with e.g. lifetime restrictions. Regular inspections during outages will include also thermal imaging.
FI-113 |  | EC | Finland | 02. Overall Ageing Management Programme requirements and implementation | 14 | The licensees review and assess the effectiveness of their overall AMP on a regular basis: please specify the review frequency |  | TVO: Licence review is normally done every tenth year. Overall AMP effectness is reported every year on regulatory basis. Fortum: done once a year.
FI-114 |  | EC | Finland | 03. Electrical cables | 22 | What is the frequency of "extra periodical testing" for MV cables in Loviisa? What are the acceptance criteria for these electrical measurements? |  | Fortum: The word "extra" is misleading. The Condition monitoring (CM) measurements are done to medium voltage (MV) cables every four years. The insulation resitance should be >1 MΩ/kV reduced in 75 °C. For tanδ and Off-line partial discharge (PD) measurement results are compared on previous tests.
FI-115 |  | EC | Finland | 03. Electrical cables | 24 | What are the plans for the frequency of regular inspections at Ol3? |  | OL3: Regular inspections will be made during outages. Frequency depends on a fuel cycle (12-18 months). Preliminary plan is to divide the cabling of the plant in four different sections and perform visual and tactile inspections and measurements during each outage for one section. This way the whole cabling of the plant is inspected every 4-6 years.
FI-116 |  | EC | Finland | 03. Electrical cables | generic 17-30 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found. Only reference lists of cable technical documentation are provided in annexes 2&3. |  | Cable groups included in the AM have been described in general.
FI-117 |  | EC | Finland | 04. Concealed pipework | 30 | Loviisa NPP: Why is no AMP in place for seawater piping? Is there at least an ISI program for seawater piping in place? |  | Fortum: Sea water piping is covered by RI-ISI program for piping.
FI-118 |  | EC | Finland | 05. Reactor Pressure Vessels |  | No information is provided in the report on the possible presence of hydrogen flakes in RPV base material in any of the operating power reactors. How this issue was investigated? |  | TVO has sent analyses to authority 31.5.2013. Fortum: RPVs base material have been inspected with UT and no hydrogen flakes were detected
FI-119 |  | EC | Finland | 07. Concrete containment structures | 78 | Regarding the first paragraph on p78, could you provide more information about the decision-making process regarding cracks that are critical or damages which need special monitoring. What are the related criteria? |  | Fortum: There are no clear acceptance criteria defined for every different ageing machanism. The inspection guideline Y-05-00005 defines criteria for reporting and decision making for repair is based on engineering judgement.
FI-120 |  | EC | Finland | 07. Concrete containment structures | 84 | It is mentioned that TVO has developed an AMP for destructive and NDE tests of the concrete structures of the containment for OL1&2. Could you provide some more details of the content of this programme. |  | Containment material tests were in the -90's destructive test and TVO did drill concrete cylinders. Beginning of the year 2000 TVO did start to use more NDE test methods. Now TVO performs every five years same NDE tests. TVO is involved in Safir2018 and Energiforsk concrete research programs and one target in those programs is to develop and test concrete NDE methods.
FI-121 |  | EC | Finland | 07. Concrete containment structures | 86 | In the table, in the 3rd row (Development of existing concrete cracks), in the Comment it is written that there is a special inspection area. Is this special area the one mentioned at the top of page 90, where cracks occurred during construction of the reactor pit between +1,50 m and +4,80 m, and the area where there was fire damage in the annulus? |  | Yes and further on the locations of the observed cracks are presented in the figure 1 above. | ref to Figure 1 in worksheet "FI_Figs"
FI-122 |  | EC | Finland | 07. Concrete containment structures | general | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | Fortum: Containment liner plate inside concrete structures is not accessible for inspections, containment leak test every 8 years reveals possible leaks of the liner. One time visual inspection sample has been done for the bottom liner plate by drilling hole in the concrete. R&D has been done for drill hole samples e.g. embrittlement research of the concrete.
FI-123 |  | EC | Finland | 09. Overall assessment and general conclusions | 99 | The SALTO peer review is a comprehensive safety review covering the evaluation of programmes and performance for the safe continued operation of nuclear power plants on the basis of the IAEA’s Safety Standards and other guidance documents. Given that the operation of NPP units is extended beyond the original design lifetime, what is the regulatory view on the benefits to the licensee of inviting such a SALTO review, and does it plan to encourage licensees to invite such a review in the future? |  | In Finland, procedures to renew an operating licence for a plant currently in operation follows one for a new plant (renewal always involves a PSR). The renewal procedures do not include SALTO reviews but any such reviews which give information about the prerequisites for an extended service time are found advisable by STUK.
FR-1 | 1.1 | Slovak Republic | France | 01. General information | Pages - general | Is there a licensee´s ageing management database in place? How is it structured? Does it include acceptance criteria and trending to decide on the required steps for corrective actions? |  | A database for internal use contains all the information concerning ageing management. It comprises criteria regarding the suitability for continued operation and all elements/data for tracing the type of corrective measures possible
FR-2 | 1.2 | EC | France | 01. General information | 20 & 21 | CABRI reactor has been modified. Question: Does this change have an Impact in the AMP? CABRI and RHF are currently under periodic safety review. Question: is the review of the AMP covered by the safety review? |  | The complete renovation of the CABRI reactor led to the replacement and the addition of many new equipment and cables for EIPS (and not EIPS) equipment. This renovation significantly reduces the impact of ageing on the EIPS and of the installation in general (new equipment). As mentionned in the NAR, ASN considers that the ageing management program must be enhanced within the frame of the periodic safety review for CABRI and ILL HFR reactors.
FR-3 | 1.3 | EC | France | 01. General information | 33 | Research reactor, safety reviews and AMP "The periodic safety review is an important tool in research reactors ageing management" * Are they other actions part of the AMP that are performed outside the periodic of the safety reviews? * Since when are safety reviews performed at research reactors? Before that, in what consisted the AMP for research reactors? |  | As a general rule, ageing management is based on periodic safety reviews (every ten years) and a periodic preventive maintenance programme. An important part of the periodical safety reviews is devoted to the examination of conformity which goes beyond the controls and monitoring (insulation resistance, test pieces with irradiation programme). As mentioned in the NAR, PSRs were conducted on Orphée and ILL HFR reactors (respectively 1997,2010 / 2002,2017). For CABRI reactor, a safety review was performed in the renovation framework and one is undergoing (novemver 2017).
FR-4 | 1.4 | EC | France | 01. General information | 33 | Appendix 1 of the order of 30 December 2015:. "...The design is based on measures…", "The calculation method may supplemented by an experimental design method…." Questions: * Almost the complete fleet is operating since several years. What about the already operating equipments, are studies and experiment performed retroactively? * What about equipment supplied by sub-contractors, are these studies/experiments also required? |  | * There is no retroactivity in the design and manufacturing requirements. The equipment manufactured with the previous order don't have to be reassessed with the current one. * There is also no retroactivity for sub-contractors equpement because the notion of sub-contractor doesn't exist within the ministerial order. The responsability is endorsed by the manufacturer.
FR-5 | 1.5 | EC | France | 01. General information | 40 | Good practice: the ageing analysis sheets (AAS) (valid for the fleet) + the detailed Ageing Analysis Report (DAAR) (valid for the fleet) + UAAR specific to the reactor Question: How can the AAS/DAAR/UARR be linked to the TLAA/AMP as referred in the IAEA documents? |  | The EDF ageing management process meets all the requirements of the international standards. However the documentary structure put into place by EDF is different from that of the IAEA documents. In particular, the elements specified in the 3 IAEA documents, i.e. AMR, AMP and TLAA, are implemented within EDF through several documents with a different documentary architecture, which is more particularly the result of management of the EDF NPP fleet as a range of plant series.
FR-6 | 1.6 | EC | France | 01. General information | 43 | The Wenra reference level I3.1+I2.3 are taken into account by the order of 10 November 1999 and article L593.18 of the Environment Code. The other levels are taken into account "semi-officially". Question: What does this mean? Is it possible to communicate evaluation results of other reference levels individually? |  | As described in 2.1.4.1, ASN issued different positions regarding ageing management, especially since 2001, for NPPs. Each of these letters addressed to the unique NPP licensee in France can cover different WENRA reference levels. For example, ASN letter dated 19/02/2001 covers reference levels I1.1, I2.1, I2.2, partially I2.5, I3.2. It is consistent with other ASN letters mentioned in the national report.
FR-7 | 1.7 | EC | France | 01. General information | 45 | Structure of the process: Question: since when the 4-step approach has been adopted and implemented? |  | Following the ASN's requests from 2001, EDF has adopted and implemented the 4-step approach since 2004 for the the preparation of the 3rd PSR of 900 MW NPPs.
FR-8 | 1.8 | EC | France | 01. General information | 46 | "For each reactor undergoing VD3 and the subsequent ten-yearly outage inspection (VD), drafting of an ageing analysis report specific to the reactor…" Question: * Are they no other actions part of the AMP and specific to the reactor performed outside the VD3/VD4? |  | The NPP ageing management programme (PLMV) is implemented between 2 VD, in addition to the maintenance programmes; the AAS are reviewed every year and may lead to new maintenance activities to be run between 2 VD.
FR-9 | 1.9 | EC | France | 01. General information | 52 | Question: Is it possible to have the list of the 12 component DAARs for the 900 MW and the list of the 9 for the 1300 MW? |  | The current DAARs for the 900 MWe NPPs are: Reactor pressure vessel, Reactor coolant system piping, Pressurizer, Steam generator, Reactor coolant pump, Main auxiliary piping, Reactor pressure vessel internals, Instrumentation and control system, K1 electrical cables, Containment penetrations, Containment building, Civil engineering structures The current DAARs for the 1300 MWe NPPs are: Reactor pressure vessel, Reactor coolant system piping, Steam generator, Reactor pressure vesselinternals, Instrumentation and control system, K1 electrical cables, Containment penetrations, Containment building, Civil engineering structures
FR-10 | 1.10 | EC | France | 01. General information | 52 | Local AMP (PLMV) Questions: Are the local AMP consistent and structured the same way between the different NPPs of the fleet? Is it possible some examples of local AMPs? |  | The PLMV must have the same structure but its content depends on the plant unit concerned, such as its specific design and operation features. The PLMV is the result of the analysis performed for the UAAR, which consists in a document established by EDF and examined by ASN during its inspections on ageing management.
FR-11 | 1.11 | EC | France | 01. General information | 53 | "The actions to be scheduled to manage ageing of SSCs for the ten years period following the VD…" It means that there are actions to be performed after the VD. Are these actions of which type? Corrective/preventive/conditional/monitoring? In page 32, the scheme describe the ageing management as actions to be performed only in preparation of and during the VD, clarification? |  | The type of actions contained in the PLMV may concern surveillance, corrective or preventive maintenance of the equipment. The PLMV is the result of the analysis performed for the UAAR, which consists in a document established by EDF and examined by ASN during its inspections on ageing management. Page 32: the main ageing management actions are carried out during VD (exceptional maintenance, installation modifications, main primary system hydrotesting, etc.), they contribute to the unit DAAR, itself based on the ten-yearly safety review leading to ASN's position regarding the unit's suitability for continued operation; other actions are also taken upstream of the VD, during interim VP and are incorporated into the DAAR
FR-12 | 1.12 | EC | France | 01. General information | 54 | "The monitoring, testing and inspection activities are more specifically contained in the Basic Preventive Maintenance (PBMP), Non-destructive testing (NDT) Programmes, the Supplementary Investigation Programmes (PIC) and in-service monitoring" Is ageing not managed as a programme in itself? It looks like ageing consists in the addition of part of other programmes? Can we consider that the maintenance of SSC qualification is sufficient for ageing management? |  | The equipment monitoring and inspection activities are contained in the basic preventive maintenance and/or specific (supplementary investigations, ...) programmes. Their aim is to search for damage identified on certain monitored items, as well as to ensure that there is no unexpected or feared damage (concept of defense in depth and supplementary programmes). The ageing analyses (AAS) evaluate the pertinence and adequacy of all of these programmes in the light of the ageing mechanisms identified. The NDT qualification certifcation is drawn up by an independent organization, which may be called on to analyse the feedback from implementation of these processes and, as necessary, review the qualification certificate. Moreover, as described in 2.3.3.5, the qualification of the SSCs for accident conditions has to been maintained through the gradual approach implemented by EDF and is considered as sufficient for ageing management.
FR-13 | 1.13 | EC | France | 01. General information | 54 | Good practice: Supplementary Investigation Programme (PIC) for the zones not covered by already existing measures (preventive or special maintenance) Question: has the PIC been specifically introduced for ageing management? |  | The PIC programme has been introduced from the 2nd PSR of 900 MW and 1300 MW NPPs, that is before the formal implementation of the current ageing management programme.
FR-14 | 1.14 | EC | France | 01. General information | 63 | Research reactors "..ageing management is based on periodic safety reviews.." Is there a specific chapter related to ageing management in the periodic safety reviews? Does it mean that there is no continuous and specific actions related to ageing management? |  | As a general rule, ageing management is based on periodic safety reviews (every ten years) and a periodic preventive maintenance programme. An important part of the periodical safety reviews is devoted to the examination of conformity which goes beyond the controls and monitoring (insulation resistance, test pieces with irradiation programme).
FR-15 | 1.15 | EC | France | 01. General information | 64 | Research reactors Ageing Management Programme: In the chapter "Assessment of ageing" obsolescence management is explained (not part of the scope of the peer review) and ageing management approach is not explained. It seems that the AMP for research reactors is mainly oriented towards obsolescence management. Question: Is ageing management not formally performed at the RRs?Does ASN consider that some parts/aspects of the EDF NPPs AMP could be applied to research reactors? If yes, which parts/aspects? |  | AMP for the CEA reactors is presently mainly oriented towards obsolescence management. No ageing management program is formally performed on RR. Ageing issue is addressed by the periodic maintenance program, periodic tests and inspections in PSR.That's why ASN stated in the report that the ageing management program must be enhanced within the frame of the periodic safety review for CABRI and ILL HFR reactors in 2017. EDF has adopted an approach to demonstrate the ageing management of the systems, structures and components (SSC) potentially affected. This approach is built around 4 steps: • SSC selection process: The SSCs potentially susceptible to ageing and whose failure can have an impact on safety are identified, • Individual analysis of ageing mechanisms: the ageing mechanisms for each SSC are identified and analysed, in order to check ageing management with regard to the operations and maintenance provisions in force. This step also comprises an analysis of the actual repairability and/or replaceability of the SSCs (contained in an Ageing Analysis Sheet (AAS)), • Additional actions and studies: when ageing management cannot be demonstrated by means of normal operating provisions, additional actions or studies are identified for ageing management (contained in a component Detailed Ageing Analysis Report (DAAR), • Drafting of a DAAR specific to the reactor, for each reactor nearing its VD3 and for the subsequent VDs, based on the AASs and component DAARs. These parts could be adapted to research reactors, considering that the operation feedback on RR woul be less important and the fact that a large number of equipment can be replaced.
FR-16 | 1.16 | EC | France | 01. General information | 67 | "on average, 5 inspections per year are carried out on this topic" Question: Since when is ASN making inspection specifically dedicated to ageing management? What the frequency of IRSN/ASN assessment specifically dedicated to evaluation of the AMP? |  | ASN performed inspections specifically dedicated to ageing management since the beginning of the 3rd PSR of the 900 MW NNPs. Regarding the generic AMP, it is assessed by IRSN/ASN in he frame of PSR of a NPP series. IRSN/ASN assess the NPP specific AMP after the PSR of each unit (it is part of the assessment of ASN for establishing its position for the continuation of operation.
FR-17 | 1.17 | EC | France | 01. General information | 30 & 32 | It appears that the periodic safety review and the ten-yearly outage inspections are used for the implementation of the AMP. * Are there actions of the AMP performed outside these periods? |  | Yes, some actions are performed outside the PSR and ten-yearly outage inspections (VD), even because of the duration of the VD they represent a privileged moment to conduct the actions of the AMP. For example the AAS are reviewed every year and the DAARs every 5 years. Moreover, some repair/replacement can be performed between 2 VD. Furthermore, preventive maintenance supported by the AAS is carried out.
FR-18 | 1.18 | EC | France | 01. General information | 40 & 41 | It appears that a structured and coherent ageing management programme has been requested by the ASN to EDF in 2001, with the view of the preparation of the first VD3? Questions: *Does this mean that a structured and coherent AMP was not requested and implemented before that? *Does this mean that the AMP mainly contain actions performed during the VD3, the same approach being used for VD4? |  | * Some ageing management was already performed but not in the structured way that has been implemented for the first VD3. Ageing management was addressed through the maintenance process, the supplementary investigations programme and R&D programmes; * The same approach will be used for the VD4 and ASN will issue its opinion on it by the end of 2018.
FR-19 | 1.19 | EC | France | 01. General information | 57 & 58 | Preventive and Corrective measures: Question: Has the maintenance programme evolved to take into account the ageing management since the introduction of the AMP? |  | The evolution of the maintenance programmes is mainly based on operating experience, which can concern ageing phenomena. Furthermore, preventive maintenance is supported by the AAS.
FR-20 | 2.1 | United Kingdom | France | 02. Overall Ageing Management Programme requirements and implementation | 45 | Section 2.3.1.1 states that each SSC/ageing mechanism combination is analysed as shown by an AAS (Ageing Analysis Sheet) the aim of which is to verify the degree of ageing management in the light of the operating and maintenance provision in force. It is further stated that for components or structures that cannot in principle be demonstrated by routine operating provisions, the production of a component Detailed Ageing Analysis Report (DDAR) is produced. The use of AAS and DDAR appears to be good practice. Please provide example templates for these documents. |  | The structure of an AAS is provided in appendix 10.2 of the national report (page 173). The structure of a component DAAR is as follows: - safety and regulatory requirements, - description of the component and its operating conditions, - rules and results of design analyses, - rules and results of manufacturing, - results of overall in-service behaviour operating experience feedback, - reminder of various ageing mechanisms or time-dependent damage modes, - for each damage mode or ageing mechanism considered to be sensitive:  a summary of scientific knowledge and OEF,  the damage kinetics,  the continued operation suitability criterion  the ageing countermeasures,  the in-service monitoring means,  in-service inspection,  the repairability of the zones concerned,  a summary for the zones concerned by this mechanism; - the obsolescence risks, - the industrial context, - the replaceability of the component
FR-21 | 2.2 | United Kingdom | France | 02. Overall Ageing Management Programme requirements and implementation | 51 | Section 2.3.2.1 classifies ageing mechanisms as confirmed or potential. Please explain what makes a mechanism confirmed or potential and what is done to further understand potential mechansms in order to confirm or dismiss them. |  | An ageing mechanism is "potential" if it is not mentioned in any OEF data, but its occurrence cannot be ruled out for the envisaged operating time-frame. An ageing mechanism is considered to be "confirmed" if it has been observed: - on a French unit of the plant series in question, or in a similar situation on a French unit of another plant series, - on a foreign PWR unit with construction and functional characteristics similar to those of the component or element in question. The maintenance and operating provisions are implemented for the ageing mechanisms in order to mitigate and detect the effects of a mechanism, whether it is potential or confirmed. When the effects of an ageing mechanism are actually detected, the ageing mechanism shifts from "potential" to "confirmed" in the relevant AAS.
FR-22 | 2.3 | United Kingdom | France | 02. Overall Ageing Management Programme requirements and implementation | 60 | Section 2.4.2 discusses internal review and updating of the process. How does EDF senior management maintain oversight of the ageing management programme? What reports or key performance indicators are provided to senior management? |  | Ageing management is the subject of a process identified in the EDF QA system. It comprises oversight and results indicators, which are periodically evaluated during an annual review chaired by the management of the EDF engineering department (DPN and DIPNN), such as total number of AAS or new AAS.
FR-23 | 2.4 | Slovenia | France | 02. Overall Ageing Management Programme requirements and implementation | 59 | External assessment of the process (Page 59): IAEA LTO module for external assessment of ageing management is mentioned in the report; are there any plans also for conducting full scope SALTO missions in France? |  | EDF was subject to external assessment by IAEA on LTO module. At this date,there's no SALTO mission scheduled yet.
FR-24 | 2.5 | United Kingdom | France | 02. Overall Ageing Management Programme requirements and implementation | General | "There is little mention of the Safety Case / Design Basis and how it interacts with the AMP. Can you provide more details of this interaction? For example in the UK Surveillance Programme 9 (SP9) takes the pressure and temperature limits from the Safety case." |  | The safety functions to be complied with and the means implemented to achieve this are defined in the safety case which are reviewed at each ten-yearly inspection of type of reactor. The operating conditions of the Safety case are monitored through an accounting of the main primary system and main secondary system equipment situations in order to check compliance with the inventory of design transients used for the safety demonstration (accounting reports are periodically produced and are analysed in order to limit the occurrence of sensitive situations).
FR-25 | 2.6 | United Kingdom | France | 02. Overall Ageing Management Programme requirements and implementation | 48 | The process documents described in the NAR are the Ageing Analysis Sheets (AAS), componentDetailed Ageing Analysis Reports (DAAR) and Unit Ageing Analyis Report (UAAR). It is not clear how these are used to ensure that the effects of ageing are minimised or detected on the plant. Please explain how the AAS, DAAR and UAAR are used to produce procedures, instructions, operaitng limits etc. to manage ageing at the NPP. |  | The list of component AAS and DAAR corresponds to a generic approach which verifies the soundness of the monitoring and maintenance programmes established at the national level. The approach may lead to modification of these programmes to ensure management of ageing. The local implementation of this generic approach leads to a unit DAAR, which identifies the specific features of the site and the local monitoring and maintenance actions (PLMV) to ensure ageing management in the plant unit, in addition to the national level strategies. As an example, the Steam generator DAAR contains a criterion regarding the suitability for continued operation based on the ratio of plugged tubes that can lead to a limited lifetime for the SG and their replacement.
FR-26 | 2.7 | United Kingdom | France | 02. Overall Ageing Management Programme requirements and implementation | 45-52 | "Page 49 states the there are approximately 600 AAS's for the 900 MWe plant series and 500 for the 1300 MWe series. Page 52 states that there are only 12 component DAARs for the 900MWe series and 9 for the 1300 Mwe series. Please: 1 provide a list of the current DAARs 2 explain why there are so few DAARs" |  | The current DAARs for the 900 MWe NPPs are: Reactor pressure vessel, Reactor coolant system piping, Pressurizer, Steam generator, Reactor coolant pump, Main primary system auxiliary piping, Reactor pressure vessel internals, Instrumentation and control system, K1 electrical cables, Containment penetrations, Containment building, Civil engineering structures The current DAARs for the 1300 MWe NPPs are: Reactor pressure vessel, Reactor coolant system piping, Steam generator, Reactor pressure vessel internals, Instrumentation and control system, K1 electrical cables, Containment penetrations, Containment building, Civil engineering structures The number of component DAAR is linked to the number of AAS of status component 2, in other words, requiring an in-depth analysis. Most of the AAS have status 0, because the maintenance and operation provisions are appropriate and can demonstrate ageing management of these SSC.
FR-27 | 2.8 | United Kingdom | France | 02. Overall Ageing Management Programme requirements and implementation | 60 | EDF hosted an IAEA OSART mission in late 2014. Please summarise the findings of the mission relating to ageing management. |  | During the IAEA corporate OSART mission in 2014, the auditors considered that the ageing management process was "robust, comprehensive and effectively structured", while complying with the IAEA requirements. The audit summary is given below: "There is a robust ageing management process in place with reference to international programs (IGALL, research programs, EPRI, etc.). Ageing management is based on the fleet approach and grouping of equipment based on the functional characteristics in compliance with IAEA safety standard NS-G-2.12. The company has implemented a very comprehensive and effectively structured fleet-wide LTO (long term operation) programme. It consists of ageing management, in-service inspections and obsolescence control. The LTO programme is in correlation with VD4 for 900 MW units and VD3 for 1300 MW units (VD 10-yearly outage) preparation and long term operation with the vision of 60 years of plant service life. These programs are based on international authorities’ recommendations (IAEA, etc.). Internal operating experience, R&D and international inputs and experience are taken into account (International Generic Ageing Lessons Learned - IGALL, EPRI, INPO, etc.)"
FR-28 | 2.9 | United Kingdom | France | 02. Overall Ageing Management Programme requirements and implementation | 27-39 | The description of the regulatory framework places great emphasis on the periodic safety review (PSR) and the ten-yearly outage inspections. There is very little description of how ageing is managed between PSRs. Please explain the regulatory framework for ageing management between PSRs. |  | There is no specific regulatory requirements for ageing management between PSRs. As described in 2.1.4, ageing management is addressed mainly in ASN positions and since the VD3 of NPPs, at the request of ASN, a structured process is implemented by EDF. Otherwise, ageing is managed through other routine processes such as maintenance (ISI, repair, replacement,...), operating experience, R&D programmes... The NPP ageing management programme (PLMV) is implemented between 2 VD, in addition to the maintenance programmes; the AAS are reviewed every year and may lead to new maintenance activities to be run between 2 VD.
FR-29 | 2.10 | Bulgaria | France | 02. Overall Ageing Management Programme requirements and implementation | p. 53 | Is explained that “If a site specificity concerning ageing is detected, the NPP may be required to create a local AAS. This will be the case if: an SSC specific to the site and included within the perimeter of the process is subject to an ageing phenomenon not covered by the national AASs or if a local ageing phenomenon, not covered by the national AASs, is identified by the NPP”. Would you please share your experience about: what kind of specificity was detected and how you dealt with it? |  | Even if most of the equipment in the French units benefits from the plant series effect, there may be site specificities, more particularly with regard to the heat sink. They mainly concern: - the design of an equipment item, installed only on one unit and which is not the subject of a monitoring programme defined at the national level, - the particular situation of a unit with regard to its environment (marine environment, heat sink characteristics, etc.) However, as the process has been implemented on NPPs, local AAS identified for a specific SSC are less and less created and now most of them are considered in the generic AAS (e.g. filtering drums for heat sink, neoprene supports)
FR-30 | 2.11 | Bulgaria | France | 02. Overall Ageing Management Programme requirements and implementation | p. 62-63 | It was given information of how the ageing management programmes were evolved through years passed. Would you please share your experience with strengths (good practices) and/or omissions faced by EDF and how last were resolved? |  | Good practices: annual review of the AAS, involvement by all EDF units (national engineering and operations units, NPP, R&D…), plant series organisation ensures considerable OEF, CAPCOV R&D database of the various mechanisms, benchmarking with IAEA standards. Weaknesses: absence of criteria concerning suitability for continued operation by equipment => Integration in 2016 into the revision of the methodology guide and implementation in the products of the process.
FR-31 | 2.12 | Belgium | France | 02. Overall Ageing Management Programme requirements and implementation | 40 | Does the request to set up a structured and coherent ageing management programme in preparation for the first VD3 of the 900 MWe reactors apply only to 900MWe reactors or to all NPPs? Can you precise if EdF must already set up an ageing management program to the non-900 MWe reactors ? And if not, if they will have to set it up only for the first VD3 of the non-900 MWe reactors? For example, for Chooz B1 and 2, when does a similar request will be elaborated? |  | ASN required a structured and coherent ageing management programme since the VD3 of the 900 MWe reactors, and this programme is now also being implemented for the VD3 of the 1300 MWe reactors, which started in 2015. The VD3 for the N4 series are scheduled for 2029. The ageing management process will be initiated for these reactors in about 2024, with the preparation of a first set of AAS. It should be noted that, meanwhile, ageing is managed through other "routine" programmes: monitoring and maintenance programmes are applied to this plant series from its start-up, consistently with the ageing mechanisms identified for the equipment on the other plant series.
FR-32 | 2.13 | Belgium | France | 02. Overall Ageing Management Programme requirements and implementation | 45/49 | Selection of the SSC potentially susceptible to ageing and whose failure can have an impact on safety; Is there a screening between passive and active components? |  | Active and passive components are dealt with in the same way in the process products (AAS, DAAR).
FR-33 | 2.14 | Belgium | France | 02. Overall Ageing Management Programme requirements and implementation | 50 | "The list of ageing mechanisms considered is based on the list in appendix 3 of NSG-2-12 and the US-GALL." In the section "International Standards 2.2, France mentions the IGALL but not the US-GALL. Is it plan to establish in the future the list of ageing mechanisms based on the IGALL rather than the US-GALL? |  | The list of ageing mechanisms considered by EDF will be updated in accordance with the IGALL changes. The drafting of the EDF methodology guide defining this list predates the publication of the IGALL, which is why EDF used the US-GALL reference to define the ageing mechanisms. A benchmarking is under way by EDF with the current AMR, TLAA and AMP of the IAEA's international standards. Major changes to the IGALL should be examined and used as input data for the ageing management process at EDF.
FR-34 | 2.15 | Belgium | France | 02. Overall Ageing Management Programme requirements and implementation | 50 | "These AAS are open-ended documents with revision index, which are periodically reviewed and, if necessary, updated." On page 51, it is indicated that the AAS are annualy reviewed. Can you precise if this is the maximal period authorized between two reviews? Does this apply to all type of SSCs? Can you precise the number of open AAS? |  | The AAS are reviewed at the same time every year, as part of the ageing management process. This review applies to all the SSC eligible for the process. For the 900 MWe plant series there are about 600 AAS - while for the 1300 MWe series, there are about 500 AAS.
FR-35 | 2.16 | Germany | France | 02. Overall Ageing Management Programme requirements and implementation | 27-42 | France explains in detail the periodic safety review. Usually, ageing management is one of the many topics to be addressed in a periodic safety review. Some requirements for design and inspection are legally required for pressure equipment (primary and secondary side). It still remains unclear, wheather ASN provides more detailed requirements (laws, decrees, regulations, guides) specifically adressing requirements for ageing management to be implemented by the licencee. Can France confirm, that the French regulatory framework does not include specific regulations / guidelines for the ageing managment programme? |  | The periodic safety reviews required by the article L. 593-18 of the environment code and carried out every ten years include an assessment of the state of the installation and therefore of ageing management. Since the VD3 of the 900 MWe reactors, ASN required a structured and coherent ageing management programme, this programme being now implemented for the VD3 of the 1300 MWe reactors. The requirements imposed by ASN for ageing management are explained in its different positions described in 2.1.4.
FR-36 | 2.17 | Germany | France | 02. Overall Ageing Management Programme requirements and implementation | 42-44 | France explains its engagement in the development of international requirements with respect to ageing, i.e. participation in WENRA, IAEA Safety Standards and IGALL. Can France provide further information about the processes to include international regulations into the national regulatory framework with respect to ageing management? |  | ASN is in progress to complete the decisions for Basic Nuclear Installations. ASN continues to finalise the missing resolutions and regulatory guides, most importantly, those related to periodic safety review, operating rules and management system of the operators.
FR-37 | 2.18 | Germany | France | 02. Overall Ageing Management Programme requirements and implementation | 50 | In the French NAR it is stated, that the list of potential ageing mechanisms to be considered is primarly based on appendix 3 of NS-G-2.12 and US-GALL. On page 44 it is said, that France actively takes part in the IGALL project. Can France explain in more detail how new insights from the IGALL project will be incorporated in the ageing management programmes of the individual nuclear power plants? |  | The list of ageing mechanisms considered by EDF will be updated in accordance with the IGALL changes. The drafting of the EDF methodology guide defining this list predates the publication of the IGALL, which is why EDF used the US-GALL reference to define the ageing mechanisms. A benchmarking is under way by EDF with the current AMR, TLAA and AMP of the IAEA's international standards. Major changes to the IGALL should be examined and used as input data for the ageing management process at EDF.
FR-38 | 2.19 | Germany | France | 02. Overall Ageing Management Programme requirements and implementation | 52 | On page 52 it is stated that 12 component DAARs for the 900 MWe plant series and 9 for the 1300 MWe plant series have been developed. Please, list the 12 component DAARs for 900 MWe plant series and the 9 component DAARs for the 1300 MWe series. |  | The current DAARs for the 900 MWe NPPs are: Reactor pressure vessel, Reactor coolant system piping, Pressurizer, Steam generator, Reactor coolant pump, Main primary system auxiliary piping, Reactor pressure vessel internals, Instrumentation and control system, K1 electrical cables, Containment penetrations, Containment building, Civil engineering structures The current DAARs for the 1300 MWe NPPs are: Reactor pressure vessel, Reactor coolant system piping, Steam generator, Reactor pressure vesselinternals, Instrumentation and control system, K1 electrical cables, Containment penetrations, Containment building, Civil engineering structures
FR-39 | 2.20 | Germany | France | 02. Overall Ageing Management Programme requirements and implementation | 52 | No component DAARs have been mentioned for the third series of French NPPs, the N4 series (NPP Chooz and NPP Civaux). Why are no component DAARs developed for the third series of French reactors, the N4 series? |  | ASN required a structured and coherent ageing management programme since the VD3 of the 900 MWe reactors, and this programme is now being implemented for the VD3 of the 1300 MWe reactors, which started in 2015. The VD3 for the N4 series are scheduled for 2029. The ageing management process will be initiated for these reactors in about 2024, with the preparation of a first set of AAS. It should be noted that, meanwhile, ageing is managed throug other "routine" programmes: monitoring and maintenance programmes will be applied to this plant series from its start-up, consistently with the ageing mechanisms identified for the equipment on the other plant series.
FR-40 | 2.21 | Germany | France | 02. Overall Ageing Management Programme requirements and implementation | 60 | France stated that the effectivness of the French Ageing Management programme is assessed by the number of national OEF reports related to ageing. In contrast to the described indicator, IAEA NS-G-2.12 suggests in para.4.32 much more detailed indicators to assess the effectiveness of the ageing management programm. Can France explain in more detail how those indicators are taken into account when assessing the effectivness of the French ageing management programme? |  | The process indicators are determined partly on the basis of the quantitative change in the different AAS categories and the number of national operating experience reports (FIREX) related to equipment ageing, by overall trend analyses. The purpose of these indicators is to check the ability of the process to: - anticipate new ageing mechanisms (to be characterised by implementing appropriate monitoring and maintenance measures), - control the behaviour of the equipment for which one (or more) mechanisms have been confirmed with regard to installations safety.
FR-41 | 2.22 | Netherlands | France | 02. Overall Ageing Management Programme requirements and implementation | 2.2.2/p44 | Has France implemented the IAEA documents in its regulation and in the NPPs/RRs? In the report, no statement can be found to confirm this. |  | As described in 2.1.4.1, ASN issued different positions regarding ageing management, especially since 2001, for NPPs. Each of these letters addressed to the unique NPP licensee in France can cover IAEA requirements. The EDF ageing management process meets all the requirements of the international standards. However the documentary structure put into place by EDF is different from that of the IAEA documents. In particular, the elements specified in the 3 IAEA documents, i.e. AMR, AMP and TLAA, are implemented within EDF through several documents with a different documentary architecture, which is more particularly the result of management of the EDF NPP fleet as a range of plant series.
FR-42 | 2.23 | Netherlands | France | 02. Overall Ageing Management Programme requirements and implementation | 2.4.1/p60 | What were the main recommendations from the IAEA corporate review mission? |  | During the IAEA corporate OSART mission in 2014, the auditors considered that the ageing management process was "robust, comprehensive and effectively structured", while complying with the IAEA requirements. The audit summary is given below: "There is a robust ageing management process in place with reference to international programs (IGALL, research programs, EPRI, etc.). Ageing management is based on the fleet approach and grouping of equipment based on the functional characteristics in compliance with IAEA safety standard NS-G-2.12. The company has implemented a very comprehensive and effectively structured fleet-wide LTO (long term operation) programme. It consists of ageing management, in-service inspections and obsolescence control. The LTO programme is in correlation with VD4 for 900 MW units and VD3 for 1300 MW units (VD 10-yearly outage) preparation and long term operation with the vision of 60 years of plant service life. These programs are based on international authorities’ recommendations (IAEA, etc.). Internal operating experience, R&D and international inputs and experience are taken into account (International Generic Ageing Lessons Learned - IGALL, EPRI, INPO, etc.)"
FR-43 | 2.24 | Netherlands | France | 02. Overall Ageing Management Programme requirements and implementation | 2.4.1/p60 | When was the IAEA SALTO mission and what were the main findings? |  | EDF was subject to external assessment by IAEA on LTO module. At this date,there's no SALTO mission scheduled yet.
FR-44 | 2.25 | Netherlands | France | 02. Overall Ageing Management Programme requirements and implementation | 2.4.4/p61 | Compliance with all international standards on AM: did EdF really create an AM with an Overall AMP comprised of specific AMPs including the dedicated organisation and integrated approach as required by WENRA/IAEA or will that be the next step? |  | The ageing assessments defined in the international standards produced by the IAEA (AMP, TLAA) are evaluated by EDF in order to check the pertinence and adequacy of its own analyses (AAS, DAAR), this benchmark could supplement the ageing analyses carried out by EDF. In addition, the various stakeholders, ASN/IRSN and the IAEA, considered that the French approach met all the requirements of the approach recommended by the international standard (only the documentary structure is different). In these conditions, EDF wishes to retain its own approach and does not envisage strict application of the organisation defined by the IAEA (AMR, AMP, TLAA). Moreover, a benchmarking is under way by EDF with the current AMR, TLAA and AMP of the IAEA's international standards. Major changes to the IGALL should be examined and used as input data for the ageing management process at EDF.
FR-45 | 2.26 | Netherlands | France | 02. Overall Ageing Management Programme requirements and implementation | 2.6 | What (national and international) external operating experience and R&D infomation is used by the French RR community to setup and improve the AM? |  | The research reactors operators take account of the external operating experience from other plants. The operating experience come from different ways such as : - periodic event with a group of research reactor operator in France; - international meeting (IAEA or IGORR for example).
FR-46 | 2.27 | Netherlands | France | 02. Overall Ageing Management Programme requirements and implementation | 2.6 | SSG-10 has been mentioned in 2.2 but in 2.6 it has not. What is its current or future role? |  | As mentionned in the NAR, ASN has considered that the ageing management program must be enhanced within the frame of the periodic safety review for CABRI and ILL HFR reactors. It will be an opportunity to verify the application of the SSG-10 IAEA guide.
FR-47 | 2.28 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation |  | Regarding chapter 02 the French report is very detailed and well grounded. The technical specifications have been followed. The AMP for research reactors is given in a separate subchapter - 2.6 which is a little deviation from the techincal specifications. |  | /
FR-48 | 2.29 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 31 | What is the harmony between the-yearly inspections and periodic safety reviews? It is not clearly explained. |  | The periodic safety reviews are required by the article L. 593-18 of the environment code and must be carried out every ten years. The ten-yearly inspections(VD) are outages with a long duration, when some specific tests (e.g. hydropressure test of the main primary system or the pressure test of the containment building) or inspections (e.g. reactor pressure vessel) and conformity check are performed. Some of these tests are regulatory required to be performed every ten years (hydropressure test of the main primary system). Moreover, EDF takes advantage of these VD to implement modifications for safety improvements resulting from the safety reevaluation.
FR-49 | 2.30 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 34 | In Appendix 1… (grey background): what is "oligocyclic" fatigue? |  | Oligocyclic fatigue corresponds by definition to the very short-lived domain. It encompasses "plastic fatigue".
FR-50 | 2.31 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 35 | "NPE with a relatively high risk" is not a definite characterization. |  | The high level of risk is to be understood as risk category of the NPE. This category is obtained based on the pressure and the volume of the equipment. The categories are defined by the ministerial order of 15 december 1999.
FR-51 | 2.32 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 37 | In Article 15…: Pressure test must be performed with no serious defect and no significant leak. What do these mean: "serious defect" and "significant leak"? They are not definite terms. |  | A leakage is allowed during the pressure test if it is not due to a defect in the material, but for example on a valve. This notion is explained in the associated regulation.
FR-52 | 2.33 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 41 | Subsection 2.1.2 says: French regulations set no time limit on the operation of the facilities. Here (2.1.4.1) the term 'operating life extension' is introduced. These two statments do not seem to be in harmony. |  | The term "operating life extension" refers to an expression commonly used to mean that operation beyond some design assumptions is considered, but is not linked to a regulatory limit of operation.
FR-53 | 2.34 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 44 | IAEA Safety Standards NS-G-2.6, Maintenance, surveillance… The identification number of the guide is missing. |  | /
FR-54 | 2.35 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 45 | Detailed Ageing Analysis Report (DAAR): this type of documents are rather programs than reports. |  | No, this is an analysis report, see structure in previous response about AAS and DAAR.
FR-55 | 2.36 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 52 | What is the relation between 'Continued operability criteria' and ISI acceptance criteria (e.g. in RSE-M)? |  | The criterion for the continued operation suitability of an equipment item corresponds to the conditions necessary for maintaining an item with no corrective action, such as replacement or major repair. It is not necessarily linked to RSEM acceptance criteria (for example: the continued operation suitability of steam generator is based on the ratio of plugged tubes that can lead to a limited lifetime for the SG and their replacement.).
FR-56 | 2.37 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 55 | "NDT processes must be qualified..." Correctly: NDT systems must be qualified… |  | Qualification is defined by article 8 of the order of 10/11/1999, which mentions the notion of NDT processes. This notion is also taken up by the RSE-M.
FR-57 | 2.38 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 56 | Title of subsection 2.3.3.5 is different in the glossay (MQCA). |  | /
FR-58 | 2.39 | General AMP expert group | France | 02. Overall Ageing Management Programme requirements and implementation | 71 | ASN consideration that 'the specific aspects of the site and of each reactor could be better' should be demonstrated by examples. |  | ASN considers that the way the NPPs take into account the generic process to evaluate the ageing of their facilities could be improved. For example, during its inspections ASN noted that some SSCs or part of SSC specific to a reactor were not always properly addressed in its UAAR.
FR-59 | 2.40 | EC | France | 02. Overall Ageing Management Programme requirements and implementation | 43 | "Level I2.3 is taken into account by article L593.18 of the Environment Code. With regard to the other levels, they are taken into account “semi-officially” through the various ASN position statements presented in section 2.1.4." Could you please indicate in which ASN position statements the different WENRA RLs are taken into account? |  | As described in 2.1.4.1, ASN issued different positions regarding ageing management, especially since 2001, for NPPs. Each of these letters addressed to the unique NPP licensee in France can cover different WENRA reference levels. For example, ASN letter dated 19/02/2001 covers reference levels I1.1, I2.1, I2.2, partially I2.5, I3.2. It is consistent with other ASN letters mentioned in the national report.
FR-60 | 2.41 | EC | France | 02. Overall Ageing Management Programme requirements and implementation | 69 | "...the entire approach is currently being examined by ASN and IRSN so that, in early 2018, the opinions of and any recommendations by the GPR and the GPESPN can be collected regarding…." The ageing management approach taken by EDF was already reviewed in the frame of the VD3, does ASN or IRSN already foresee some critical points or issues that could come out from this entire review in 2018? |  | The examination by ASN and IRSN of the AMP implemented by EDF was presented in March 2018 to the experts committees: there are no critical points foreseen, even if some adjustments in the methodology used by EDF or further investigations should be addressed by EDF in the perspective of VD4. ASN will issue its final opinion on it by the end of 2018.
FR-61 | 3.1 | Poland | France | 03. Electrical cables | 89, 89-91, 94, 95, 95, 95, 95. | 1. With what frequency inspection activities are done for MV cables? What are the acceptance criteria? 2. Is there any testing, sampling or inspection activities performed by a third party certification organizations? 3. What are criteria used for selecting electrical cables within the scope of ageing assessment in the Jules Horwitz Reactor and the CABRI research reactors? 4. What is licensees experience of the application of AMP for electrical cables? There are no information about this in report. 5. What are criteria for taking any actions based on the insulation resistance measurements for the CEA research reactors? 6. What are frequencies of the EIP cables inspections by the ILL? It is only mentioned ‘systematically’. 7. What are technologies/technics of performed by the ILL tests used to assess ageing mechanism in electrical cables |  | 1. For NPP, the frequency is maximum every ten years and is reduced if some criteria are not met. For example, a criteria is defined on the drift observed regarding tangent delta evolution and its stability at different voltage levels. The criteria depends on insulation matérial (formulation). The tangent delta has been measured during the first years of operation by operators and by cable manufacturers when supplying cables. For ILL, the insulation of the 5,5 kV is continuously controlled by means of permanent insulation controllers (acceptance criteria = 200 kΩ). No 20 kV electrical cable control is required by the safety demonstration 2. Measurements are performed by accreditated laboratories or by using diagnostic tools that have been developed for NPP and validated on cables. Second level inspection is performed to judge on the quality of control. Data are post-analyzed by engineering team and R&D department of EDF in the case of NPP. For ILL, there is systematically an inspection performed by a third party certification organization before the commissioning of each modification related to electrical cables. 3. The cables selected as part of the ageing assessment are the "electrical" cables important for safety (EIPS) participating in the protection of interests (management of the radiological and conventional risks), required in case of earthquake and impacted by the loss of electrical power supplies, at least all neutron chain measurement cables. The failure of other cables assigned to shutdown leads to or promotes shutdown ; there are therefore no safety issues. The power supply cables are generally not selected because they are not irradiated much; however, they are subject to insulation control. Loss of power supplies should not result in loss of the EIPS monitoring or loss of the EIPS requirements. 4. The examination by ASN and IRSN of the AMP implemented by EDF was presented in March 2018 to the experts committees: there are no critical points foreseen, even if some adjustments in the methodology used by EDF or further investigations should be addressed by EDF in the perspective of VD4. Concerning the cables, progress have been made regarding decision criteria and ageing indicators used in NPP even if further developemnt or more in depth analysis are still in progress for specific issue (margin assessment regarding long term performances in harsh environment). ASN will issue its final opinion on it by the end of 2018. For ILL, as mentionned in the NAR report, the line resistances, the insulation and the sealing of containment penetration cables are controlled. The cables important to safety are checked systematically. Measuring channels cables are controlled yearly. Power cables are controlled through the programme of tests before each cycle, 3 to 4 cycles a year. The cables necessary for the availability of the facility are checked on a sampling basis. The inspections have revealed some cables whose cladding material has become embrittled through ageing after about forty years, through exposure to gamma radiation in the case of the neutron detector splice connectors. They have been replaced by mineral insulation cables.The number of cables necessary to replace is very small. 5. There are no systematic criteria. There are essentially technical criteria based on the measurement of insulation resistance. As an example, for the CABRI reactor : 1) for coaxial cables (neutron and failed fuel element detection systems measurements) insulation resistance > 108 Ohms, annual monitoring; 2) for low voltage cables: those of standard NF C 15-100. 6. Measuring channels cables are controlled yearly. Power cables are controlled through the programme of tests before each cycle, 3 to 4 cycles a year. 7. The insulation of the 5,5 kV is continuously controlled by means of permanent insulation controllers. The response of the measuring channels is controlled yearly with regard to their precision.
FR-62 | 3.2 | Bulgaria | France | 03. Electrical cables | p.76 | Could you provide more information about the methods used before the “delta tangent measurements” and “partial discharge measurements” used from 2013 and 2015 and the reasons for not using these two methods? |  | These methods were already used before 2013. However, the measurement techniques and maintenance tools (portable diagnostic devices) have evolved which enables to use these methods more frequently on site in case of indications during inspections.
FR-63 | 3.3 | Bulgaria | France | 03. Electrical cables | p.3.1.1.2.2 | Could you please clarify the possibility of combining semi-empirical model and multi-scale model methods for in-depth research and more accurate results? |  | The possibility of combining physico-chemical models (kinetiks) and other models (diffusion) to link these properties to structural and electrical properties of cables under normal and accidental conditions is under-way, based on experimental and R&D studies. Several research studies are underway and model are currently improved and validated by comparing results to measurements performed on cables (both artificially aged and aged within the plant).
FR-64 | 3.4 | Bulgaria | France | 03. Electrical cables | p.3.1.1.3.2 | Concerning the following: “The level of risk is assessed for a ten-year period (the time between inspections) taking into account the possible aggravation of the observed faults”, could you clarify is the faults observed during a given period of time the only parameter used for determining the level of risk? |  | The period of 10 years is linked to a regulatory requirements (reexamination of safety of each plant every 10 years). If some cables present degradations (category "degraded" or "non compliant"), they will be subject to complementary monitoring.
FR-65 | 3.5 | Bulgaria | France | 03. Electrical cables | p.3.1.3.1 | Regarding the following: “The monitoring programme for MV cables implemented since 2011 in accordance with international recommendations is based on the following activities:..”, could you provide more information about the monitoring programmes for MV cables before the year mentioned? |  | Before the year mentioned, monitoring program of MV cables was less structured and mostly based on periodical test and characterization of ageing phenomenon that has lead to failure during operation of the plant or during periodical tests
FR-66 | 3.6 | Bulgaria | France | 03. Electrical cables | p.3.4.1.2.1 | Concerning the following: “Identification of the predominant ageing phenomena has enabled the manufacturers to improve cable behaviour (improvement in the materials). Application of the ageing management programme will enable this improvement to be confirmed.”, could you provide more information about the role of the Regulatory body the process mentioned? |  | EDF informs yearly safety authority on learning and finding concerning cable ageing management program (main results of experiments, failure/defect detected...). TSO of regulatory body (IRSN) performs experiments on cable and technical monitoring.
FR-67 | 3.7 | United Kingdom | France | 03. Electrical cables | 75 | Section 3.1.1.2.1 This section lists the main diagnostic methods usable on site, specifically the visual inspection which describes what techniques are used to undertake it. It doesn't describe the use of thermographic cameras as a techniques to support the visual inspection. In the UK thermographic cameras are used to support its visual inspection. Has consideration been given to the use of thermographic cameras in support of a visual inspection and what was the outcome? |  | Themographic camera are used to determine hot spot especially in control and electrical cabinets and electrical junction boxes. Specific attention is given on MV equipments (evolution of temperature is monitored especially at electrical interfaces/junctions locations), As mentionned in the report, thermographic ckecks are performed on LV cables to detect any overloaded power cables.
FR-68 | 3.8 | United Kingdom | France | 03. Electrical cables | 91 | "Section 3.1.3.2 advises that each site carries out a periodic visual inspection of: i) a periodic ten yearly visual inspection of the zones of stresses identified by the initial inspection and that all the cables classified as degraded (or noncompliant and not yet corrected); and ii) every ten years, of the overloaded cables. Please explain the reason for the ten year period, if consideration has been given to reducing the period due to the symptoms of ageing mechanisms identified and what was the outcome of the considerations." |  | The period of 10 years is linked to a regulatory requirements (reexamination of safety of each plant every 10 years). If some cables present degradations (category "degraded" or "non compliant"), they will be subject to complementary monitoring.
FR-69 | 3.9 | United Kingdom | France | 03. Electrical cables | 92 | Section 3.1.4.2 advises of an example of under sized cables had been identified which had a theoretical overload of 150%. It also advises that substantial margins exist due to the LV cables produced to stringent technical specifications. Please prvide further details of the example. If one example of under sizing and theoretical overloading was identified, what measures were taken to provide the assurances that no other cables were undersized and theoretically overloaded? |  | Some LV cables supplying the pressuriser heaters display signs of degradations but didn't fail. They are subject to preventive replacement. Furthermore, an identification of all MV cables have been done to verify that there is no oversizing. Cables that are oversized have been replaced by considering that maximal temperature of conductor shall not exceed specified value in case of maximum loading + maximum expected outside temperature (both in and out of containment). Actions are on going concerning LV-power cables.
FR-70 | 3.10 | Finland | France | 03. Electrical cables | 27-44 | In § 2.1 and § 2.2 the report presents the periodical safety reviews, related to IAEA guides, ASN life time extension related letters 2001 and 2013 and design guide No. 22 2017. However, no AMP specific guidance is mentioned. Will this large experience related to the AMP be credited in the development of more specific regulatory guidance for ageing management? |  | The periodic safety reviews required by the article L. 593-18 of the environment code and carried out every ten years include an assessment of the state of the installation and therefore of ageing management. Since the VD3 of the 900 MWe reactors, ASN required a structured and coherent ageing management programme, this programme being now implemented for the VD3 of the 1300 MWe reactors. The requirements imposed by ASN for ageing management are explained in its different positions described in 2.1.4.
FR-71 | 3.11 | United Kingdom | France | 03. Electrical cables | 75 | Section 3.1.1.2.1 states there is no established rule between a drop in insulation resistance and a drop in its dielectric strength. Is there not strong empirical evidence that both are linked? |  | Permitivity and resistivity are different physical properties. Relationship between these both criteria is hard to establish in case of real material (heterogeneous materials, difficulty to establish diffusion law for loads within insulation…)
FR-72 | 3.12 | United Kingdom | France | 03. Electrical cables | General | Little information has been is given for new build. Given the value identified of visible inspections, how will this be addressed when cable tray wrapping, both fire load reduction and functional, is applied given there is little opportunity to inspect the cables? Has additional environmental monitoring been installed in known problem areas to help predict future cable condition over and above general monitoring? It is noted that whole cables are removed for tear-down rather than using samples. How are the replacement cables then monitored separate to the bulk cables given they may not be of identical manufacture? |  | New build is done by considering experiences gained on operating plants. Cable routes are modified to limit stresses in specific locations for examples. Hallogen free fire retardant cables are used rather than PVC… The choice of measuring environmental conditions by using fixed monitoring devices or through dedicated measurement campaign should consider several criteria (possibility of having more measurement with less instrumentation, robustness and accurracy of measurement devices, ...). Furthermore, cable routes are generally better identified and stress they will be submited to is assessed through more accurate models (temperature, irradiation). The validity of those models is assessed regarding measurement of environmental conditions done on site (during plant operation) for different NPP.
FR-73 | 3.13 | Switzerland | France | 03. Electrical cables | 58 | Textline28: '... part of a continuous improvement approach … is to classify the components…’ Is there any classification scheme by plant design (e.g. Safety Class acc. IEC61513)? |  | Classification scheme is proposed by operator and assessed by regulatory body. In NPP, there is no distinction for ageing management of cables regarding functional classification. All cables important to safety are within the scope of AMP program.
FR-74 | 3.14 | Switzerland | France | 03. Electrical cables | 83 | textline14: How big is the proportion of PVC-cables? Are there no problems in case of fire? |  | Insulation and jacket material includes a large amount of fire retardant. A large amount of MV-power cables outside the containment are PVC insulated cables in 900 MWe PWR. PVC has been replaced by PRC for 1300 MWe serie (for unipolar cables) and by hallogen free insulation for N4 (for all MV cables). All MV-cables that have been replaced by the mid of the 1990's are hallogen free. Hallogen free cables are used regarding their properties in case of fire (limitation of corrosive combustion gaz).
FR-75 | 3.15 | Switzerland | France | 03. Electrical cables | 96 | Textline11/20: What kind of insulation materials for cables are/will be installed in the Flammanville3 containment? |  | Hallogen free cables from two suppliers NEXANS and PRYSMIAN are installed in the Flamanville containment. Insulation matérials are mainly based on crosslinked PolyEthylene.
FR-76 | 3.16 | Czech Republic | France | 03. Electrical cables | 75 | "…the sheath is more exposed than the insulation. The sheath, therefore ages faster than insulant. If there is no sign of ageing of the sheath, it can generally be concluded that the insulant is not degraded." This very strong statement was proved or it follows from experiments on cables installed at French NPPs? There exist many examples with opposite ageing effect. Insulation was totally degraded, while jacket was in good condition. |  | The statement given in the report is true only for the following additional conditions : 1/The sheath usually consists of a polymer which is technically less elaborate than the polymer used in the insulant, and thus more sensitive to thermal/irradiation sollicitation 2/ the sheath is more exposed to stress than the insulant (especially on case of very low voltage where self heating doesn't play a significant role).
FR-77 | 3.17 | Czech Republic | France | 03. Electrical cables | 80 | "EdF has chosen to take samples of cables in service and not to install extra cables (control cables) on site" It means EdF has no cable deposits and evaluates only cables taken from the service. OK. In Chapter 3.2.1 and 3.2.2 is mentioned, that 14 MV cables and 2 LV cables from NPP were measured up to now. Does it really cover all the cable types in French NPPs? I would propose more measurements to estimate the actual condition than only 2 LV cables removed from NPP . |  | A lot of LV-cable deposit are scheduled on the 2018-2019 period. Priority has been given to LV cables with LOCA requirements at this stage (NIS + LV-power cables exposed to high irradiation). Samples that are chosen shall be representative of polymer formulation (by taking into account suppliers, concentration of main components) and submited to high stress. Stress considered are temperature (including self-heating), irradiation and risk of water exposure.
FR-78 | 3.18 | Slovenia | France | 03. Electrical cables | 74 | Section 3.1.1 (page no.74): Why are buried or trenches cables not considered in the report? |  | There are not buried or trenched cables that are "important to safety". Some AMP is done for those types of cables but have not been included to the present report for this reason
FR-79 | 3.19 | Slovenia | France | 03. Electrical cables | 74 | Section 3.1.1 (page no. 74): Why are the cables categorized only to MV and LV cables, while HV cables are not considered? |  | French AMP include all cables with nominal voltage under 10kV AC. There is no cable with nominal voltage value between 10 kV AC and 225 kV AC in French NPP (225 kV AC or 400 kV AC is tranformed to an alternative current with nominal rated voltage under 10 kV)
FR-80 | 3.20 | Slovenia | France | 03. Electrical cables | 74 | Section 3.1.1 (page no. 74): Why are not cables separated to different voltage levels? |  | French AMP include all cables with nominal voltage under 10kV AC. There is no cable with nominal voltage value between 10 kV AC and 225 kV AC in French NPP. As mentionned in the report, the cables are grouped in different categories : medium voltage cables, low voltage power cables, measuring cables (LV), instrumention and control cables (LV). Some phenomenon such as water tree degradation are strongly influenced by electrical field an dthus voltage,
FR-81 | 3.21 | Slovenia | France | 03. Electrical cables | 89 | Section 3.1.3 (page no. 89): Why there is no information about third party certification organisations? |  | Measurements are performed by accreditated laboratories or by using diagnostic tools that have been developed for NPP and validated on cables. Second level inspection is performed to judge on the quality of control. Data are post-analyzed by engineering team and R&D department of EDF in the case of NPP. For ILL, there is systematically an inspection performed by a third party certification organization before the commissioning of each modification related to electrical cables.
FR-82 | 3.22 | Slovenia | France | 03. Electrical cables | 79 | Section 3.1.1.2.3 (page no. 79): Do France NPPs intend to replace PVC cables considering the following practices: • IAEA SALTO missions recommendations that PVC cables should be replaced because of bad material properties, • some countries have already partly or totally replaced PVC cables (e.g. NPPs in Switzerland, Germany, Nederland…) |  | All PVC cables of the French units (classified or not) have been initially qualified and have been supplied based on strict technical specifications. The qualification and strict cable specifications have resulted in the installation of much higher grade PVC cables than the standard commercial cables offered by some other cable suppliers. Results of expetises of PVC cables removed from site show the good behaviour of PVC cables of French NPPs. Concerning the reaction in case of fire, PVC cables have been designed not to propagate fire (they are compliant to category C1 of NFC 32070). No large-scale replacement of PVC cables is envisaged as a preventive measure. If a cable needs a replacement the cable replacement is performed by using qualified cables using hallogen-free insulation. Hallogen free insulations are prefered regarding their availability (supply chains) and the gaz emitted in case of combustion (limitation of side effects like smoke opacity and chemical corrosivity of combustion products). Replacement cables are designed with respect to category C1 of NFC 32070 and to category B of IEC 60332-3.
FR-83 | 3.23 | Slovenia | France | 03. Electrical cables | 89 | Section 3.1.2, 3.1.3, 3.1.4 (page no. 89): What is the status of inaccessible, buried or trenches cables in France NPPs? |  | Cables important to safety in France are not burried or in trenches
FR-84 | 3.24 | Slovenia | France | 03. Electrical cables | 91 | The frequency for visual inspection is 10 years. Is this not too long frequency for visual inspection (page no. 91)? |  | The period of 10 years is linked to a regulatory requirements (reexamination of safety of each plant every 10 years). If some cables present degradations (category "degraded" or "non compliant"), they will be subject to complementary monitoring. t is therefore adapted regarding statements or evolution of observed parameters during inspection (visual + temperature measurement)
FR-85 | 3.25 | Slovenia | France | 03. Electrical cables | 89 | What is the status of HV cables in France NPPs for voltage level above 3kV (Chapters 3.1.2, 3.1.3, 3.1.4, 3.2, page. no 89)? |  | French AMP include all cables with nominal voltage under 10kV AC. There is no cable with nominal voltage value between 10 kV AC and 225 kV AC in French NPP (225 kV AC or 400 kV AC is tranformed to an alternative current with nominal rated voltage under 10 kV)
FR-86 | 3.26 | Slovenia | France | 03. Electrical cables | 96 | Are AMPs for cables in France NPPs fully implemented in accordance with national regulation and international standards (IAEA, iGALL…) (page no. 96)? |  | AMPs for electrical cables in French NPPs complies with the requirements of IAEA and especially with EPRI guides. AMP for electrical cables is also compliant with IGALL , as explained in chapter 2.3, even if the documentary structure differs sometimes from IGALL documents.
FR-87 | 3.27 | Slovenia | France | 03. Electrical cables | 89 | Which are third party certification organisations in France (Chapter 3.1.3, page no. 89)? |  | Measurements are performed by accreditated laboratories or by using diagnostic tools that have been developed for NPP and validated on cables. Second level inspection is performed to judge on the quality of control. Data are post-analyzed by engineering team and R&D department of EDF in the case of NPP. For ILL, there is systematically an inspection performed by a third party certification organization before the commissioning of each modification related to electrical cables.
FR-88 | 3.28 | Belgium | France | 03. Electrical cables | 86 | It is mentioned that EDF has decided not to bury the MV cables, thereby preserving them from water. Was it decided since the construction of the first NPP or a later decision? If they are burried MV cables important for safety, how is the ageing managed? |  | it was decided from the first NPP. So, it is the case for all NPP in operation (900 MWe, 1300 MWe, N4 and EPR). Some MV cables are in trenches but they are not "important to safety".
FR-89 | 3.29 | Belgium | France | 03. Electrical cables | 86 | It is mentioned that, for MV cables passing through galleries or trenches, measures put in place through the ageing management programmes enable damp conditions to be detected. Are these conditions detected by visual inspections? If yes, what is the frequency of these inspections? |  | An initial visual inspection was carried out between 2012 and 2015 for all MV cables, allowing to detect damp conditions. The follow up of cables submitted to these conditions is performed periodically by sampling with tangente delta and partial discharges measurements.
FR-90 | 3.30 | Belgium | France | 03. Electrical cables | 95 | For the Jules Horowits Reactor it seems that the cables important for safety were selected based on qualification tests performed by EDF. Was it also the case for the other Research Reactors (CABRI, ILL)? If not, did the licensees developed qualification programmes for demonstrating that the selected cables will be able to fulfill their safety function in accidental conditions? |  | For CEA RRs, most of the power, control or measurement cables (not only EIP cables) are cables for technical and nuclear power plants (CPTN) designed according to EDF technical specifications (CST). For ILL, specifications based on design reports are used to define insulation, section surface, fire resistance (in comparison with NFC 32070 norm), air tightness and irradiation level acceptance. When the gamma rate is high, mineral insulation is used.
FR-91 | 3.31 | Germany | France | 03. Electrical cables | 80, 83-84, 91 | EDF does not use/does not intend to use (the reviewer understands that the cable ageing management/sampling of LV cables has yet to start) cable deposits in order to extract samples for testing purposes. Instead EDF does use in-service cables. Cable deposits have the advantage of providing cables from an environment where several stressors (radiation and temperature) are the most severe and allow the conduction of destructive tests on these cables. Taking in-service samples requires careful attention to where these samples are taken. The criteria applied for the MV cable sampling process on p. 80 do not mention the dose rate as an selection criteria, p.83-84 mention that existing environmental stresses for MV cables were identified by visual inspection. A similar approach for LV cables is described on p.91. How are dose rates be identified or confirmed reliably by visual inspections? Temperature as a stressor might also be hard to evaluate if the actual temperature is somewhat near the design temperature? This also affects the classification process, e.g. when a cable is considered to be operated within design assumptions. Are these visual inspections periodically repeated? Is there an intervall specified after which the grouping and categorizing process of MV cables as described on page 83/84 is repeated or checked for being up to date? For LV cables a ten-year period is mentioned on p.84 |  | Dose rates have been measured through dedicated on site campaign in NPP of 900 MWe and 1300 MWe series during plant operation. These measurements were performed on a limited set of NPP considering the high standardization of NPP belonging to the same serie. These masurements enable to verify if cables are respecting maximum dose rate requirements given by RCC-E and to identify location where dose rate or temperature specifications are not respected. These measurements areas well used to identify the most stressed cable portions and to take samples from the plant for expertises (including destructive tests such as elongation at break, IRTF, OIT...). These measurements are completed by thermography campaigns to detect high temperature spots and to follow up heating of power cables and connectors.
FR-92 | 3.32 | Germany | France | 03. Electrical cables | 84-85 | On p.85 it is written that "a mapping of the installed LV cables has been produced, recording the part numbers of the LV cables for each group by sampling". This conflicts with p.84 where it is stated that "due to the very large number of LV cables (…), recording all the cable part numbers is out of the question". Which is the correct description of the situation? If no cable part numbers are recorded how can it be confirmed that the ageing management program considers all LV cable types (e.g. insulator materials) in use? |  | A mapping of the installed LV cables has been produced, recording the part numbers of the LV cables for each group by sampling. NPP suppliers have already identified each cables formulation and date of installation. A complete mapping is in fact not possible for all signal/control cables due to installed length. Routes are nevertheless quite good identified which enables to establish a cartography (temperature/irradiation sollicitation).
FR-93 | 3.33 | Germany | France | 03. Electrical cables | 89-90 | On page 89-90 the monitoring and cable sampling inspection procedure for MV cables is described, it says that both the diagnostic tests (tan delta, partial discharge and VI) and the risk assessment are carried out periodically. How often are these conducted? |  | Periodicity is adapted with respect to result of tangente delta measurement (variation of tangente delta with respect to different reference voltage…) and the stress to which cables is submitted to
FR-94 | 3.34 | Germany | France | 03. Electrical cables | 80-82, 89-91, 93 | On page 89-91 the periodic monitoring and cable sampling inspection procedures for MV, LV and neutron flux cables are described. All explicitly mentioned test are nondestructive in-service tests. The overview on the diagnostic tests on page 80-82 and the EDF experience feedback on p. 93 also mentions destructive testing methods (EAB, OIT etc.) conducted in the laboratory (presumably on sampled cables). Are these destrcutive test intended to be singular one-off tests or are they intended to be conducted periodically? Were the tested cables also subjected to LOCA-conditions ? |  | Destructive tests are performed periodically on a limited set of cables (periodicity is adapted regarding results of the test/ kinetiks of evolution of key parameteres monitored). Choice of cable depends on formulation and on stress to which it is submited locally. Destructive tests is performed on several portions of the same cable (that is entirely deposit) to have measurements (elongation at break, OIT, IRTF...) for different level of stresses . IRTF is performed for different concentric layer of insulation to have information on degradation depth (oxidation layer thickness, ...). Characteristic of aged cables are compared when possible to the same characteristic measured on cables of the same formulation (new and after an accelerated ageing test sequence).
FR-95 | 3.35 | Netherlands | France | 03. Electrical cables | 3.1.1.2.2 / p.78 | Could the results of the examinations of cable samples please be included in Fig.7 to show indeed the confirmation of the model for at least the first 35 years? |  | Experimental results is covered by intellectual property. EPR insulations that have been expertised after 35 years (naturally aged) have a measured elongation at break of more than 170 % (for the most exposed portion of cable deposit). This value depends strongly of formulation of EPR and this result is not representative of all EPR formulations.
FR-96 | 3.36 | Netherlands | France | 03. Electrical cables | 3.1.4.3 / p.92 | What were the criteria for deciding to replace the mineral coaxial cables for the N4 series now already? In 3.1.2.3 it is claimed that the outer Scotch27 cladding is only subject to long term degradation. Is the 2017-2029 time frame compatible with this long term, or are the cables replaced prematurely? If so, why? |  | Replacement of those cables is due to local deterioration of outer scocth during handling operation (EMC disturbance). Modification was decided with respect to increase availability of the plant (limitation of spurious trip)
FR-97 | 3.37 | Netherlands | France | 03. Electrical cables | 3.2.1 / p.93 | Regarding the 2015 faulty MV cable: why has the upcoming breakdown not been detected by successive previous delta-tangent measurements? |  | No breakdown occurred in 2015. Tangent delta measurement met its limit and therefore cable was replaced.
FR-98 | 3.38 | Cables expert group | France | 03. Electrical cables | 4 | What is the reporting interval established by ASN for EDF to inform on the status of 1E classified cable? |  | EDF has to update the synthesis report on DAAR "cable" every 5 years. Yearly, a presentation is done to ASN and IRSN by EDF on the state of degradation of cables including main learning (failure, monitoring/expertise results).
FR-99 | 3.39 | Cables expert group | France | 03. Electrical cables | 4 | As the concept of AMP of cables also relies on "Predictive lifetime studies", could you give examples of such studies on cables? Are such studies done on both new and used cables? In the case of latter, how old are the used cables considered |  | EDF develops kinetiks models on physico-chemical and an associated "multi-scale approach".The models needs time to be developed and validated : they are not mature enough to be substituted to measurements performed on aged cables. However, they provide an estimate of the cable service life and an evaluation of the state of a cable. The measurements combined with these predictive studies give a high level of confidence that cable operabilty will be maintained for the next 10 years. Several Ph D and experimental studies are on going to improve and validate these models.
FR-100 | 3.40 | Cables expert group | France | 03. Electrical cables | 73 | The TPR report seems to suggest that the AMP is applicable to the cables needed to " operate the reactor". Does that means that only 1E cables are considered within AMP? |  | All cables are considered (approach is not restricted to 1E cables)
FR-101 | 3.41 | Cables expert group | France | 03. Electrical cables | 75 | Is there any continuous monitoring inside the containment in the French NPP to detect hot spots? |  | Environmental monitoring are generally performed continuously during a limited time frame (one operating cycle / between two refueling)
FR-102 | 3.42 | Cables expert group | France | 03. Electrical cables | 75 | Are there any considerations regarding hot spots when the qualified lifetime is used as a basis of the maintenance? |  | Cables located in hot spots have specific monitoring. Qualified life time is not used as a basis of maintenance
FR-103 | 3.43 | Cables expert group | France | 03. Electrical cables | 94 | What are the criteria used for selecting electrical cables for ageing assessment in the Jules Horwitz Reactor and the CABRI research reactors? |  | The cables selected as part of the ageing assessment are the "electrical" cables important for safety (EIPS) participating in the protection of interests (management of the radiological and conventional risks), required in case of earthquake and impacted by the loss of electrical power supplies, at least all neutron chain measurement cables. The failure of other cables assigned to shutdown leads to or promotes shutdown ; there are therefore no safety issues. The power supply cables are generally not selected because they are not irradiated much; however, they are subject to insulation control. Loss of power supplies should not result in loss of the EIPS monitoring or loss of the EIPS requirements.
FR-104 | 3.44 | Cables expert group | France | 03. Electrical cables | 94 | For the CEA RRs, please clarify whether the cables beyond the group of neutron measurement cables (of the neutron safety monitoring system and of the failed fuel element detection systems) are addressed in the ageing management programme. |  | The cables selected as part of the ageing assessment are the "electrical" cables important for safety (EIPS) participating in the protection of interests (management of the radiological and conventional risks), required in case of earthquake and impacted by the loss of electrical power supplies, at least all neutron chain measurement cables. The failure of other cables assigned to shutdown leads to or promotes shutdown ; there are therefore no safety issues. The power supply cables are generally not selected because they are not irradiated much; however, they are subject to insulation control. Loss of power supplies should not result in loss of the EIPS monitoring or loss of the EIPS requirements. The control-command is designed with positive securities, the failure of a cable has therefore no impact on safety.
FR-105 | 3.45 | Cables expert group | France | 03. Electrical cables | 95 | For ILL, please clarify whether some categories of cables are considered of particular importance for safety and consequently are selected for specific ageing management activities |  | The cables which are required by the safety demonstration : measuring channels cables, power cables, actuators (pumps, motors, valves …). they are subject to yearly controls. Furthermore, a conformity analysis is done through periodic safety review for each equipement important to safety.
FR-106 | 3.46 | Cables expert group | France | 03. Electrical cables | 95 | For ILL and CEA RRs, could you provide more details regarding the acceptance criteria for specific ageing mechanisms |  | For ILL HFR, the acceptance criteria are the insulation for the 5,5 kV cables, the visual aspect during tests and maintenances, the precision for the control of the measuring channels (the acceptance criteria are defined in the safety documentation). For CEA RRs, there are essentially technical criteria based on the measurement of insulation resistance. As an example, for the CABRI reactor : 1) for coaxial cables (neutron and failed fuel element detection systems measurements) insulation resistance > 108 Ohms, annual monitoring; 2) for low voltage cables: those of standard NF C 15-100. The control-command is designed with positive securities, the failure of a cable has therefore no impact on safety.
FR-107 | 3.47 | Cables expert group | France | 03. Electrical cables | 95 | What are criteria for taking any actions based on the insulation resistance measurements for the CEA research reactors? What are technologies/technics of performed by the ILL tests used to assess ageing mechanism in cables? |  | For CEA RRs, there are essentially technical criteria based on the measurement of insulation resistance. As an example, for the CABRI reactor : 1) for coaxial cables (neutron and failed fuel element detection systems measurements) insulation resistance > 108 Ohms, annual monitoring; 2) for low voltage cables: those of standard NF C 15-100. The control-command is designed with positive securities, the failure of a cable has therefore no impact on safety. For ILL, specifications based on design notes are used to define insulation, section surface, fire resistance (in comparison with NFC 32070 norm), air tightness and irradiation level acceptance. When the gamma rate is high mineral insulation is used.
FR-108 | 3.48 | Cables expert group | France | 03. Electrical cables | 95 | What are frequencies of the EIP cables inspections by the ILL? It is only mentioned ‘systematically’. |  | see comment line 3 (point 1) : By the ILL, measuring channels cables are controlled yearly (insulation resistance and response of measuring channels). LV-power cables are controlled through the programme of tests before each cycle, 3 to 4 cycles a year (before each cycle). Continuous control of the insulation for HTA cables.
FR-109 | 3.49 | Cables expert group | France | 03. Electrical cables | 95 | For CEA RRs, is the verification of the insulation is the only activity carried out to check the ageing of the cables. What are the acceptance criteria established for this? |  | There are essentially technical criteria based on the measurement of insulation resistance. As an example, for the CABRI reactor : 1) for coaxial cables (neutron and failed fuel element detection systems measurements) insulation resistance > 108 Ohms, annual monitoring; 2) for low voltage cables: those of standard NF C 15-100. For the RJH, the insulation check is carried out only during calibrations as this ckeck is likely to degrade the cables (mechanical degradation during disconnection.
FR-110 | 3.50 | Cables expert group | France | 03. Electrical cables | 95 | For ILL, please provide more details on monitoring and testing activities carried out to verify the performance factors related to the line resistances, insulation and sealing of containment penetrations What are the related acceptance criteria? |  | The evolution of the line resistance is indirectly controlled during the response control of the measuring channels (acceptance criteria are defined in the safety documentation). The insulation of the 5,5 kV is done by the means of permanent insulation controllers. The control of the sealing of containment penetrations requires a large procedure with a pressurisation between the two containments, the armed concrete one and the metallic one (acceptance criteria is 20 m3/h for the whole confinement) .
FR-111 | 3.51 | Cables expert group | France | 03. Electrical cables | 95 | For CEA and ILL RRs, what measures are adopted when a defect on a cable is detected? Could you provide examples of cable replacements on those RRs. |  | For ILL, An analysis is done and the cable is replaced if necessary, complying with the processus of treatment of a non-conformity. The only replacement we have needed is the replacement of a few extension cables of sensors which are implemented near the reactor block due to the gamma rate, presently mineral insulation cables are in place for these applications. For CEA RRs, if failure occurs, the cable is replaced. There has been no cable replacement other than the ones to modify the path for reasons of physical separation (fire risk). These replacements were not related to ageing.
FR-112 | 3.52 | EC | France | 03. Electrical cables | 80 | EDF has chosen to take samples of cables in service instead of having cable deposits. Could you please describe more the replacement of removed samples. Are they replaced with same cable type as the original, or some new type? Can you explain in more detail the sampling of LV cables in sections? |  | Cables are replaced with the same cable type as original (same voltage/section/functional requirements under all service conditions). The sampling of LV cables in sections consist of performing measurement on different portion of the same cables that are not sumbitted to the same stress levels (external temperature/irradiation).
FR-113 | 3.53 | EC | France | 03. Electrical cables | 80 | Is the principle of taking samples of cables in service instead of having cable deposits applied also in the EPR? |  | Yes, similar approach is used for EPR FA3 and French NPP fleet.
FR-114 | 4.1 | Poland | France | 04. Concealed pipework | 105-106 | 1. With what frequency inspection activities are done for concealed pipework? |  | The frequency of the inspection activities depends on the concealed pipes and their functionality. Inspections are planned for certain concealed pipework through the "preventive national maintenance programme". For the other concealed pipework (not concerned by a "preventive national maintenance programme"), the AMP will lead to one inspection. The AMP process can lead to adapt the frequency ou extend the scope of the concealed pipework inspections : these conclusions will be reported in a "synthesis report", written for each NPP.
FR-115 | 4.2 | United Kingdom | France | 04. Concealed pipework | 103 | Section 4.1.2.3.1 states that "If some data are not available, BPWorks by default considers a conservative value for the analysis". Are there any examples where EDF has applied a level or scrutiny to these outputs to reduce these estimates where they may be overly conservative? |  | EDF used these default values of BPWorks or from its OPEX.
FR-116 | 4.3 | United Kingdom | France | 04. Concealed pipework | 106 | Section 4.2. When does EDF expect to complete the programme of inspections for the leading 900MWe sites, and is this timeframe considered acceptable by ASN? |  | The inspections have been completed for Fessenheim, Bugey and Tricastin. Furthermore, a "reverse schedule" is done from the 4th PSR (VD4) of each NPP to be able to make repair works on TRICE and important for safety pipes before the 4th PSR. The generic framework has been considered as acceptable by ASN, but ASN will assess this programme for each NPP to ensure that it is acceptable.
FR-117 | 4.4 | United Kingdom | France | 04. Concealed pipework | 105 | Section 4.1.2.3.2 mentions operating experience feedback in the context of inputs sought from other EPRI contributors. Have there been any defects or failures due t oageing identified within the fleet that are worth highlighting? Can any examples be highlighted from across your fleet? |  | EPRI meetings advise EDF to inspect weld bead on stainless steel. EDF did some complementary inspections and measures, complementary to the measures already done to check the corrosion. The inspections performed until now didn't hightlight any feedback.
FR-118 | 4.5 | United Kingdom | France | 04. Concealed pipework | 106 | Section 4.1.4 suggests that more work is required on the programme to be able to identify any corrective actions. Is there any indication at this stage on what the actions may look like e.g. are any gaps between the proposed arrangements and the current approach likley to be significant? In addition, what are the likley timescales to be in a position to fully identify any corrective actions for the fleet? |  | When the NAR was edited, preventive and corrective actions were not defined because the inspections were not completed. The inspections carried out on Tricastin and Bugey sites concluded that there are no corrective actions to be done. The inspections programme will be carried out on the oher sites. At this stage, EDF doesn't know yet what kind of repairs could be needed within the schedule of VD4. There is no "more works" : repairs are included and schedulded in the programme. EDF doesn't know yet what kind of repairs it could be but it is included in the "reverse schedule". Furthermore, the programme for Tricastin and Bugey concluded that there are no corrective actions to be done.
FR-119 | 4.6 | United Kingdom | France | 04. Concealed pipework | 107 | Section 4.4.1 confirms that the pilot programme at Bugey will, at some point, be expanded to the rest of the fleet. What is the basis for the continued confidence in the overall fleet position prior to the implementation of the overall programme? Is it based on a lack of evidence or lack of failures? |  | A full analysis is conducted on each NPP, depending of the specifities of each NPP. Bugey is a "pilote NPP" with Tricastin because their VD4 are before the other NPPs ones. The analysis is integrally redone for each NPP since they are not totally a duplicate from Bugey or Tricastin. For each NPP, the OPEX of the previous NPP inspections is included.
FR-120 | 4.7 | Finland | France | 04. Concealed pipework | 102 | Concerning the scope of AMP, what is the amount of concealed pipelines in ground and in concrete in NPPs and other nuclear facilities? |  | The amount of concealed pipelines in ground and in concrete in NPPs studied until now is : Bugey : 78 379 m (in ground : 72774m / in concrete : 5605m) Tricastin : 37 657 m (in ground : 31682m / in concrete : 5975m) Fessenheim : 31 888 m (in ground : 27664m / in concrete : 4224m) Gravelines : 102 844 m (in ground : 95355m / in concrete : 7489m) Dampierre : 66 643 m (in ground : 60519m / in concrete : 6124m) Blayais : 66 582 m (in ground : 55399m / in concrete : 11183m) Percentage of safety significant pipework: see Table 1.jpg | ref to Table 1 in worksheet "FR_Figs & Tables"
FR-121 | 4.8 | Finland | France | 04. Concealed pipework | 102 | Are also reinforced concrete pipes, possibly with steel tube inside the concrete in the scope of AMP? If so, are there corre-sponding findings? |  | The reinforced concrete embedded steel cylinder pipes are included in the AMP because all the pipes corresponding to the criterion of concealed pipework is included in the analysis, whatever their material is. However, for the reinforced concrete embedded steel cylinder pipes, which are already covered by a specific preventive maintenance programme, no additional inspections are planned as part of the expertise on buried piping, since this maintenance ensures the durability of the requirements associated with these pipes. The operating experience feedback of the application of the AMP (through the specific preventive maintenance programme) for CBAT lead to reinforce the dispositions and frequencies of preventive maintenance (2 visites per cycle instead of one for the SEC-essential service water system piping in Paluel, Penly and Flamanville NPPs).
FR-122 | 4.9 | Finland | France | 04. Concealed pipework | 107 | What are the corresponding safety and operation challenges, like maintaining safe shutdown condition, flooding risks, etc. connected to AMP? |  | The analysis includes the failure consequences whatever the initiating event (internal event, hazard…). It is weighted in BPWorks software.
FR-123 | 4.10 | Bulgaria | France | 04. Concealed pipework | p.102 | Would you please clarify which concealed pipes were included into the scope of ageing management? |  | The concealed pipes included in the programme are all the pipes buried in the ground or placed in poorly accessible or inaccessible trenches (whatever the material, function, conveyed fluid, gravity flow or pressurised pipes, ...). For examples, the following systems are included in the AMP : CRF( Circulating Water System), JPD- JPU (Indoor or outdoor Fire-Fighting water distribution system, RAZ ( Nuclear Island Nitrogen Distribution system).
FR-124 | 4.11 | United Kingdom | France | 04. Concealed pipework | 107 | It is noted that EDF is planning to apply a new approach to management of buried pipework based on a study at Bugey and that this is being examined by ASN & IRSN. What is the objective of this examination and how will the application of the new approach be regulated across the fleet? |  | As part of its review of EDF AMP for the VD4, ASN /IRSN are assessing this new approach used by EDF. The generic framework has been considered as acceptable by ASN, but ASN will assess this programme for each NPP to ensure that it is acceptable. At this stage, ASN is not considering that there is a need for regulation. However, IRSN/ASN will assess the NPP AMP after the PSR of each unit, as part of the assessment of ASN for establishing its position for the continuation of operation.
FR-125 | 4.12 | Slovenia | France | 04. Concealed pipework | 102 | Section 4.1.1, page 102: What are the groups of concealed pipes that are subject to the AMP? |  | The concealed pipes included in the program are all the pipes buried in the ground or placed in poorly accessible or inaccessible trenches (whatever the material, function, conveyed fluid, gravity flow or pressurised pipes, ...). For examples, the following systems are included in the AMP : CRF( Circulating Water System), JPD- JPU (Indoor or outdoor Fire-Fighting water distribution system, RAZ ( Nuclear Island Nitrogen Distribution system)
FR-126 | 4.13 | Slovenia | France | 04. Concealed pipework | 102 | Section 4.1.2, page 102: Is there no problem of deposits/pipe fouling observed in concealed pipelines? This would be much easier to comment if the groups/functions of concealed pipework systems from Section 4.1.1 were known. |  | Some deposits were observe in raw water pipes, but without occlusion. If the occlusion risk is high according to BPWorks, EDF recommends to inspect the pipe from inside (televisual inspection).
FR-127 | 4.14 | Slovenia | France | 04. Concealed pipework | 105 | Section 4.1.2.3.1, page 105: What does the term “minimum thickness” of the pipe wall mean? Does it refer to the minimum allowable thickness that a pipe wall should have in order to withstand nominal stresses during operation? If so, why are the pipelines with a smaller wall thickness value than the minimum one (condition CA2) not replaced at once, i.e. without any tests or verifications? |  | The term « minimal thickness » refers to the « minimum thickness allowable for a pipe wall to withstand nominal stresses during operation ». The CA2 condition is still conservative. This condition aims to better characterize the default. It prevents the replacement of pipes that do not need replacing. The CA2 condition still has margin in.
FR-128 | 4.15 | Slovenia | France | 04. Concealed pipework | 105 | Section 4.1.2, page 105: What R&D programmes are used, if any? |  | No EDF R&D programmes were used. The method is based on the ASME code and EPRI work.
FR-129 | 4.16 | Slovenia | France | 04. Concealed pipework | 105-106 | Section 4.1.3, page 105-106: Are the inspections of concealed pipes carried out periodically? If so, what is the period of inspections? |  | The frequency of the inspection activities depends on the concealed pipes and their functionality. Inspections are planned for certain concealed pipework through the "preventive national maintenance programme". For the other concealed pipework (not concerned by a "preventive national maintenance programme"), the AMP will lead to one inspection. The AMP process can lead to adapt the frequency ou extend the scope of the concealed pipework inspections: these conclusions will be reported in a "synthesis report", written for each NPP.
FR-130 | 4.18 | Belgium | France | 04. Concealed pipework | 105 | Inspections will be carried out by making excavations in the ground or opening in trenches in order to gain access to the pipe to inspect. Are these plannified inspections or opportunistic inspections? In case they are plannified, are these one-time inspections or inspections with a defined frequency? |  | If EDF may sometimes do opportunistic inspections, inspections are mostly planned either once or based on "preventive national maintenance plan"
FR-131 | 4.19 | Belgium | France | 04. Concealed pipework | 103 | According to the description given in §4.1.2.3.1, the BPWorks uses a points system to estimate the risks of failure : points are assigned to each consequence of the failure (safety, security, loss of production). In this methodology, is it ensured that piping important for safety but whose failure would have no other impact (on loss of production for example) are rated at a high risk? |  | BPWorks can rate piping important for safety at low risk but EDF upgrades them systematicaly to high risk to include them in the analysis.
FR-132 | 4.20 | Germany | France | 04. Concealed pipework | 107 | The AMP for concealed piping are still in preparation. For the definition of the inspecion programme for NPP new inspection methods are envisaged that are currently under development. What kind of inspection methods are considered to be exploitable within the next 5 years? |  | For the inspections related to AMP, EDF tested some unconventional methods (pulsed eddy current, inspections by scanner-robot) and used them up to now. For future sites, these methods will be used if the conventional methods do no permit to get the escompted results.
FR-133 | 4.21 | Netherlands | France | 04. Concealed pipework | 4.1.2, p.102 | AMPs for concealed pipework is under development for French NPPs, therefore not all information is presented as requested by the TPR technical specification. Since the operating conditions, pipe material and diameter as well as environment can influence the degradation mechanism, ageing effects and, hence, ageing management activities, could you please provide this information? |  | Input data for the design of the piping (material, diameter, …) are known, are specific for each system and are included in the analysis. The program covers a broad scope of pipes. For example for the Tricastin's NPP : - diameters can be from DN25 (RAZ pipe) to DN3480 (CRF pipe). - materials can be carbon steel, stainless steel, cast iron, concrete, HDPE, ... - the variation is also on other parameters like the kind of transported fluid, pressure, temperature, flow, ... CRF (Circulating Water System), JPD- JPU (Indoor or outdoor Fire-Fighting water distribution system, RAZ ( Nuclear Island Nitrogen Distribution system)
FR-134 | 4.22 | Netherlands | France | 04. Concealed pipework | 4.1.2.3.1, p.103 | Is it correct to assume that in a BPWORKS software all concealed pipelines are grouped in accordance with the failure probability due to corrosion? Is there distinction made between different types of corrosion mechanisms? What were the input parameters for the BPWORKS software? |  | BPWorks addresses a degradation mechanism (corrosion) and identifies 5 ageing effect or risks : ID break, ID leak, OD break, OD leak and occlusion. BPWorks doesn't distinguish different types of corrosion. See the section 4.1.2.3.1.
FR-135 | 4.23 | Netherlands | France | 04. Concealed pipework | 4.1.2.2 | Are any provisions made for identifying other degradation mechanisms - besides corrosion, which is identified by the BPWORKS software? |  | BPWorks addresses a degradation mechanism (corrosion) and identifies 5 ageing effect or risks : ID break, ID leak, OD break, OD leak and occlusion.
FR-136 | 4.24 | Concealed pipework expert group | France | 04. Concealed pipework | 102 | Paragraph. 4.1.1 - Give a description of the groups of concelaled pipework for each of the 19 EDF sites. |  | Pipes on nuclear sites are assigned to a basic functional system. Each NPP has its own functional system. For examples, the following systems are included in the AMP : CRF (Circulating Water System), JPD- JPU (Indoor or outdoor Fire-Fighting water distribution system, RAZ ( Nuclear Island Nitrogen Distribution system)
FR-137 | 4.25 | Concealed pipework expert group | France | 04. Concealed pipework | 103 and 107 | Paragraph 4.1.2.3 and paragraph 4.4 - The ageing analysis procedure, using the BPWorks software developed by EPRI, is "based on a generic approach carried out on the Bugey pilot site which, once validated and adapted, will the applied site by site" and its application is currently examined by ASN and IRSN. So, at the moment which ageing management program is in force in each NPP? |  | At the moment, ageing management is adressed by the "preventive maintenance programme".
FR-138 | 4.26 | Concealed pipework expert group | France | 04. Concealed pipework | 106 | Paragraph 4.1.3 - Describe the monitoring, testing, sampling and inspection activities performed by the licensee for each NPP, giving details about the frequencies and the acceptance criteria. Give also information about the inspection history identifying trends and progressive deterioration in French NPPs about concealed pipework. |  | For corrosion risk, the programme recommends to make UT measures. For occlusion risk, the programme recommends televisual inspection. Inspection history is an input to the BPWorks software. A FFS (Fitness For Service) method (ASME code) is carried out to evaluate the period in which the pipe is fit for service (or the time when repair is needed)
FR-139 | 4.27 | Concealed pipework expert group | France | 04. Concealed pipework | 106 | Paragraph 4.1.4 - Is it not in force for each NPP the ageing management programme that allows to have information about the preventive and corrective actions that have been identified, also resulting from the past experience about the corrosion, for example, of concealed pipework. What does it mean that "the preventive and corrective actions are not defined in this stage of programme progress"? |  | When the NAR was edited, preventive and corrective actions were not defined because the inspections were not completed. The inspections carried out on Tricastin and Bugey sites concluded that there are no corrective actions to be done. The inspections programme will be carried out on the other sites. At this stage, EDF doesn't know yet what kind of repairs (not identified by the present maintenance program) could be needed within the schedule of VD4.
FR-140 | 4.28 | Concealed pipework expert group | France | 04. Concealed pipework | 106 | Paragraph 4.2 - Give a short description of the buried pipe inspection programmes established in each site. Please give also information about the results of inspection in progress. Formulate an evaluation on the adequacy of the SSC specific AMPs according to WENRA TS (page 19). |  | Here is a short description of the buried pipe inspection programmes established in the first NPPs : - Bugey : 12 systems inspected (18 zones / 18 sections) => The FFS analysis concluded that the inspected pipes will ensure their functions until 2040. - Tricastin : 6 systems inspected (11 zones / 17 sections) => The FFS analysis concluded that the inspected pipes will ensure their functions until 2039, except for a pipe of the JPU's system which function is ensured until 2035. EDF recommends to inspect again this system in 10 years to monitor the thickness loss. This monitoring could be done by measuring the thickness of the sections already analysed in 2016 and on the adjacent sections. - Fessenheim : 12 systems inspected (17 zones / 29 sections) => The FFS analysis concluded that the inspected pipes will ensure their functions until 2040, except for 4 sections of the JPD's system for which the analysis is still in progress.
FR-141 | 4.29 | Concealed pipework expert group | France | 04. Concealed pipework | 107 | Paragraph 4.4.1 - The Report doesn't describe the ASN experience from inspection and assessment as part of its regulatory oversight. Please give information, also evaluating from the regulatory point of view the adequacy of the licensee's SSC specific ageing management programmes. |  | As described in 2.7.1 ASN performed specific inspections specifically dedicated to ageing management since the beginnig of the 3rd PSR of the 900 MW NNPs (on average, 5 inspections per year are carried out on this topic). Concealed pipewoek AMP will be inspected as it will be implemented on NPPs. Regarding the generic AMP, it is assessed by IRSN/ASN at least for the first PSR of a NPP series. IRSN/ASN assess the NPP AMP after the PSR of each unit (it is part of the assessment of ASN for establishing its position for the continuation of operation.
FR-142 | 4.30 | Concealed pipework expert group | France | 04. Concealed pipework | 106 | Section 4.1.4 – The NAR does not contain any detail relating to preventative and corrective actions for concealed pipework and states “The preventive and corrective actions are not defined at this stage of programme progress.” Section 4.1.4 of the WENRA NAR technical specification states that “The NAR should describe key preventive and remedial actions that have been identified for each NAR example.” Please can you provide some detail relating to the criteria for taking actions, procedures for taking actions and description of the actions to be taken? |  | When the NAR was edited, preventive and corrective actions were not defined because the inspections were not completed. The inspections carried out on Tricastin and Bugey site concluded that there are no corrective actions to be done. The inspections program will be carried out on the different sites. At this stage, EDF doesn't know yet what kind of repairs (not identified by the present maintenance program) could be needed within the schedule of VD4. A FFS (Fit For Service) method (ASME code) is carried out to evaluate the period in which the pipe is fit for service (or the time when repair is needed)
FR-143 | 4.31 | Concealed pipework expert group | France | 04. Concealed pipework | 107 | Section 4.4.1 – Please can the objectives of ASN’s examination of the “application” used by EDF France be explained further. Is it to test the adequacy of the process, or just to ensure that it is correctly implemented at station level? |  | The objectives of ASN examination is to address both aspects, process and implementation on sites. This examination is part of ASN assessement as described in 2.7: regarding the generic AMP, it is assessed by IRSN/ASN at least for the first PSR of a NPP series. Further, IRSN/ASN assess the NPP AMP after the PSR of each unit (it is part of the assessment of ASN for establishing its position for the continuation of operation. ASN also performed specific inspections specifically dedicated to ageing management since the beginnig of the 3rd PSR of the 900 MW NNPs (on average, 5 inspections per year are carried out on this topic). Concealed pipewoek AMP will be inspected as it will be implemented on NPPs.
FR-144 | 4.32 | EC | France | 04. Concealed pipework | 106 | CABRI: What is the design and materials of concealed piping? |  | During the CABRI works, a large number of underground pipeworks were renovated including the industrial effluent system. Rainwater and sanitary network: PVC and glazed stoneware; City water: black steel. Industrial effluent network: PVC and glazed stoneware (these pipes undergo a televisual inspection and waterproofing every 3 years).
FR-145 | 4.33 | EC | France | 04. Concealed pipework | 106 | High Flux Reactor Grenoble: What happens to the reactor when the cooling water system breaks? What is the material of the cooling water system pipe (carbon steel with protective coating on outer surface?)? |  | The cooling system is not an equipemnt important to safety : it is not required after the shutdown of the reactor, the natural convection being sufficient. The cooling system is made out of carbon steel with protective coating on outer and inner surfaces.
FR-146 | 4.34 | EC | France | 04. Concealed pipework | 101-107 | 900 Mwe PWRs: What is the design and materials for concealed pipework? How will the ageing management program and in-service inspection program for concealed piping that is currently underdevelopment look like? |  | The program covers a broad scope of pipes. For example for the Tricastin's NPP : - diameters can be from DN25 (RAZ (Nuclear Island Nitrogen Distribution system) pipe) to DN3480 (CRF (Circulating Water System) pipe). - materials can be carbon steel, stainless steel, cast iron, concrete, HDPE, ... - the variation is also on other parameters like the kind of transported fluid, pressure, temperature, flow, ... The inspections carried out on Tricastin and Bugey site concluded that there are no corrective actions to be done. The inspections program will be carried out on the different sites. At this stage, EDF doesn't know yet what kind of repairs could be needed within the schedule of VD4.
FR-147 | 5.1 | United Kingdom | France | 05. Reactor Pressure Vessels | 113 | Section 5.1.1.5 – Page 113 – final paragraph – The classification using the Ageing Analysis Sheets (AAS) is useful to see where the highest risk items are from a perspective of ageing. Please provide some details on how this process works. An example would be useful. |  | §2.3.2.1 answers this question: it explains the general classification process of the AAS, based on the analysis of ageing mechanism and its proven or potential character, the possibilities of repair / replacement and the maintenance provisions implemented. This classification procedure is applied in the same way to all components, including the RPV.
FR-148 | 5.2 | United Kingdom | France | 05. Reactor Pressure Vessels | 119 | 2nd paragraph – It is interesting that there is a regime of sampling (speculative) inspections for the RPV. Please provide some more information on this regime? |  | The Investigation Complementary Program consists of consolidating the relevance of preventive maintenance of equipment by confirming the absence of deterioration occurring in service in areas that are not normally monitored. The investigations are conducted, by survey, under the defense in depth; there is therefore no defect a priori sought.
FR-149 | 5.3 | United Kingdom | France | 05. Reactor Pressure Vessels | 120 | 1st paragraph – There is a substantial amount of useful data that will have been accumulated over the operation of these reactors that would useful worldwide to assist in predicting irradiation behaviour. How can this be used for the benefit of the international community? |  | The data of the "PSI" are EDF property. However, EDF regularly communicates on its "PSI" internationally. The last communication took place at the ASTM STP1603 Workshop: International Review of the Nuclear Reactor Pressure Vessel Surveillance Programs of June 29, 2016. The compilation of the papers of this workshop is being published
FR-150 | 5.4 | United Kingdom | France | 05. Reactor Pressure Vessels | 121 | 1st bullet – What is the typical extent of the defects detected in the nozzles? |  | The underclad defect of reference (representative of all the defects detected in the French nuclear fleet) is 12 mm large x 60 mm long. Some specific defects size were defined on some reactors, when the detected defects were not enveloped by the generic defect.
FR-151 | 5.5 | United Kingdom | France | 05. Reactor Pressure Vessels | Genera | General comment – There is no discussion on the issues discovered at Le Creusot. Please provide an update on the current position. |  | The issues discovered at Le Creusot are not concerned by ageing mechanisms so far. Anyway, the review of the manufacturing process files is still ongoing. No unacceptable non-conformities have been detected so far.
FR-152 | 5.6 | United Kingdom | France | 05. Reactor Pressure Vessels | General | General – There is no discussion on resolution of WENRA recommendations following the discovery of hydrogen flaking at Doel/Tihange? Has this been addressed for all French reactors? |  | Following the discovery of the defects due to hydrogen in the RPV of Doel 3 and Tihange 2, ASN asked EDF to review the In Service Inspection carried out on the RPV. This examination allows to detect hydrogen flakes in the first 80 mm of the shell walls. In addition, at the request of ASN, EDF conducted a control of the entire RPV core area of the Blayais 2, Bugey 3, Cruas 3, Dampierre-en-Burly 3, Gravelines 4 and Penly 2 reactors. No defects were highlighted.
FR-153 | 5.7 | Finland | France | 05. Reactor Pressure Vessels | General | The list of abbreviations could be provided. |  | A list of abbreviations is given ine the Appendix 10.1 of the NAR
FR-154 | 5.8 | Finland | France | 05. Reactor Pressure Vessels | 115, 125 | There is no reference to the MacLean model. Could you give a reference to the MacLean model? |  | If you look at §5.2.2, you can notice that the MacLean model was used to determine a thermal ageing model from results obtained by low alloy steel aged for 20,000 hours at temperatures between 300°C and 550°C.
FR-155 | 5.9 | Slovenia | France | 05. Reactor Pressure Vessels | 110 | Scope of the RPV AMP (page 110): On which bases are the degradation mechanisms affecting RPVs parts identified? Which AMPs for the management of the aging mechanisms were established? |  | With regard to ageing mechanisms, the procedure is described in paragraph 2.3.2.1. The identification of mechanisms is based on knowledge, developed notably by national and international REX (nuclear structures) and R&D. It is integrated into the products of the ageing control process (FAV and DAPE) that are applicable in France (equivalent to the IAEA standard, AMP, ...)
FR-156 | 5.10 | Slovenia | France | 05. Reactor Pressure Vessels | 130 | Irradiation ageing/monitoring of the core zone (page 130): In the report stay that the approach adopted by EDF consists of several steps. The first step is evaluation of fluence. How is fluence received by the RPV evaluated and how is most highly irradiated point (hot spot) determined? The last step is margins calculations. What are mechanical margins and how are they calculated? |  | The fluence is estimated by calculations taking account of the operating parameters (reload pattern, time of the cycle). These calculated fluences are confronted to the fluence level determined by the tests performed on 'PSI' capsules placed and withdrawn every ten years from each RPV (programme monitoring radiation effects). (see § 5.1.2.1 and 5.1.3.1.1). The most highly irradiated point (hotspot) is modelised on the basis of these calculations with an extrapolated value at the end of lifetime. Mechanical analyses are performed for the most penalizing thermalhydraulic transient of each category. Margins are calculated by dividing the tenacity (KIC) by the stress intensity factor (Kcp). - The tenacity considers a shift of RTNDT (provided by an embrittlement formula, 'FFI ' formula, based on the 'PSI' results). - The stress intensity factor is calculated at the highest stresses zone, taking into account safety coefficients (a) that depend on the likelihood of a transient (1.2 < a < 2). The criteria is : KIc/a . Kcp >1.
FR-157 | 5.11 | United Kingdom | France | 05. Reactor Pressure Vessels | General | "There is little mention of the Safety Case / Design Basis and how it interacts with the AMP. Can you provide more details of this interaction? For example in the UK Surveillance Programme 9 (SP9) takes the pressure and temperature limits from the Safety case." |  | The safety functions to be complied with and the means implemented to achieve this are defined in the safety case which are reviewed at each ten-yearly inspection of type of reactor. The reactor vessel contributes to the safety objectives of the installation by demonstrating its integrity in any operating situation. Provisions are put in place in operation to contribute to this demonstration of its integrity, in connection with the control of ageing, notably through the implementation of a control approach to ageing, as part of the general principles of safety outlined in the safety case. The operating conditions of the Safety case are monitored through an accounting of the main primary system and main secondary system equipment situations in order to check compliance with the inventory of design transients used for the safety demonstration (accounting reports are periodically produced and are analysed in order to limit the occurrence of sensitive situations).
FR-158 | 5.12 | United Kingdom | France | 05. Reactor Pressure Vessels | 119 | "Section 5.1.3 - Implementation of test programmes to monitor properties which will be difficult to monitor on equipment in situ. Which components does this programme consider and which degradation mechanisms are monitored?" |  | The programmes to monitor properties concern the beltline zone. Samplings (metal capsules are removed from the material of the beltilne region) are used in the "PSI" (§5.1.3.1.1). The aim is to provide datas on the effect of irradiation by performing destructive tests on the metal capsules. For thermal ageing, experimental programs are used to validate predictive models of ageing over long operating periods. For the RPV the materials associated with specific experimental programs are: * low-alloy steels and their welds * the dissimilar weld
FR-159 | 5.13 | United Kingdom | France | 05. Reactor Pressure Vessels | 125 | "Section 5.2.1 - The core zone undergoes a complete automated ultrasonic inspection at each 10 yearly outage, covering the entire under-cladding zone. a. Please clarify what is meant by the core zone. Does this include the whole of the upper and lower core shell including the parent material? b. This isn’t an ASME requirement, is this inspected in-accordance with RSEM? c. Have inspections revealed any hydrogen flaking? d. Is there any radiography of the RPV or any other components within the containment vessel?" |  | a. The base material (25 first mm of the most irradiated zone) of the beltline zone as well as the welds are examined. The vertical extension of the monitored heart zone is defined according to the projected irradiation level at the end of life (criterion at 10 ^ 18 n / cm2). b. ASME requirements are not applied in France. The codes used are RCC-M and R-SEM. A specific maintenance programme is established in compliance with RSE-M code, at least every ten years, to define the qualitative and quantitative non-destructive tests performed on each SSC, such as RPV. c. No hydrogen flaking were detected. d. Radiographic testing are performed every ten years on nozzles, specially on bimetallic welds.
FR-160 | 5.14 | Switzerland | France | 05. Reactor Pressure Vessels | 119 | Exist for RTNDT a screening criterion as an acceptance limit alternative to a full fast fracture analysis? |  | Nor the RCC-M code either the RSE-M code define a RTNDT limit. The acceptance criteria is based on the calculation of the margin factor (KIc/a . Kcp >1, with a a security factor comprised between 1,2 and 2, depending on the likelihood of transients).
FR-161 | 5.15 | Switzerland | France | 05. Reactor Pressure Vessels | 121 | Section 5.1.3.4, Is a real time fatigue monitoring system used which includes the RPV studs? Is the influence of environmental effects (FEN-factors) taken into account? |  | None of the RPVS components are concerned by fatigue. Environmental effects are not taken into account for RPV studs as they are not in contact with the primary water.
FR-162 | 5.16 | Switzerland | France | 05. Reactor Pressure Vessels | 125 | In section 5.2.1, the report refers to a conservative deterministic approach for demonstration of fast fracture resistance, which uses a hypothetical defect whose dimensions are at the NDT detection limit. How is this NDT detect limit determined? |  | The non destructive examination performed on RPV are qualified in a specific way. The NDE are qualified in order to be able to detect certain type and size of defects. Mock-ups with known defects are used to qualify the NDE and check their performances.
FR-163 | 5.17 | Switzerland | France | 05. Reactor Pressure Vessels | 125 | Is only one postulated crack depth analyzed for fast fracture analysis? |  | There is only one postulated crack analyzed for fast fracture (5 mm x 25 mm), which is the smallest defect whose detection is guaranteed. If a real defect is detected, there is also an analysis based on the real size of this or these defects and its actual position which conditions the loading taken into account. The qualification of the process gives the detection limit
FR-164 | 5.18 | Switzerland | France | 05. Reactor Pressure Vessels | 125 | Demonstration of fast fracture resistance is carried out for “the most highly stressed and irradiated part of the RPV”. Does it mean, that different locations were investigated, because highest stresses and highest irradiations are found typically at different positions? |  | The fast fracture demonstration is performed assuming the generic defect at the highest stresses location, considering that this zone cumulates high stress AND hot spot. This approach is conservative.
FR-165 | 5.19 | Finland | France | 05. Reactor Pressure Vessels | Chapter 5.4.1 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? |  | EDF evaluates the most penalising thermal-hydraulic transients in each situation category from the initial conditions to the safe shutdown state and calculates the mechanical margins with respect to the risk of an incipient defect according to the above elements.
FR-166 | 5.20 | Belgium | France | 05. Reactor Pressure Vessels | 123 | What are the reasons that led to classify status 2 the AAS relative to thermal ageing of low alloy steels for the outlet nozzles? |  | The AAS relative to thermal ageing of low alloy steel for the outlet nozzles is classified status 2 because the mechanism is confirmed and there is no possibilty to repair or to replace.
FR-167 | 5.21 | Belgium | France | 05. Reactor Pressure Vessels | 124 and 132 | The ISI highlighted an indication in a BMI penetration at Gravelines 1 in 2011. This BMI penetration has been withdrawn and repaired. Is it foreseen to repair systematically flawed BMI penetrations or are did ASN/IRSN develop specific acceptance criteria? |  | If the crack is identified as due to CSC, ASN considered that it has to be repaired.
FR-168 | 5.22 | Belgium | France | 05. Reactor Pressure Vessels | 119 | In the frame of the Complementary Investigations Programmes, sampling inspections are also carried out on certain zones to confirm the absence of modes of degradation that had not been identified. Could more information be given about these sampling inspections: what kind of examinations and which zones are inspected? |  | The Complementary investigation program consists of consolidating the relevance of preventive maintenance of equipment by confirming the absence of deterioration occurring in service in areas that are not normally monitored. Investigations (NDT or expertises) are conducted, by survey, under the defense in depth; there is therefore no defect a priori sought.
FR-169 | 5.23 | Germany | France | 05. Reactor Pressure Vessels | 121/126 | In general all welded joints of the RPV are subject to recurrent inservice inspections. From the text on page 121 it appears that the flange/dome weld of the RPV upper heads are inspected recurrently only, if the first inspection revealed any defects. What is the reason for this exception, considering the fact that this weld is subject to bending moments, i.e. low cycle fatigue? |  | As demonstrated by mechanical studies, the flange/dome weld of the RPV upper heads with a defect lower than the generic defect is not subject to fatigue. If a defect is detected at the initial inspection, it's taken into in the mechancial studies and it is controlled every ten years.
FR-170 | 5.24 | Germany | France | 05. Reactor Pressure Vessels | 125 | A thermal ageing model for low alloy steels was validated by a complementary ageing programme to cover 60 years of plant operation. What are the predictions of this model for the base and weld metal and heat affected zone of the French RPV steel? How are they considered in the brittle fracture analyses? |  | The prediction of this model is different between the base metal /weld metal AND the heat affected zone. In fact, thermal ageing is more significant in heat affected zone because of the grain size. There are different RTNDT shifts defined depending on the temperature, the service life, the phosphorus content, the type of metal (base, weld, heat affected). For example, at 350°C, for 60 years, with a phosphorus content equal to 40ppm, the RTNDT shift is 9°C in metal base and 13°C in the heat affected zone. This shift is added to the RTNDT.
FR-171 | 5.25 | Netherlands | France | 05. Reactor Pressure Vessels | Ch.5 | The information provided in this NAR in its chapter 5 on ageing management of reactor pressure vessels, is to a great extent qualitative. However in the Technical Specification for the NARs, the countries are requested to report in their NARs on the acceptance and action criteria for the various ageing phenomena. Apart from indicating those criteria, it is obvious that the NARs must discuss the compliance of the reactors with these criteria. Could you please provide this information? |  | An evaluation accounting for the degradation of mechanical properties due to ageing is performed for each RPV every ten years to check that calculations respect all the criterias (e.g. usage factor < 1 , margin factor KIc / a . Kcp > 1). KIc is the tenacity; Kcp is the stress intensity factor; a is a safety coefficient that depends on the likelihood of a transient (1.2 < a < 2).
FR-172 | 5.26 | RPV expert group | France | 05. Reactor Pressure Vessels | 110 | I note that the RPV bodies and heads, for the CP0, CPY and some P4 reactors, are made to different design codes (ASME and RCC-M). How is the difference in code requirements for aging management handled, especially at points of intersection? |  | The fact of having different codes on the various RPV of the EDF fleet does not condition the ageing management. It should be noted that the use of the ASME at the origin has in practice resulted in the mechanical design of the equipment (mechanical analyzes), whereas the manufacturing was done according to the provisions of a codification. French (CPFC). Mechanically, studies are updated every ten years in accordance with regulations to incorporate the safety review reassessement and the operating feedback. On the occasion of these successive updates, all the studies gradually switched to the RCC-M code, including the components initially designed according to the ASME. The analysis results used to support and evolve the content of the FAV are therefore homogeneous throughout the EDF fleet in terms of study benchmarks. From the point of view of supply, most of the original CPFC provisions were transferred to the RCC-M when it was created. While some provisions may have evolved during the manufacture of the various levels (often in the sense of a strengthening of the requirements on the most recent levels), there are no fundamental differences between the components of the various levels concerning the materials used and the manufacturing process used. Ageing models used are developed or confirmed from materials tests representative of the entire French fleet, regardless of their original supply code
FR-173 | 5.27 | RPV expert group | France | 05. Reactor Pressure Vessels | 116 | In section 5.1.2.3 the report talks about dilution anomalies in buttering layers. How are the mechanical properties in these layers veriefied positively within the aging management system? |  | The toughness properties of dissimilar welds with dilution anomalies have been established on the basis of experimental tests and are taken into consideration in the fast fracture resistance analyses of these zones.
FR-174 | 5.28 | RPV expert group | France | 05. Reactor Pressure Vessels | 130-133 | How are the ageing management systems for the research reactors baselined against the aging management systems for the power reactors, and vice versa? |  | For NPPs, most of ageing aspects are linked to carbon steel, which is not used in RPV of research reactors (RR). There is though a potential common area for stainless steel, for which each ageing management process generally comprises similar items, such as a requirement of a low maximam value of ferrite rate. There are no aluminium parts in NPPs’ RPV and stainless steel is mainly used for cladding. The in-service inspection machine (MIS in French for machine d’inspection en service) is used on each ten years in the frame of ageing management inspection, notably to detect under cladding defects. There is no AMP to small parts made of austenitic stainless steel. In RRs’ RPV, structures are made of aluminium and stainless steel without any cladding. there is no reason to perform inspection using MIS on RR. Moreover, it is physically not doable. Ageing management program should be more formalised on RR. Ageing issue is presently addressed by the periodic maintenance program, periodic tests and inspections in PSR.That's why ASN stated in the report that the ageing management program must be enhanced within the frame of the periodic safety review for CABRI and ILL HFR reactors in 2017.
FR-175 | 5.29 | EC | France | 05. Reactor Pressure Vessels | Chapter 5.4.1.1, page 130 | In page 130 is indicated "for all the vessels, the zone subjected to neutron irradiation undergoes non-destructive inspections every ten years to check that no new defects have appeared and that existing defects have not evolved.". Question: Is this inspection performed only for the welds or also for the base material? |  | The control is carried out on all the welds of the RPV and also on the level of the base material situated in front of the core zone. The objective of this last control is to search the possible underclad defects.
FR-176 | 5.30 | EC | France | 05. Reactor Pressure Vessels | Chapter 5.4.1.2, page 131 | Correct "under-classing defects". It should be "under-cladding defects". |  | Typing error
FR-177 | 5.31 | EC | France | 05. Reactor Pressure Vessels |  | No information is provided in the report on the possible presence of hydrogen flakes in RPV base material in any of the operating power reactors. How this issue was investigated? |  | Following the discovery of the defects due to hydrogen in the RPV of Doel 3 and Tihange 2, ASN asked EDF to review the ISI carried out on the RPV. This examination allows to detect hydrogen flakes in the first 80 mm of the shell walls. In addition, at the request of ASN, EDF conducted a control of the entire RPV core area of the Blayais 2, Bugey 3, Cruas 3, Dampierre-en-Burly 3, Gravelines 4 and Penly 2 reactors. No defects were highlighted.
FR-178 | 7.1 | Bulgaria | France | 07. Concrete containment structures | chapter 7.1 | In conjunction with chapter 7.1 DESCRIPTION OF AGEING MANAGEMENT PROGRAMME FOR EDF CONCRETE CONTAINMENTS, please, clarify what methods and criteria for selecting components within the scope of the ageing management are used. |  | Methods and criteria are mentionned in §2.3.4.1. The SSC included in the AMP are the following: · SSCs important for safety (EIPS), · non-EIPS SSCs, for which ageing could lead to failures liable to compromise the design hypotheses adopted in the safety case; · non-EIPS SSCs which, with respect to the PSA (Probabilistic Safety Assessments) make a significant contribution to limiting the core melt risk. The containment is an SSC EIPS. All its components with a safety requirement are concerned by ageing analysis (concrete, prestressing cables, liner,...). The paints and non-reinforced coatings of the reactor building are included since they may call into question the hypotheses assumed in the safety demonstration. The instrumentation system is also included. It is not EIPS, but participates in monitoring the good behaviour of the containment.
FR-179 | 7.2 | Bulgaria | France | 07. Concrete containment structures | chapter 7.1 | In conjunction with chapter 7.1 DESCRIPTION OF AGEING MANAGEMENT PROGRAMME FOR EDF CONCRETE CONTAINMENTS, please, clarify what procedures for the identification of ageing mechanisms for the different materials and components of the concrete structures are used. |  | With regard to ageing mechanisms, the procedure is described in paragraph 2.3.2.1. The identification of mechanisms is based on knowledge, developed notably by national and international REX (nuclear structures) and R&D but also non-nuclear (dams, bridges).
FR-180 | 7.3 | Bulgaria | France | 07. Concrete containment structures | chapter 7.1.2 | In conjunction with chapter 7.1.2 ASSESSMENT OF AGEING OF CONCRETE CONTAINMENTS please clarify the key standards and guidance used to prepare SSC Aging Management Program. |  | The key standards and guidance used to prepare SSC Aging Management Program are : 1) The regulatory requirements listed in section 2.1.1. 2) The International Standards listed in section 2.2
FR-181 | 7.4 | United Kingdom | France | 07. Concrete containment structures | 140 | Section 2.3.2.1 refers to leaching of concrete being added to the AASs at the end of 2016. This information is not further described in Section 7.1.2 relating to concrete structures. Please provide further information on the nature of the leaching problem, why it was added into the AASs and what actions are taken following its discovery. |  | Concrete leaching refers to a phenomenon of concrete leaching by an aggressive solution (rain water, sea water...) which generally leads to its decalcification. The main consequences of this pathology are the surface degradation of the facing and the increase in porosity and permeability of the concrete. This phenomenon is not likely to suddenly change the mechanical strength of these structures during their service life. Visual inspections carried out under maintenance programme allow this phenomenon to be detected and defects to be treated if necessary (by patching, for example). Those inspections have not identified any leaching phenomenon in the the EDF safety related civil structures. However, following a recent comparison of the AASs with the AMR listed in the IAEA IGALL, it is decided that leaching will be incorporated in a future update of the AASs.
FR-182 | 7.5 | United Kingdom | France | 07. Concrete containment structures | 146 | Section 7.1.3.1 and Table 13 provide a summary of the monitoring carried out on the containment. For single wall containments and the inner wall of double wall containments reference is made to "U5 tests". Please provide a description of the "U5 Tests" carried out. |  | In the event of a severe accident, the U5 procedure consists of decreasing the pressure in the containment by using a sand filter that retains the radioactivity in the reactor building. The tank full of sand is tested every 10 years, taking advantage of the pressure test.
FR-183 | 7.6 | United Kingdom | France | 07. Concrete containment structures | 156 | Section 7.2.4 describes an Optimum Instrumentation System that is being deployed to all operational containments in the fleet. The system comprises the original instrumentation and any additional instrumentation that may be required in support of ageing management. This approach to ageing management appears to be good practice. Please provide an example of how this system has been implemented. |  | Facing sensors are deployed on all the NPP containments for example in the cylindrical part : 2 pairs of extensometers (1 tangential, 1 vertical) are installed. These facing sensors make it possible to follow the deformations of the concrete of the containments. They consist of a 1 m long Invar bar. One end is anchored in the concrete, the other end slides in a bar anchored in the concrete. The displacement between the 2 bars is measured to obtain the deformations of the concrete. see Figure 1.jpg | ref to Figure 1 in worksheet "FR_Figs & Tables"
FR-184 | 7.7 | Slovenia | France | 07. Concrete containment structures | 146 | Monitoring, testing, sampling and inspection activities for concrete containments (Page 146): Is there also requirements for material sampling and mechanical testing of the concrete containment material in France, beside described comprehensive scope of activities in this area? Are these requirements written in the plant procedures? Are maintenance activities for concrete structures also provided or evaluated by third party certification organizations? |  | There is no systematic requirement for material sampling and mechanical testing of the concrete containment material in France. The maintenance activities for concrete structures are evaluated by ASN and IRSN .
FR-185 | 7.8 | United Kingdom | France | 07. Concrete containment structures | 143 | Section 7.1.2.6 states that "Blistering of the liner is caused by deformation of the containment. This phenomenon has been observed on several 900 Mwe reactors". It is not clear whether this containment deformation relates to elastic movements of the concrete wall or due to localised degradation of the concrete / reinforcement behind the liner. Please clarify the cause of the blistering, the extent of deformations that have been observed to date and clarify if corrosion behind the liner is considered as an ageing mechanism? |  | Blistering of the liner is caused by elastic movements of the concrete wall, not to localised degradation of the concrete / reinforcement behind the liner. Corrosion behind the liner is considered as a potential ageing mechanism, in case a foreign object was left in the concrete during construction. That case has not been observed on the French NPPs.
FR-186 | 7.9 | United Kingdom | France | 07. Concrete containment structures | 154 | Section 7.3.6. lists the surveillance aspects performed on the metallic liner. There is no discussion on the required level of inspection competence required by personnel undertaking these inspections. Please provide information on the qualifications and experience requirements for inspectors to perform these activities and how these arrangements are managed. |  | Inspectors are trained and qualified to identify degradation by visual inspection and to measure thickness by ultrasonic means.
FR-187 | 7.10 | United Kingdom | France | 07. Concrete containment structures | 154 | Section 7.3.6. lists the surveillance aspects performed on the metallic liner. There is no discussion on the required level of inspection competence required by personnel undertaking these inspections. Please provide information on the qualifications and experience requirements for inspectors to perform these activities and how these arrangements are managed. |  | Inspectors are trained and qualified to identify degradation by visual inspection and to measure thickness by ultrasonic means.
FR-188 | 7.11 | United Kingdom | France | 07. Concrete containment structures | 154 | Section 7.1.4.2 discusses the application of protective coatings to the inner face of double containment structures. This section includes a statement that reads "The phenomena responsible for any increase in the leak rate diminish over time". It is not clear which phenomena this sentence is referring and also the claim that they diminish with time. Please provide more information on the phenomena being discussed and explain why these diminish with time. |  | The phenomena responsible for the increase in the leak rate of double containment are shrinkage and creep of the concrete, that lead to a progressive and slight detension of the tendons. Following the dessication of concrete, shrinkage and creep kinetics diminish over time, as currently observed on all pre-stressed civil structures.
FR-189 | 7.12 | United Kingdom | France | 07. Concrete containment structures | 155 | "Section 7.2.2 provides useful operational experience from the early 90s, and discusses corrosion flaws that were observed at various low points on the metal liner of the reactor containments of the 900 MWe series. In particular, the text discusses the peripheral local expansion seals at the interface between the basemat of the internal structures and the containment gusset, and the metal liner pressurisation channels at the bottom of the RB. The section goes onto to discuss the important remedial works that were undertaken but does not provide information on the root cause of corrosion. Please provide more information on the root cause of the corrosion and discuss whether (i) ground water ingress is considered as an ageing mechanism / threat to the steel components (ii) boric acid implications & (iii) other causes for water collection in the lower regions of the liner. " |  | The corrosion observed in the 1990s in the peripheral seal area and in the liner pressurisation channels is explained by the presence, in contact with the liner, of chlorinated pollutants resulting from the leaching of the initial material composing the seal between the containment and the basemat of the internal structures (Flexcell). This is why this material was replaced in the 90s. Water inflows into this area are not possible except in the event of an operating accident. Ground water ingress is very unlikely on the 900 MWe sites.
FR-190 | 7.13 | Finland | France | 07. Concrete containment structures | 138, 146 | What kind of feedback you have received regarding decontamination criteria and decontamination activities on paints and coatings from AMP? |  | The paints and non-reinforced coatings of the reactor building are included in the ageing management programme since they may call into question the hypotheses assumed in the safety demonstration.
FR-191 | 7.14 | United Kingdom | France | 07. Concrete containment structures | 139 | For 1300 Mwe and N4 plants it is stated that there is lost formwork on the inner surface of the dome. How is the inner surface inspected if the lost formwork is obscuring the dome surface? |  | That lost formwork is made of precast reinforced concrete elements, on which the dome concrete has been poured. The only inner surface to inspect is the one of the precast elements.
FR-192 | 7.15 | United Kingdom | France | 07. Concrete containment structures | 147 | Are there pre-determined allowable limits for measurements such as settlement and tilt? Or on discovery of a minor variation, does an engineering case have to be made? |  | Values of settlement are determinated during the design phase. They are not considered as allowable limits, but the measurements are compared to those design values. On the discovery of a significant variation, an engineering case is made.
FR-193 | 7.16 | United Kingdom | France | 07. Concrete containment structures | 156 | Thermocouples and VWSGs embedded in concrete are historically unreliable, is there a minimum requirement for the number/distribution to be giving reliable readings to validate the measured parameters? |  | Concerning the thermocouples and VWSGs embedded in concrete, EDF has defined a minimum requirement for the number and distribution to give reliable data : those devices are a part of the Optimum instrumentation system cited in section 7.2.4.
FR-194 | 7.17 | United Kingdom | France | 07. Concrete containment structures | 160 | "It is understood that the quality and demonstration of lack of voids in the grouted tendons is proven through the use of mock-ups. Is there a method to determine the effectiveness of the grouting during the operational lifetime? In addition, has any thought been given to the inspection of the grouted tendons during decommissioning, to inspect the tendons post-operational and monitor any degradation that has occurred throughout the lifetime of the containment vessel?" |  | The injection mock-ups carried out before the injection in the prestressing tendon ducts on site make it possible to verify that the injection methods guarantee the correct filling of these ducts, including for strongly deviated cable layouts. EDF and Freyssinet use a grout with specific properties to guarantee good protection of the prestressing cables. As regards the possibility of observing prestressing cables during decommissionning, EDF has so far not encountered this opportunity. This option will be considered in due course.
FR-195 | 7.18 | Switzerland | France | 07. Concrete containment structures | 140 | How is the experience (e.g. long-term behavior) with the containment instrumentation system? (strain gauges, thermocouples, etc.) |  | In the course of time, losses of sensors (drowned extensometers, thermocouples) can be observed on some NPP containment. For example, for the 1300 MW serie there are 7 to 15% of embedded sensors out of service. The instrumentation system installed on the containment is robust (more sensors than necessary): the functionality of the sensors is monitored, the failures observed can also be compensated by the installation of replacement sensors (installation of the optimum instrumentation as indicated in § 7.2.3 to ensure long term means of measurement.
FR-196 | 7.19 | Switzerland | France | 07. Concrete containment structures | 146 ff. | How are the structures and the structural elements assessed which are inaccessible for visual inspections (indirect / indicative methods)? |  | The structural elements of the containment which are inaccessible for visual inspections are indirectly assessed with the help of the instrumentation system.
FR-197 | 7.20 | Switzerland | France | 07. Concrete containment structures | 146 ff. | Are there specific testing and inspection requirements for safety related anchorage elements (e.g. pull-out tests with acceptance criteria)? |  | Anchor inspections are designed to detect corrosion and possible damage to the concrete at the anchors. The contacts and blocks are checked by loosening and tightening at torque on a sample of anchors. Tere are no pull-out tests.
FR-198 | 7.21 | Switzerland | France | 07. Concrete containment structures | 147 | How are the acceptance criteria for the inspected concrete structures defined? (crack width and depth, crack patterns, carbonation depth, prestress loss, ...) |  | The criteria are established from the design and construction rules. For example, for crack openings, the criteria take into account the aggressive or non-aggressive nature of the environment, the type of structural element. It is considered that from 0.3 mm (value commonly accepted by the profession and taken up by Eurocode 2) cracks can play a role on the corrosion of the rebars. As far as presstressing losses are concerned, the criteria on deformations come from studies of the mechanical behaviour of the containment performed for operating periods of 40 years or more.
FR-199 | 7.22 | Switzerland | France | 07. Concrete containment structures | 149 | In addition to the visual inspections of the concrete surfaces, do you consider using onsite instrumental inspections and laboratory material testing as part of the aging management? (e.g. carbonation progress, corrosion potential of reinforcement, material strength, concrete cover depth, ...) |  | The structures control are systematically performed by visual inspections. In addition, other destructive and non-destructive testing techniques, such as those mentioned or such as the installation of cracks measurement instrument to monitor the evolution of crack opening, shall be used as necessary for the management of ageing and the extension of service life. They are used for specific analyses that can be implemented depending on the results of the harmfulness analyses.
FR-200 | 7.23 | Czech Republic | France | 07. Concrete containment structures | chapter 2 - generally (44-62) and chapter 7 - generally (137-157) | How often - or if even - are the inspection intervals of civil structures reassessed? Are those inspection intervals changes based on operational experiences and ageing effect treds? Is the NPPs age, especially when considering the LTO phase of operation with higher risk of ageing effects appearance), taken into account for establishment of the inspection intervals? |  | The periodicity of the controls is given in Table 13. In cases of particular phenomena, increased periodocity may be required (pressure test evrery 5 years if no respect of group B criterion ). In addition, periodic controls are carried out under the maintenance programme.
FR-201 | 7.24 | Czech Republic | France | 07. Concrete containment structures | chapter 7.1.2. (141) and chapter 7.2 - generally (155-157) | Have you ever detected the ASR (alkali-silica reaction) in reinforced concrete structures of nuclear power plants during their operation? If so, which parts of structures were affected? Please describe, if the appearance was found in monolithical parts of constructions built on site or in imported prefabricated materials. If ASR was found, how did you proceed this issue? |  | As far as the containment is concerned, only one Civaux containment (cylindrical part) is locally concerned by the RAG. ASR is the subject of specific monitoring (due to the potential ASR risk for each of French structures or even part of a structure), potentially accompanied by sampling and characterisation of the pathology. If the containment function is impacted, studies to verify the impact of the anomaly observed would be carried out and, if necessary, palliative treatments would be implemented.
FR-202 | 7.25 | Czech Republic | France | 07. Concrete containment structures | chapter 2.3.3. (54-57) | In what form you have processed the zero-condition passportization of flaws and malfunctions of NPP civil structures? Is this base passportization updated on the basis of results of regular maintenance activities and/or more detailed survey of intednded structural objects? Do you regulary evaluate appearance of new flaws or changes in previously found flaws and malfunctions with respect to the base zero-condition passport? What kind of documentation do you use for planning and conducting of this constructional-technical survey (e.g. ISO 13822)? What kind of degradation that was found within the constructional-technological surveys is most often (please provide examples, e.g. shear cracks, bend cracks, shrinkage and creeping of concrete, carbonation of concrete CO2, corrosion of reinforcement or concrete, mechanical overload, stability loss of constructions - tilting, bracing, excessive bending, etc.)? |  | The zero-condition passportization of flaws and malfunctions of NPP civil structures has been recorded following the initial inspections of those structures. It includes an initial state measured with the containment monitoring system. This base is periodicly updated, after each inspection and each record provided by the monitoring system. Conc erning the containment structure, the most usual "degradation" is the shrinkage and creep of the concrete, leading to pre-stressing losses.
FR-203 | 7.26 | Czech Republic | France | 07. Concrete containment structures | chapter 7.1.3.2. (147) | Do you have geodetic measurement and assesments of settlement and tilt of civil structures important for (main production block, containment, confinement) and related to (ventilation chimney, building with dieselgenerators, blackout dieselgenerators, main pump station, end heat receiver, etc.) nuclear safety in your aging management programs? Did you find any problems with uneven foundation settlement of NPP civil structures? Did you identify any typical flaws (shear cracks) caused by civil structures settlement? If so, please specify and describe, how did you deal with this issue |  | There are geodetic measurements and assessments of settlement and tilt of important civil structures, such as the containment structure. No flaw or problem on the containment caused by settlement was observed. The rest of the question is out of TPR's scope.
FR-204 | 7.27 | United Kingdom | France | 07. Concrete containment structures | 156 | "Section 7.2.4 discusses the failure and ageing of monitoring instrumentation that is used to inform the structural behaviour of the containment. The introduction of the OIS (Optimum Instrumentation System) is observed as a strength and good example of proactively managing the effects of this ageing effect. Please could more information be provided on the OIS strategy and in particular (i) what is the coverage of original instruments that remain functional since original commissioning (ii) what is the coverage of new instruments installed (iii) what are the minimum acceptance limits for functioning instruments on the containment to support operation (iv) how effective are the newly installed facing instruments in providing an alternative means of measuring strains etc. " |  | The instrumentation system installed on the NPP containments is robust: the functionality of the sensors is monitored and the observed failures are compensated by the installation of replacement sensors. Over time, losses of sensors embedded extensometers, thermocouples) can be observed on some containments For example, for the 1300 MW bearing, there are 7 to 15% of embedded sensors out of service. In order to ensure long term instrumentation availability, an optimum instrumentation has been implemented as presented in § 7.2.3. EDF has defined requirements.For extensometers, the minimum requirements are as follows: see Table 2.jpg When the embedded extensometers are no longer functional, facing sensors are installed on the external side as close as possible to the embedded sensor. The installed sensors give satisfaction and allow to measure concrete deformation rates The displacement sensors (pendulums and invar wires) are part of the optimum instrumentation system and can be replaced identically. | ref to Table 2 in worksheet "FR_Figs & Tables"
FR-205 | 7.28 | United Kingdom | France | 07. Concrete containment structures | General | Bearings - there is no discussion on the ageing management, inspection routines or acceptance criteria for rubber bearings that provide support to the containment structures. These are important structural components. Please provide information on the ageing management strategy for rubber bearings where these have been installed. |  | Only the Cruas site has its nuclear island on neoprene supports. These supports are the subject of a FAV, dealing with neoprene ageing and fretting corrosion. These devices are subject to specific monitoring: visual inspection of neoprene supports to detect traces of rust or cracks, stiffness measurements and determination of the dynamic modulus of supports on the basis of samples kept for Cruas supports. If necessary, these supports can be replaced.
FR-206 | 7.29 | Belgium | France | 07. Concrete containment structures | 140-145 | What are the acceptance criteria related to the ageing mechanisms listed? |  | The mechanical strength and leak rate criterion of the containment are checked during the pregnant tests. The ageing phenomena are the subject of particular monitoring, potentially accompanied by sampling and characterisation of the pathology. If the containment function is impacted, studies to verify the safety of the disorder observed would be carried out and, if necessary, palliative treatments would be implemented.
FR-207 | 7.30 | Belgium | France | 07. Concrete containment structures | 140 | Can one example of R&D programmes concerning ageing degradations mechanisms be given? |  | The most significant R&D program to address the aging effects of containment is the VeRCoRs program. Through a 1/3 scale model of a highly instrumented containment, EDF is able to observe in an accelerated manner the effects of ageing on the long-term behaviour of containments, in particular on their tightness during testing.
FR-208 | 7.31 | Belgium | France | 07. Concrete containment structures | 140 | Why differential settlement is not considered? |  | Because of the rigidity of the containments, differential settlement is not a proper ageing mecanism.
FR-209 | 7.32 | Germany | France | 07. Concrete containment structures |  | Nothing is indicated in the chapter on 07. Concrete containment structures regarding the inaccessible areas. How the ageing management programs are applied for these areas? What the procedures are used to evaluate the ageing phenomena in inaccessible areas? |  | The structural elements of the containment which are inaccessible for visual inspections are indirectly assessed with the help of the instrumentation system.
FR-210 | 7.33 | Germany | France | 07. Concrete containment structures | 147-148 | It is stated that mechanical behaviour of the containment is regularly monitored in op-eration and during containment pressure tests by means of an instrumentation system which measures overall deformation and displacement. Overall displacements and local deformations are monitored. Local deformations of the concrete are measured by means of vibrating wire strain gauges (acoustic indicators). The measurements from the strain gauges located in the straight part in the middle of the cylinder are used to calculate the instantaneous modulus of elasticity of the wall and its Poisson’s ratio. Afterward the shrinkage and creep of the concrete are evaluated. This process is being performed throughout the lifetime. In addition to the straight zones, these instruments are installed in the base-mat, the gusset, the toroidal belt and the dome. The height of cylindrical part of containment is up to 45 m. This is a massive, thick-wall structure from cast-in-situ concrete. Thus the special variability of concrete properties can not be ignored in this case. Why were strain gauges not also installed in the upper and lower parts of cylindrical part of containment to better assess the creep and shrinkage of concrete? |  | Strain gauges were also installed in the upper and lower parts of cylindrical part of containment. They allow a better assessment of the containment mechanical behaviour.
FR-211 | 7.34 | Germany | France | 07. Concrete containment structures | 156, 162 | It is stated, that occurrence of a loss of containment tightness on Bugey-5 reactor was detected in 2015. The origin of this event was corrosion of the liner at the bottom of the peripheral seal, the precise location of which could not be identified. Repairs were made, consisting in replacing the base-mat-containment gusset seal to stop the corrosion mechanism and restore containment tightness at this seal. The checks have been performed on all reactor buildings in France concerning containment tightness. However, these checks on Bugey-5 reactor were unable to prevent or precisely identify the origin of the metal liner corrosion. The following conclusion given in the report: “The repairs made were nonetheless considered by ASN to be satisfactory. These repairs could however be better prepared in advance in order to improve treatment in the event of the feared ageing phenomenon occurring”. Why didn’t the event in Bugey-5 initiate an improvement of this APM for the French re-actors to prevent such ageing induced degradation in the future? |  | As part of the VD4, the ageing management program was reviewed by IRSN and presented to the advisory committee in March 2018. As regards corrosion of the liner, a repair solution on the Bugey No. 5 has been carried out by EDF without, however, providing elements confirming the sustainability of this solution, and thus its feasibility on all the 900 MWe reactor enclosures. EDF is considering extending this repair solution to other 900 MWe reactors, should they be affected by a similar liner corrosion. A study on this subject should be completed in 2019. ASN considers that a sustainable preventive liner repair solution should be defined.
FR-212 | 7.35 | Netherlands | France | 07. Concrete containment structures | 7.1.3 | The 10 yearly pressure test is carried out at design pressure. What are the ratios between the the design pressure of the pressure test and the design pressure in accident conditions? |  | The design pressure of the pressure test is equal to the design pressure in accident conditions.
FR-213 | 7.36 | Netherlands | France | 07. Concrete containment structures | 7.4.1 | How does the ASN supervise the effect of the 10-yearly pressure test? Is an inspection caried out before and after the pressure test? |  | The ASN supervises the effect of the 10-yearly pressure test through inspection carried out either before or after the pressure test, and through the assessment of the test report.
FR-214 | 7.37 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | 141 | Please explain why "Cracking of the prestressed concrete which could lead to corrosion of the passive rebars or prestressing tendon ducts" has been discounted for the N4 and EPR reactors |  | 900 MWe single containments are subjected to the atmospheric causes of degradation. Hence, they deserve special care and maintenance procedures to prevent and treat "Cracking of the prestressed concrete which could lead to corrosion of the passive rebars or prestressing tendon ducts" . On the opposite, double wall containments (i.e. P4, P'4, N4 and EPR reactors listed in the section 1.1.1 of the NAR) offer a protection and a controled atmosphere to the inner pre-stressed wall. Hence, the maintenance procedures of that inner wall are adapted to less severe conditions, as compared to 900 MWe single containments.
FR-215 | 7.38 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | 142 | It is stated that "The double-containment design of the reactor building of the 1300 MWe and N4 plant series protects the prestressing components from the potentially corrosive marine atmosphere." Does this mean there is active management of the atmosphere to prevent fresh external air from entering the areas where the tendon ends are ? |  | In the double-containment design (1300 MWe and N4 plant series), the volume between the two walls (or containments) is closed and its air is controled. It means there is an active management of the atmosphere to prevent fresh external air from entering the areas where the tendon ends are.
FR-216 | 7.39 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | 146 | The table suggests that for the 900Mw series mechanical behaviour checks are done - "Every three months (every month for certain cases)" Please provide further details |  | As a general rule, the monitoring system of the containment provides measurements every two weeks, and a monitoring report, established every three months, allows the Engineering Services of EDF to check the correct mechanical behaviour of the containment during that period.
FR-217 | 7.40 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | 147 | For Single wall containment and inner wall of double-wall containments, it suggests monitoring of the mechanical penetratins is "continuous", please provide further details |  | Indeed, continuous monitoring of mechanical penetrations is ensured by monitoring the air mass in the internal enclosure during an operating cycle. This follow-up aims at detecting possible leaks on the mechanical crossings following valve manoeuvres for example.
FR-218 | 7.41 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | 158 | The allowable leak rate for the CABRI research reactor is much larger than for the operating fleet, please explain the rationale |  | The term source and the operation of the CABRI reactor, are not comparable to the EDF fleet of nuclear power reactors. The reactor building is equipped with a ventilation system that maintains a depression at a value of approximately 10 daPa (alarm threshold 5 daPa) and that traps the products emitted on HEPA filters and/or iodine traps. It is designed to withstand an accidental overpressure of 400 daPa.
FR-219 | 7.42 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | 160 | Section 7.3.2.2 gives only a very short description of the inspection requirements. In addition, the allowablw leak rate is very high. Please provide further details |  | These rates are not direct leaks. HFR has a double containment (inner: concrete containment and outer metal containment). The internal annulus between the two containments is over pressurized (135 mbar). Consequently, these leak rates are not from the inside of the reactor building to outside. For information, the direct leak rate from the reactor building to outside is about 20 m3/h when the internal annulus space is not over pressurized compared to the inside of the reactor building.
FR-220 | 7.43 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | 138 - 140 | The content of para “7.1.1 Scope of Ageing Management Programme for Concrete Containments” of the France NAR corresponds to the requirements listed in section 07.1.1 of RHWG REPORT TO WENRA and comprises sufficient information on the process/procedures for the identification of ageing mechanisms. At the same time, there is no information on the methods and criteria used for selecting components within the scope of ageing management (see item “a” of para 07.1.1 of RHWG REPORT TO WENRA). This information should be added to the France NAR or corresponding clarifications might be provided as an answer. |  | Methods and criteria are mentionned in §2.3.4.1. The SSC included in the AMP are the following: · SSCs important for safety (EIPS), · non-EIPS SSCs, for which ageing could lead to failures liable to compromise the design hypotheses adopted in the safety case; · non-EIPS SSCs which, with respect to the PSA (Probabilistic Safety Assessments) make a significant contribution to limiting the core melt risk. The containment is an SSC EIPS. All its components with a safety requirement are concerned by ageing analysis (concrete, prestressing cables, liner,...). The paints and non-reinforced coatings of the reactor building are included since they may call into question the hypotheses assumed in the safety demonstration. The instrumentation system is also included. It is not EIPS, but participates in monitoring the good behaviour of the containment.
FR-221 | 7.44 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | 140 - 145 | The content of para “7.1.2 Assessment of Ageing of Concrete Containments” of the France NAR corresponds to the requirements listed in section 07.1.2 of RHWG REPORT TO WENRA and provides sufficient information on the ageing mechanisms, establishment of acceptance criteria related to ageing management etc. Also, there is no information on standards, design, manufacturing and operating documents used in assessment of aging (see para 07.1.2 of RHWG REPORT TO WENRA). This information should be added to the France NAR or corresponding clarifications might be provided as an answer. |  | The supporting documents for monitoring ageing phenomena are the preventive maintenance programme. The design and construction standards are updated by integrating feedback from experience in terms of ageing.
FR-222 | 7.45 | Concrete containment PCPV expert group | France | 07. Concrete containment structures | - | Para “7.4 Regulator’s Assessment and Conclusions on Ageing Management of Concrete Structures” of RHWG REPORT TO WENRA is absent in the France NAR. This information should be added to the France NAR or corresponding clarifications might be provided as an answer. |  | That paragraph is present in the NAR, in pages 160 to 163.
FR-223 | 7.46 | EC | France | 07. Concrete containment structures | p 149 | Please explain why Bugey and Fessenheim NPPs have domes coated with a tightness compound, and please precise which surface exactly is coated. What is the lifetime of this coating? How is the degradation of these coatings by ageing being monitored? Does it need to be preventively replaced after some time? Was this covered by any research? |  | Bugey and Fessheim domes are coated with asphalt. At the time of the design of the CP0 serie, external water inflows were feared with regard to the durability of structures. This coating is followed in application of preventive maintenance programme and PMLV and by visual inspections in particular. If degradation is observed, the coating is replaced or repaired. There is no specific research program on this coating.
FR-224 | 7.47 | EC | France | 07. Concrete containment structures | p140 | How is the absence of instrumentation of the outer containment of double-walled containments compensated to ensure appropriate monitoring of key parameters (beyond visual inspections and leak assessment)? |  | Experience confirms that visual inspections and leak assessment are sufficient to ensure appropriate monitoring of that passive structure.
FR-225 | 7.48 | EC | France | 07. Concrete containment structures | p143 | Composite coatings have been applied on the inner surface of some double-wall containment to reduce the leak rate. The report states that coatings selection took account of normal service irradiation until VD4. Medias reported recently that EDF wants to keep most of its fleet of 58 commercial reactor units in operation until 2029, when they will reach their 50 years of design lifetime. Will the composite coatings need to be preventively replaced during the VD4? Has the behaviour of these coatings beyond VD4 been covered by any research, including under accident conditions? |  | The behaviour of these coatings beyond VD4 has been analysed by research and qualification programs, including under accident conditions.
FR-226 | 7.49 | EC | France | 07. Concrete containment structures | p147-p154 | The report indicates that the containment metal liner is inspected only before and after the pressure test, i.e. only every ten year. However, operating experience show cases of corrosion or damage to containment liners that led to loss of containment leak tightness between two pressure tests. Therefore, inspecting the liner only every ten years seems not enough and it is suggested to perform at least an intermediate visual inspection of the liner. |  | An inspection of the liner painting on the accessible areas is also carried out every 5 years, which makes it possible to ensure the absence of corrosion.
FR-227 | 7.50 | EC | France | 07. Concrete containment structures | p154 | Following visual inspection of the facings, cracks with an opening of more than 0.3 mm are injected with resin to ensure leak tightness. This acceptance criterion is ok for cracks in indoor walls, however for cracks in outdoor surfaces subjected to freeze - thaw cycles or in marine environment the consensus is that smaller cracks are expected to be repaired (see namely TECDOC-1054 p75 and NP-T-3.5 p203). Could you provide some clarification on this point. |  | It is considered that from 0.3 mm (value commonly accepted by the profession and taken up by Eurocode 2) indoor or outdoor cracks can play a role on the corrosion of rebars.
FR-228 | 7.51 | EC | France | 07. Concrete containment structures | p154 | When cracks in concrete are found, beyond the pure repair work, is the following performed?: 1. Assessing what is the probable origin of the crack (cause, such as design errors, construction errors, corrosion of reinforcement, accidental or impact loading, foundation movement, chemical reactions, etc.); 2. Determining whether the cracks are active or dormant. |  | When a crack is found during a visual inspection, a first classification of defects is made and the probable causes of the crack are evaluated. The dormancy or not is decided during the preventive maintenance programme follow-up.
FR-229 | 7.52 | EC | France | 07. Concrete containment structures | p156 | The report mentions a loss of containment tightness on Bugey reactor 5. What was the estimated leak rate of the reactor building (in % per day of gas contained under LOCA conditions)? The origin of this event was corrosion of the liner at the bottom of the peripheral seal, the precise location of which could not be identified. How is it guaranteed that this loss of containment cannot also occur in other 900MWe reactors? |  | The evolution of the measured leak rate between 2001 and 2011 was higher than the one required in the general operating rules (cf §7.1.3.4.1.1 group B criterion), which led to perform a anticipated pressure test in 2015, The measured leak rate in 2015 was 0.162%/d. in test conditions, which corresponds to 0,225%/j in LOCA conditions, This value is equal to the acceptable leak rate (accounting for the ageing and a potential drop in the confinment capacity (Feacc). It cannot be guaranteed that this does not happen on other 900 MW enclosures, however the tightness and its evolution is monitored during pregnant tests. Fora likely to present in the medium or long term the same problem as Bugey 5 are the object of a specific attention.
FR-230 | 7.53 | EC | France | 07. Concrete containment structures | p158 | The allowable overall leak rate for the ORPHEE reactor is very high (24% of the total volume per hour). The allowable overall leak rate for the CABRI reactor is even higher (in %vol/hour). What are the actual measured values of the overall leak rate for these two reactors? Could the leak rates be reduced (for instance using coatings on the most critical parts)? |  | For the CABRI reactor, the measured value is less than 240 m3/h and therefore less than the required requirement (300 m3/h). No specific work is therefore planned. CABRI operates for only one or two RIA tests per year. For the ORPHEE reactor, the measured value is less than 115 m3/h and therefore less than the required requirement (150 m3/h). No specific work is therefore planned. Its final shutdown is planned before 2020.
FR-231 |  | Bulgaria | France | 09. Overall assessment and general conclusions | p. 169 | In subchapter “9.3.2 The ageing management approach” is stated that “In the context of the requests to extend the operating life of the NPPs, EDF proposes continuing this approach for the fourth ten-yearly outages (VD4). This approach will be extended to all the SSCs that are important for the management not only of radiological risks but also of conventional risks.” Would you give more information about what kind of risks are defined as “conventional risks” and how SSCs which are important for limitation of these risks will be selected. |  | The French regulation (BNI order) defines the notion of Elements Important for the Protection of Interests (EIP). The interests to be protected are public security, public heath and safety, the protection of nature and the environment. These interests relate to the risks and detrimental effects suffered outside the site. - The assessment of the risks presented by the facilities and the scale of their potential consequences are the subject of the nuclear safety case, taking the form of the BNI safety analysis report. - The detrimental effects are defined in relation to the impacts caused by the facility on health and the environment, owing to water intake and to discharges, detrimental effects caused by the dispersal of pathogenic micro-organisms, noise and vibration, odours and dust. Given the different nature of the various risks and detrimental effects, the EIP can be broken down into three categories: - EIPS (Elements Important for Protection / Safety) for risks linked to radiological incidents and accidents (elements for which the failure would have direct or indirect consequences on control of the nuclear safety functions); - EIPR (Elements Important for Protection / conventional Risks) for risks linked to non-radiological incidents and accidents (elements for which the failure would have consequences on the functions linked to non-radiological accidents affecting the confinement of dangerous substances, the protection of persons and the environment against the effects of dangerous phenomena); - EIPI (Elements Important for Protection / detrimental effects) for detrimental effects linked to the normal operation and degraded mode operation of the facilities (elements for which the failure would have health or environmental impacts). The methodology applied up to now is being extended to EIPR and EIPI, either by extending the area of applicability of existing AAS or by creating new AAS. In case that during the preparation of the 4th PSR NPPs identify SSC EIP, which are not covered by existing AAS, the same methodology will be applied.
FR-232 |  | General AMP expert group | France | 10. References | 171 | 10.1 Glossary. It is not a glossary but a list of abbreviations. |  | /
HU-1 |  | Poland | Hungary | 04. Concealed pipework | 37 - 48 | 1. What are criteria used for selecting mentioned cables within the scope of ageing management? 2. What is frequency of tests performed by the KFKI of the primary side cables? 3. What ageing mechanisms were identified in the AMP for electrical cables? 4. Why cables that are included in AMP and described in the report cover only primary side cables of the two transformers and 7 nuclear measurement chains and do not cover any cables supplying important to safety SSCs? What are the criteria used for selecting this two types/groups of cables? 5. What are the criteria used for selecting this two mentioned in the report types/groups of cables? 6. What is licensee’s experience of the application of AMPs for electrical cables? | Website | 1. The method of selection is written on page 40. It is based on the evaluation of safety functions of cables originated from electical circuit drawings analysis of PSA studies.. 2. BRR has no high voltage cables 3. Regarding insulation materials of conductors: oxidative ageing, ageing due to radiation, moisture, chemical ageing, maintenance load; Regarding outer jackets: oxidative ageing due to radiation 4.The selected cabels are safety relevant and they are tested regularly 5. The selected cabels are safety relevant and they are tested regularly 6.Based on the experience of the ageing management assessment measures no significant ageing effect is observed on cables. The AMP is adequate, there is no need to modify that.
HU-2 |  | Poland | Hungary | 03. Electrical cables | 46, | 1. Does the phrase „extended service life” refer to the extended license of the NPP or rather extended service life of particular cables with regard to the design of NPP? 2. (Ageing assessment of cables and wires) mentions the defined comparison dose DLTO of 46 kGy as a design radiation dose of the materials. How is this value obtained? | Website | 1. Refers to the extended license of NPP, which means 50 years. 2. The reference of 46 kGy is not found in the report. The other dose rates in the 1.3 annex table are originated from measurements and calculations.
HU-3 |  | Norway | Hungary | 02. Overall Ageing Management Programme requirements and implementation | 17 | How do the HAEA determine whether the methodology of evaluation of TLAAs is acceptable and comprehensive? | Website | Review of the TLAAs was also carried out in 2017 as part of the 10-year PSR; the validity of the TLAAs with some corrective measures was demonstrated. In the clear majority of the cases the TLAAs are still valid, because the conditions, baseline data taken into consideration during their preparation have not changed and according to our current knowledge the applied analysis methods meet the requirements.
HU-4 |  | Bulgaria | Hungary | 03. Electrical cables | chapter 3 | Could you please provide more detailed information about the results from laboratory tests and results from the removed cables depot and are the results from cables depot used for verification of laboratory results? | Website | During the first some years of qualification efforts we tried to use cable depots. There were many problems with overexposition of samples, handling the depots. At that time we performed the measures of elongation at breaks on the samples, but these did not give a comprehensive and trending result probably because of the method of manufacturing of cables (partial irradiation of cables). Finally we gave up this method and started a new program to permorm LOCA tests on every effected cable types. These could give reliable information about the qualification life of the cables.
HU-5 |  | Bulgaria | Hungary | 03. Electrical cables | chapter 3 | Concerning the Budapest Research Reactor, could you provide more information about the cables of nuclear measurement chains which are subject to ageing management. Could you give more information if the research reactor has emergency power supply and if does, could you clarify if these cables are within the scope of the ageing assessment? | Website | The cables of the nuclear measurement chains are measured together with the neutron detectors (they can not be separated). Insulation resistance is measured once or twice annually. Acceptance citerion is 10E+8 Ohm.
HU-6 |  | Bulgaria | Hungary | 04. Concealed pipework | chapter 4 | Do you use software for assess the risk of corrosion damage for buried pipelines (for example BFWORKS or ect.)? | Website | No software is used.
HU-7 |  | Bulgaria | Hungary | 02. Overall Ageing Management Programme requirements and implementation | p. 37 | The report states that ageing management is included in the regulatory inspection system as a separated inspection area. The main topics that should be especially considered during the inspections are also described. Could you please provide more information on what specific/comprehensive inspections on Paks NPP were implemented, their scope, covered areas, main results and any significant findings from the inspections? | Website | Inspection of the implementation of ageing management programmes is reviewed both as part of the ad hoc (under-major outage) and in comprehensive inspections. In the licensing process of LTO systematic inspections was performed, where AM programmes are inspected, the documentation, drawings, proofs, and actual physical status have been verified. Drawing document validation has been validated by units. The AM programmes are part of the framework programmes, which are systematically inspected on the basis of the annual inspection programmes.. The authority shall check that the gained experience, the known error location and the experience of the events have been reversed into the AM frameworks. According to the annual oversight program of the HAEA the technical condition and operation of Paks NPP were reviewed in the framework of a comprehensive inspection in the second half of 2016 and 2017 to. During the inspection, the authority paid special attention to assess the technical condition of the facility, including equipment qualification, qualified status, monitor the implementation of periodic tests, ageing management and maintenance issues. Specialy in the inspections on Ageing Management area the inspectors have not identified deviations, the documents viewed and the processes described are in accordance with the natioanal and international requirements. The annual report of the NPP contains general evaluation of the AM, and also contain the detailed evaluation of all framework programmes.
HU-8 |  | Slovak Republic | Hungary | 02. Overall Ageing Management Programme requirements and implementation | Page 19 | In chapter 02.3.2.2 it is written as follows: „The TBE304 procedure [14] states that the operational experience of ageing management programmes, based on industry practice may require: - management of new degradation mechanisms; - clarification of the technical-scientific knowledge about the degradation mechanisms;“ How can the licensee identify the new degradation mechanisms? How are licensees prepared to identify the unforeseen ageing mechanisms? (see para 2.7) Does clarification of the technical-scientific knowledge about the degradation mechanisms concern the new degradation mechanisms only? | Website | New forms of degradation, or new degradation mechanisms can be found during the implementation of AM programs ( in-service inspection, maintenance, periodic condition inspections), or during operation. The continuous monitoring of the industry’s AM related experience (IAEA meetings, conferences, IGALL, WANO, VVER club, etc.) ensures that any previously unanticipated or unknown degradation mechanisms which have been or are not known to the licensee will be managed. Of course, not just the new degradation mechanisms need clarification of the technical-scientific knowledge.
HU-9 |  | Slovak Republic | Hungary | 02. Overall Ageing Management Programme requirements and implementation | Page 15 | The database of SSCs and cables covered by ageing management in Paks NPP can be found in the central technical database (AS6) as well as in the ADRIA information systems. What are the functionalities (capabilities) of the database, which parameters, data, information or documents (link to them) are involved in it? What software is used for its operation? Is the same database also in the AS6 and in the ADRIA information systems or are there two different databases? | Website | These are two different databases. ADRIA is an ORACLE based, individually developed database, which contains all of the cable data, including: type, cable route, safety function, the equipment it connects, and the qualification grouping and results. AS6 is the generally used sofware tool by many companies for action tracking, work management, technical data storing, etc. It contains the data of equipment, including safety classification, location, etc. ADRIA gets these data through an interface from AS6.
HU-10 |  | Slovak Republic | Hungary | 03. Electrical cables | Page 39 | Is the programme to monitor cable fire-proof coating involved in the Paks NPP ageing management process? | Website | There is no such kind of AMP for fire-retardant/fire-proof cables, because all of those cables are environmentally qualified.
HU-11 |  | United Kingdom | Hungary | 03. Electrical cables | 16 | "Budapest Research Reactor Ageing Management of electric cables Please explain what ageing degradation mechanisms were identified to have caused the premature ageing and inadequate insulation resistance readings of the nuclear measurement chain. Have improvements been identified and implemented to prevent this re-occurring?" | Website | Not relevant, as there ar no high voltage cables in BRR.
HU-12 |  | Finland | Hungary | 04. Concealed pipework | 56 | What are the corresponding safety and operation challenges, like maintaining safe shutdown condition, flooding risks, etc. connected to AMP? | Website | No major issue .The AMP identify all ageing mechanisms, determine the possible consequences, and determine necessary activities in order to maintain the operability and reliability of SSCs.
HU-13 |  | Finland | Hungary | 07. Concrete containment structures | 84, 85 | Concerning the borated water effects in heavy concrete structures: • Is there a specific reason why bo-rated water has been especially damaging for heavy concrete? • Has cracking been identified as a root cause for the extent of degra-dation? • Have the above mentioned phe-nomena been considered in the de-sign of leakage collection and de-tection systems? | Website | • The operational temperature of the heavy concrete structures is generally higher than that of the regular concrete structures, which accelerates the chemical phenomena; the presence of free oxygen from iron oxides, which causes corrosion; presence of chloride ions; inhomogeneous structure due to the difficulties occurring during placing of the heavy concrete. • The proceeding chemical processes have been identified as a root cause; cracking – which is the consequence of the structure’s degradation – enhances the escalation of the degradation. • The source of the borated water entering the concrete structures is the leakage of the technological system, rather than the designed leakage collection system. The leakages and the marks of the earlier leakages are mapped during each overhaul, and the changes with time are analysed.
HU-14 |  | Switzerland | Hungary | 03. Electrical cables | 17 | Table2.3.1.3-2: Is there an AMP for electronic and actuators (capacitor, relais, modules, drives)? | Website | No, there is not, because they are active components which are managed by maintenance and - in case it is neccessary - environmental qualification.
HU-15 |  | Switzerland | Hungary | 03. Electrical cables | 43 | Textline6: Which (kind of) (6kV) cables are (periodically/permanently?) monitored by OWTS? Is this a kind of reflectometry/resonance analysis? | Website | Every 6 kV cables are measured by OWTS method (only in case of repair or replacement). This is a reflectometry method.
HU-16 |  | Switzerland | Hungary | 03. Electrical cables | 47 | Textline27: Which activities on residual lifetime determination are ongoing? What method(s) are applied therefore? | Website | Other areas reflect to degradation due to design and construction failures, which are out of the scope of AM, may can effect to the condition of cables.
HU-17 |  | Switzerland | Hungary | 03. Electrical cables | 48 | Textline20: On which degradation mechanisms of other areas should attention be paid? | Website | Corrosion life time assessment is performed in the case of carbon steel pipings, based on the estimation of the remaining minimum wall thickness, using measured data. For SS piping corrosion life time assessment is not performed, local defects, that are not allowable (through-wall or close to through-wall) are repaired. Fatigue life is estimated for safety class 1-2 pipings. There are similar and different corrective measures, depending on the pipe material, and the active degradation mechanisms. Local repair of the local defects and partial pipe replacement can be mentioned as possible common measures for all SS and CS pipes, while for example the CIPP lining is taken into account as corrective measure just for carbon pipes with high rates of Danube river side corrosion.
HU-18 |  | Czech Republic | Hungary | 04. Concealed pipework | 49 | You have set up 8 specific AMPs which are focused on concealed pipeworks. Do you perform lifetime assessment for every individual specific AMP? How does the lifetime assessment look like? Do you define different corrective measures for every individual piping or are the corrective measures common for whole group of pipings concerned with AMP? | Website | Corrosion life time assessment is performed in the case of carbon steel pipings, based on the estimation of the remaining minimum wall thickness, using measured data. For SS piping corrosion life time assessment is not performed, local defects, that are not allowable (through-wall or close to through-wall) are repaired. Fatigue life is estimated for safety class 1-2 pipings. There are similar and different corrective measures, depending on the pipe material, and the active degradation mechanisms. Local repair of the local defects and partial pipe replacement can be mentioned as possible common measures for all SS and CS pipes, while for example the CIPP lining is taken into account as corrective measure just for carbon pipes with high rates of Danube river side corrosion.
HU-19 |  | Czech Republic | Hungary | 04. Concealed pipework | 50 | You have mentioned that pipework containing radioactive effluents are managed in the scope of ZSAMP-17 and Z-SAMP-19. Does it mean that one piping is in the scope of two different AMPs? How do you ensure consistent lifetime assessment and corrective measures? | Website | The two AMPs are covering different pipings that are containing radioactive effluents. The scope of the ZSAMP-17 is limited to the spent fuel pool and shaft no.1 cooling pipings, with known and currently active local corrosion degradation mechanisms (MIC) to be managed. The ZSAMP-19 covers other partially concealed corrosion resistant steel pipeworks.
HU-20 |  | Czech Republic | Hungary | 05. Reactor Pressure Vessels | 58 | Does your lifetime assessment of RPV contain individual assessments of every degradation mechanisms for every component defined in table 05.1.1-1? | Website | Life time assessment was performed for fatigue (CUF calculations) and radiation and thermal embrittlement (PTS calculations) of the components indicated in the table. In the case of other degradation mechanisms/aging effects, like local defects, loss of material have to be repaired and the design condition to be restored.
HU-21 |  | Czech Republic | Hungary | 05. Reactor Pressure Vessels | 60 | You have mentioned fatigue, including environmental effects at the inner surfaces in operational contact with the coolant. What methodology do you use for environmentally assisted fatigue calculations? Do you use the acceptance criteria mentioned on the page 60 in the case of enviromentaly assissted fatigue calculations? | Website | HAEA Guideline 3.25. describes the methodology of the environmental fatigue assessment (NRC RG 1.207, NUREG/CR-6909). Yes, the same criteria are used.
HU-22 |  | Czech Republic | Hungary | 07. Concrete containment structures | 85 | 07.2.1. Assessment of degradation mechanisms to be managed, 11. Hermetic liner: "Does the control calculations, which has been done for the areas of deviations, take into account the loads caused by the potential LOCA accident? (pressure and temperature increase) If so, what acceptance criteria in terms of mechanical stress have you set in this calculation for a hermetic steel liner under LOCA conditions to ensure tightness? (For example, the yield strength or tensile strength or % deformation?)" | Website | The loads caused by the potential LOCA accidents are taken into account in the control calculations. Yield strength is set in the calculation as acceptance criteria. According to the descriptions in the AMP for hermetic lining, local control calculations are carried out in those areas where the decrease in lining thickness exceeds 10 %.
HU-23 |  | Bulgaria | Hungary | 04. Concealed pipework | p.49 | Would you please clarify whether the concealed pipes were with inner and/or outer insulation/coating? | Website | The buried in the ground CS pipes belonging to the scope of the National Assessment Report, operating with Danube water were installed with inner and outer coating. The emergency diesel fuel buried in the ground CS pipes belonging to the scope have just outer coating. The SS buried pipes belonging to the scope are not covered by coating/insulation.
HU-24 |  | Bulgaria | Hungary | 05. Reactor Pressure Vessels | p.59 | Would you please clarify whether the thermal ageing was considered as well as possible ageing mechanism? | Website | Yes, the thermal aging was taken into account and analyzed amoung the TLAAs (Thermal Aging and PTS TLAAs.) These TLAAs results justified that no additional AM measures are needed.
HU-25 |  | Finland | Hungary | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Website | There are no challenges. The AMP identify all ageing mechanisms, determine the possible consequences, and determine necessary activities in order to maintain the operability and reliability of RPV.
HU-26 |  | Czech Republic | Hungary | 04. Concealed pipework | 16 | "04.1.2.3.:The results of these studies and laboratory tests have confirmed the previous assumptions, i.e. microorganisms, that could survive and multiply in the given conditions (temperature, boric acid concentration), played a significant role in the corrosion damage of the spent fuel pool cooling system; furthermore, the studies established and validated microbiological methods and procedures of MIC monitoring that can also be utilized at Paks NPP." Biological analysis also confirmed that there are a number of microorganisms in essential waters in our NPPs. However, it seems that the main cause of corrosion of austenitic materials is mainly the local concentration of chlorides. Do you really prove that the main cause is microbial corrosion? | Website | From a corrosion’s point of view, the spent fuel cooling system is considered as a complex and open system. Its corrosion behavior is determined by many contributing factors as well as by their interaction. The specific effect and the relative weight of the individual factors may vary and the observed localized pitting corrosion degradation cannot originate from a single, well defined factor or root cause. Based on the evaluation of the results of the investigations and analyses performed, the following major contributors to the corrosion degradation were identified: the oxide layer on the HAZ of the welds and associated corrosion sensitivity nearby, the effect of micro-organisms, and the operating conditions such as flow velocity, stagnation and low temperature. The observed defects were not connected to local concentration of chlorides.
HU-27 |  | United Kingdom | Hungary | 03. Electrical cables | 16 | Section 03.1.3.1. IGALL AMP 207 does not require condition monitoring, sampling and inspection activities during the qualified lifetime of the cables, however, periodic and ad-hoc assessments of environmental parameters are performed. Do the results obtained from the periodic and ad-hoc assessments of environmental parameters support the continued implementation of IGALL AMP 207 or do they support the implementation of another relevant international practice(s)? | Website | Yes, they do. There were no any significant changes found in the room conditions, as it was concluded during the completion of the Periodic Safety Review.
HU-28 |  | United Kingdom | Hungary | 03. Electrical cables | 16 | "Paks NPP Section 03.1.3.1. In terms of the qualification maintenance activities, please explain: (i) the periodicity used to perform ad-hoc assessments of environmental parameters; (ii) the term ad-hoc when used to describe the environmental parameter assessments and; (iii) how consistency is ensured for the purposes of recording, trending and analysing any parameter assessments recorded." | Website | We have performed the initial qualification process already under the conditions of operating plant, which means we had to collect the environmental operational conditions by measurements. No calculations or assumptions were done, therefore these data are very reliable. The conditions are not changing rapidly, therefore we are performing an evaluation of the environmental conditions in every ten years during the preparation of the Periodic Safety Analysis Report.
HU-29 |  | Netherlands | Hungary | 02. Overall Ageing Management Programme requirements and implementation | 02.3.2.6 | Operating experience: the sources of external and international experience should be provided (ageing related events). What activities are carried out with respect to disemminating information to other operators in other countries? | email | Presentations, and discussions on the AM related meetings, conferences organized by WANO, IAEA, VVER Operators, etc. One example: WANO meeting in 2017 at the Paks NPP (Corrosion defects in the cooling pipes of the spent fuel pool) with participants from VVER operators.
HU-30 |  | Netherlands | Hungary | 02. Overall Ageing Management Programme requirements and implementation | 02.3.1 BRR | In this chapter the emphasis of the scope of the AMP BBR is mainly on mechanical. Almost no information is given for electrical and concrete/building. Please elaborate on that. | email | From the electrical part the most important is the annual investigation of accumulators. Cables ar not of importance as they are below 400 V. The building is checked annually by walk around. Measurement of chamber insulation resistance for nuclear measuring chains. For iodine and aerosol filters, spent fuel element gamma dose rate measurement at a store. Water chemistry analysis.
HU-31 |  | Netherlands | Hungary | 02. Overall Ageing Management Programme requirements and implementation | 02.3.2 BRR | Return of experience. The return of experience from external sources is claimed to be very limited because of the unique design and the obsolete other RR of similar design. However one could argue this claim is too pessimistic as it should be possible to exchange information about ageing management approaches, ageing phenomena, monitoring and inspection methods. Nothing can be found in the text about sharing information about problems with other countries of RR e.g. through the IRSRR database. Please elabortate on that. | email | Information is gained from external sources as wekll, e.g. from IAEA data bases and from information available on the internet. The information is given in detail in our annual reports. Participation in workshops (e.g. RROG see above) gives also important contribution. In the framework of the IAEA decommissioning IDN projects (DACCORD, CERREX, CIDER), the databases of the Ukrainian and Czech VVR-S reactors were compared to the BRR aging database. IRSRR databases are filtered from experience and participated in the IRSRR meeting.
HU-32 |  | Netherlands | Hungary | 03. Electrical cables | 3.2.1 / p.45 | Has the expectancy of 'no significant ageing' for V-SAMP-07 cables been confirmed by the AMP? | email | Yes, up till now there is no mentionable trend of parameteres.
HU-33 |  | Netherlands | Hungary | 03. Electrical cables | 3.2.3 / p.47 | Why is there no limit imposed on the number of failures? Is the number of OWTS-failures in the faulty 2001 6-kV cable now the 'de facto' justified limit above which other cables need to be replaced (as suggested in the last sentence of the 3rd paragraph) | email | Before the failure of that cable there were no OWTS measures and limits for the acceptable value of OWTS measures for medium voltage cables. Because it suffered from a short circuit it was impossible to perform OWTS measure on the failed cable and compare any values. Following this failure we started to implement this measurement method on PVC insulated 6 kV cables, but we could not find any criteria for PVC insulations, therefore we have replaced all of the cables with relatively high degree of failure locations and partial discharges.
HU-34 |  | Netherlands | Hungary | 03. Electrical cables | 3.3 / p.48 | Would it be possible to mention these "other areas of degradation mechanisms" more explicitly? | email | Other areas reflect to degradation due to design and construction failures, which are out of the scope of AM, may can effect to the condition of cables.
HU-35 |  | Netherlands | Hungary | 03. Electrical cables | general comment | All pages between 17-57 are numbered “Page 16/116” in the bottom right corner | email | Editing error
HU-36 |  | Netherlands | Hungary | 05. Reactor Pressure Vessels | Ch.5 | The information provided in this NAR in its chapter 5 on ageing management of reactor pressure vessels, is to a great extent qualitative. However in the Technical Specification for the NARs, the countries are requested to report in their NARs on the acceptance and action criteria for the various ageing phenomena. Apart from indicating those criteria, it is obvious that the NARs must discuss the compliance of the reactors with these criteria. Could you please provide this information? | email | The compliance of the RPV components with the allowable fatigue usage is proved by the fatigue design review calculations resulting CUF<1,0 for all pressure retaining components. The CUF>1,0 results of the calculations of the CRDM housing nozzle inner tube fixing welds (that plays the role of cladding for corrosion protection), was taken into account as acceptable after introducing annual inspections of the weld area. The compliance of the RPV components with the allowable radiation embrittlement is proved by the PTS calculations resulting allowable critical emrittlement temperature values that are much higher than the calculated - on the base of EOL fluence, and validated by surveillance program - Tk values of the RPV components.
HU-37 |  | Netherlands | Hungary | 07. Concrete containment structures | 7.1.2 | Reference is made to a lot of different documents (like listed in among others section 7.1.2.2). What are the leading principles for the ageing assessment? | email | The leading principles for the ageing management were taken from the Guidelines of the HAEA, US NRC GALL Report, IAEA – TECDOC-1025, IAEA No. NS-G-2.6 and the ACI 349-02 documents. During the reviews and development of the AMPs the most relevant documents – e.g. IGALL – were also taken into account.
HU-38 |  | RPV expert group | Hungary | 05. Reactor Pressure Vessels | - | 5.1.3 In accordance with WENRA Technical Specification, chapter 5.1.3, can you describe in more detail the ageing management programs applied to the RPV?. | expert group 2 | All the AMP elements required by the WENRA TP 5.1.3 are described in the National Report. See Fig. 2.3.1-1 in general and subsection 05.1.1 in particular. For more detailed description of the RPV AMP can be found in ISI, RPV maintenance programs, RPV wall surveillance, fatigue cycle monitoring, water chemistry etc programmes which extent large and those exceed the suggested page/volume limitations of the National Report.
HU-39 |  | RPV expert group | Hungary | 05. Reactor Pressure Vessels | - | 5.1.3.1 NAR Chapter 5.1.3.1. Could you provide more information about the in-service inspection activities established?. | expert group 2 | ISI of RPVs has been performed since the commissioning of the plant: standardized NDT methods (VT, UT, ET, PT and AET) have been applied and performed manually or by remotely controlled manipulator according to the accessibility and radiation conditions of the given location. UT is implemented from both ID and OD. ID inspection has always been done by vendor using state-of-the-art technique such as TOFD, whilst OD examination is performed by the plant staff using the upgraded USK-213 equipment. The ID UT system (equipment, procedure) currently applied for examination of circumferential welds, base metal in beltline region, inner radii and safe end-to-pipe welds, and the ET system (equipment, procedure) currently applied for examination of cladding are qualified. The qualification is made in accordance with the European methodology. Acceptance standards comply with ASME BPVC Section XI standards. Details of ISI is presented in subsection 05.1.3.1.
HU-40 |  | RPV expert group | Hungary | 05. Reactor Pressure Vessels | 63 | 5.1.3.1 NAR Table 05.1.3.1-1 Are all activities of this table performed within the in-service program?. Including the manual ultrasonic testing of the cladding adhesion?. | expert group 2 | All NDT procedures listed in Table 05.1.3.1-1 are used during ISI. Manual UT for cladding adhesion is used on the RPV flange.
HU-41 |  | RPV expert group | Hungary | 05. Reactor Pressure Vessels | - | 5.1.3.1 What is the inspection program applied to surveillance of dissimilar metal welds (DMW)? | expert group 2 | ISI program of RPV DMWs: UT and ET from ID and UT and PT from OD (inspection category is B-F according to ASME BPVC Section XI).
HU-42 |  | RPV expert group | Hungary | 05. Reactor Pressure Vessels | 66 | 5.1.3.1 What load assumptions have been considered to revalidate the fatigue analyses for the new operation period (LTO)? Has been considered in these analyses the influence of primary water (environmental fatigue)?. | expert group 2 | A new load catalog was generated and taken into account by the revalidation calculations. The basis of the new load catalog was the original design load catalog that was partially modified, supplemented using the 20-30 years of operation experience, taking into account the past and the planned changes of the operational modes. EAF was taken into account. (See also the answer in question line 22). | the reference points obviously to Q22 i.e. HU-22 since the source file line 22 does not contain querstion for Humgary
HU-43 |  | RPV expert group | Hungary | 05. Reactor Pressure Vessels | 64 | 5.1.3.1 Is applied in Paks NPP an ex-vessel neutron dosimetry programme (EVND) for the monitoring of neutron exposure of the vessel materials up to the end of lifetime (LTO)?. | expert group 2 | Ex-vessel (cavity) dosimetry program is applied to validate fast neutron flux calculations.
HU-44 |  | Concrete containment PCPV expert group | Hungary | 07. Concrete containment structures | par. 7.1.2 | Specify which part of the RD programs is managed by Licensee and which from Industry or other relevant bodies (par 7.1.2. pag.27 of WENRA TS); | expert group 4 | Both the on-site inspection programmes and the laboratory tests are done by industrial and other relevant parties.
HU-45 |  | Concrete containment PCPV expert group | Hungary | 07. Concrete containment structures | par. 7.1.3 | The acceptance criteria (point C, pag.27 of WENRA TS) are not reported in par. 7.1.3. Please enhance the information | expert group 4 | In the para 7.1.3. a reference can be found for the acceptance criteria, which are placed in para 7.1.2.1. (Both ageing effects and acceptance criteria are covered in para 7.1.2.1.)
HU-46 |  | Concrete containment PCPV expert group | Hungary | 07. Concrete containment structures | 75 - 77 | The content of para “7.1.1 Scope of ageing management for concrete structures” corresponds to the requirements listed in section 07.1.1 of RHWG Report to WENRA and comprises sufficient information on the process/procedures for the identification of ageing mechanisms. At the same time, there is no information on the methods and criteria used for selecting components within the scope of ageing management (see item “a” of para 07.1.1 of RHWG Report to WENRA). This information should be added to the Hungary NAR or corresponding clarifications might be provided as an answer. | expert group 4 | Selection of components within the scope of ageing management is dealt with in para 2.3.1. “Scope of the overall AMP”.
HU-47 |  | Concrete containment PCPV expert group | Hungary | 07. Concrete containment structures | 81 - 82 | The content of para “7.1.3 Monitoring, testing, sampling and inspection activities for concrete structures” corresponds to the requirements listed in section 07.1.3 of RHWG REPORT TO WENRA and comprises sufficient information on operational monitoring, non-destructive tests requirements and intervals for different parts of concrete structures subjected to AM, and related acceptance criteria. At the same time, there is no information on the monitoring programmes used for monitoring, testing, sampling and inspection activities for concrete structures (see para 07.1.3 of RHWG REPORT TO WENRA). This information should be added to the Hungary NAR or corresponding clarifications might be provided as an answer. | expert group 4 | The list of 16 programmes used for monitoring, testing, sampling, and inspection activities for concrete structures is shown in Table 7.1.1.1.-1. in para 7.1.1.1. These programmes contain the detailed descriptions of the visual inspections, of the non-destructive and destructive examinations (using samples), and of the laboratory examinations. The programmes also include the regulations for the execution of the above examinations, for trend analyses, and for stress calculations. All of the above structure programmes are based on the 10 attributes presented in para 2.2. Building programme BAMP-B-002 for the main building including the hermetic compartment determines the specific conditions, framework, logistical aspects, etc. for the implementation of the structure programmes. The surveillance programmes used for the main building including the hermetic compartment are related to building settlement, leak-tightness of the hermetic compartment, and boric acid corrosion of the reinforced concrete structures (BAMP-A-008, BAMP-A-0013 and BAMP-A-005).
HU-48 |  | Concrete containment PCPV expert group | Hungary | 07. Concrete containment structures | 82 - 83 | The content of para “7.1.4 Preventive and remedial actions for concrete structures” does not fully correspond to the requirements listed in section 07.1.4 of RHWG REPORT TO WENRA. There is no description of the criteria and procedures for the implementation of actions. Actually, it is written in para 7.1.4 that preventive actions are contained in the relevant building programmes and structure programmes. The proposed approach seems to be acceptable. Information of section 07.1.4 of RHWG REPORT TO WENRA should be added to the Hungary NAR or corresponding clarifications might be provided as an answer. | expert group 4 | The preventive and remedial actions and the criteria and procedures for their implementation is contained in the relevant building programmes and structure programmes. Section 7.1.4.1. and 7.1.4.2. list some typical examples for the preventive and remedial actions for concrete structures. The details can be found in the building programmes and structure programmes. E.g., para 2. “Preventive actions” of the AMP for Reinforced concrete superstructures contains the following parts (among others): 2.1. Preventive actions; 2.1.1. Examination and evaluation methods (Non-destructive examinations, Structural performance (integrity) tests, Examination of concrete and reinforcing steel, Destructive examinations, Methods of analyses and calculations); 2.1.2. Cracking treatment; 2.1.3. Repair of concrete. Acceptance criteria, Corrective actions and their implementation, Processes of certification and feedback, Administrative control are dealt with in Chapters 6, 7, 8, and 9 of this programme, respectively.
HU-49 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter 04.1.1.2 | The text states that the Regulator identifies degradation mechanisms affecting concealed piping in its Guideline. Is the Regulator responsible for degradation mechanisms missed in the guideline? | expert group 5 | The development of the guide is a complex process involving the relevant TSOs and licensees and based on the best international and national practises. The regulatory guideline identifies the critical degradation mechanisms and the licensees is responsible for the exhaustiveness.
HU-50 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter 04.1.2.1 (Z-SAMP-18) | CS piping experienced heavy pitting due to MIC. The same does not apply for CS ESW piping carrying the very same Danube water. What is the reason of such completely opposite behaviour? | expert group 5 | The main reason is the difference in the operational circumstances. The CS pipes with MIC related leakages originated from the Danube side are operated with stagnant, or very small flow velocities, the WENRA sample related, buried CS pipes are operated continuously with relatively high flow velocities. MIC is active in both pipings, but with different corrosion rates.
HU-51 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter 04.1.2.1 (Z-SAMP-18) | Is the paragraph addressing MIC of SS in boric acid related to SAMP18 (Danube water CS pipings) or to SAMP17? | expert group 5 | SAMP-18 does not, the SAM-17 does manage stainless steel pipes with boric acid media.
HU-52 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter 04.1.3.1 | A permeability of pipe section and deposits are checked using special programmes. What kind of programmes are used? Flow balances, flow rate measurements, remote VTs? | expert group 5 | Flow rate measurement is applied.
HU-53 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter 04.1.4.1 | What does it mean "high pressure flushing"? Is it a water lancing/washing (https://en.wikipedia.org/wiki/Pressure_washing)? How it is accomplished inside long and narrow piping? | expert group 5 | Yes, high pressure water pipe cleaning/washing technology with pressure-jet self-moving heads is applied for the long, and narrow pipes as well.
HU-54 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter Budapest Research Reactor | TZ lines use double wall SS (austenite probably) piping. A crack of inner wall is identified by leak observed in storage building. The same approach cannot be used for outer wall cracks or pin holes unless piping is below water table level. If the piping is above water table then a hole in outer piping can remain unnoticed and subsequent hole in inner pipe can result in uncontained radioactivity spillage. The site has a history of salt assisted corrosion damage which is a concern for SS. Is there any measure addressing described concern? | expert group 5 | The designed lifetime is minumum 30 years. The funcionality is regularly checked by differemt methods, i.e. water laevel in the gravity tank, water chemistry, visual inspections and pressure tests. No corrective measures are necessary as the mentioned tests show no problem.
HU-55 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter Budapest Research Reactor | Weekly VTs are a key measure addresing leaks. Are these true VTs done by qualified NDT stuff or walkdowns by operational personel. Is there a formal procedure for these VT/walkdowns? | expert group 5 | Yes, both. There is a procedure for walk downs.
HU-56 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter Budapest Research Reactor | What is a technical basis for 10 yrs estimated residual lifetime of pipings? Is it based on VTs? | expert group 5 | It's based on design datas.
HU-57 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | Chapter Budapest Research Reactor | What is a minimal volume of leaked radioactive waste from TZ pipeline which can be identified by tank level measurement? | expert group 5 | The minumum detectable change in water level is 1 cm, it corresponds to about 500 litres. The value is checked in the control room every six hours.
HU-58 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | 52 | Section 4.1.3.1 - Activities, methods, inspection frequency, for pipework containing radioactive effluents. The NAR states that “Visual inspection and/or other material testing at least every 10 years in areas where visual inspection, material testing can be carried out, in non-accessible areas in case the occurrence of defects is detected i.e. during in service pressure tests or single condition assessment” Please can you provide some detail of what this material testing entails and how the results are interpreted? | expert group 5 | The pipes were examined using remotely controlled special pipe manipulator (crawler), equipped with UT, ET transducers and TV cameras. Most of the detected flaws are surface flaws, some are shallow volumetric type, (small, connected cavities). Volumetric indications with depth of more, than 50% of the wall thickness were/are repaired by local welding or replaced.
HU-59 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | 52 | Section 4.1.3.1 - Pipework that transfers fuel to emergency power supply. The NAR states “Detection of signs of possible leakage because of through wall defects during the in-service walkdowns”. I would expect that detection of a loss of integrity via establishing the presence of leaks would be an unattractive option to manage the condition of the pipework. Please can you confirm whether this option is considered a “last resort” once all other methods of inspection etc. have been considered and employed? I also note that reference is made to inspection of excavated reference pipe sections at least every 10 years. Is there any operational experience to identify the potential benefits and challenges of adopting this approach? For example, does the repeated excavation of the same section on numerous occasions have an adverse effect on its integrity? | expert group 5 | Yes, the detection of signs of possible leakage during the walkdowns is considered to be the "last resort” and listed as the last one of the inspection activities. Yes, we agree, that the excavation activities can result in damages of the outer surface corrosion protection of the pipes. The excavation is needed for the measurement of the remaining wall thickness map of smaller diameter buried piping.
HU-60 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | 56 | Budapest Research Reactor, secondary circuit VA01; VA08 pipework. Assuming that the replacement pipework is carbon steel as per original design, please can you identify the future inspection program for the new buried carbon steel pipe. I understand that “the use of salt was forbidden and also a weight limitation on vehicle transport was introduced within the area”, However has additional inspection been considered to confirm the pipe’s integrity? | expert group 5 | A pressure test was performed, it can be repeated any time.
HU-61 |  | Concealed pipework expert group | Hungary | 04. Concealed pipework | 50 | Page 50 Section 4.1.2.1 - Ageing mechanisms and acceptance criteria. I consider that a good level of detail has been provided to describe the aging mechanisms and how they have been accounted for. The inclusion of some detail (section 4.1.2.3) relating to R&D activity to establish the nature of microbiologically influenced corrosion in the spent fuel pool cooling system was also useful. | expert group 5 | There is no question, otherwise the comment is accepted.
HU-62 |  | General AMP expert group | Hungary | 02. Overall Ageing Management Programme requirements and implementation | 12 | The programs of Aging Management on RR include the NDT to both priority and non - priority components. IS that a graded approach, or NDT is applied to all components? | expert group 3 on other topics / expert group 1 | As it is indicated on the Figure 2.3.1.1-1. NDT is performed for all priority mechanical SSCs/main components and just "defined components" are in the scope of NDT of non-priority mechanical SSCs. It is graded approach following ASME BPVC Section XI concept.
HU-63 |  | General AMP expert group | Hungary | 02. Overall Ageing Management Programme requirements and implementation | 37 | In the Aging Management Program for the RR form 2009 estimates the residual lifetime of the equipment is 10 years. It is not mention which equipment (SSC) is that, and what will happen with that equipment after the period of 10 years is over? | expert group 3 on other topics / expert group 1 | Tests are done for 10 years because every 10 year we have temporary safety inspection. After the period is over the next test will be preformed.
HU-64 |  | General AMP expert group | Hungary | 02. Overall Ageing Management Programme requirements and implementation | 33 | The categories of R&D applied for Aging Management support for RR are divided in priority and non - priority activities. What is the basis is for such categorisation? | expert group 3 on other topics / expert group 1 | Basis of categorisation of R&D tasks to priority and non-priority ones is their direct impact on safe Long Term Operation.
HU-65 |  | General AMP expert group | Hungary | 02. Overall Ageing Management Programme requirements and implementation | 7 | From the chapter 2.2 of the national reportis is not very clear if the national regulatory framework contains also specific provisions for establishing an AMP for research reactors in Hungary. Could Hungary provide clarificationin in this regard? | expert group 3 on other topics / expert group 1 | Yes, the national regulatory framework contains also specific provisions for establishing an AMP for research reactors in Hungary. Volume 5 of the Nuclear Safety Codes consists of two main chapters, the design of research reactors and the operation of research reactors. The design chapter's aging management subsection contains clear requirements for establishing AMP.
HU-66 |  | General AMP expert group | Hungary | 02. Overall Ageing Management Programme requirements and implementation | N/A | Comment: The description of the AMP for nuclear installations in Hungary covers all elements required by Topical Peer Review 2017 - "Ageing Management Technical Specification for the Na-tional Assessment Reports" | expert group 3 on other topics / expert group 1 | The comment is accepted.
HU-67 |  | Cables expert group | Hungary | 03. Electrical cables | 17 | What are the criteria for establishing periodicity of technical state evaluation using non-destructive methods for NPP cables important to safety? | expert group 3 | We have investigated a lot of technically available measurement methods on cables together with Technical University of Budapest. Finally we have choosen two methods which showed trends with ageing and they were incorporated into the AMP (Shore D hardness measurement and a reflectometry measurement). TUB has performed a lot of measurments on samples with these two methods and found there is a certain but slow degradation mechanism which can be revealed by these methods. Therefore they could determine the peridodicity of measurments for these two methods, as not so frequent. For other methods in AMPs we could use the proposals of IGALL programs.
HU-68 |  | Cables expert group | Hungary | 03. Electrical cables | 26 | For RR, the cables seems not to be in the series of SSCs that are in the scope of the AMP. Is this correct? | expert group 3 | Yes, they are not in the scope of of the AMP.
HU-69 |  | Cables expert group | Hungary | 03. Electrical cables | 39 | Is there any difference between the terms, “cables important to safety” and “safety relevant cables"? Kindly explain. | expert group 3 | No difference, they mean the same.
HU-70 |  | Cables expert group | Hungary | 03. Electrical cables | 39 | Cable Group SR and SR1: It appears that those cables do not need to be qualified. Nevertheless, as indicated in the table 03.1.1 1 in NAR annex, some of them are supported by “LOCA documents” or “artificial ageing data”. Could you kindly clarify this? | expert group 3 | It is only the document identification question of the company who had performed the laboratory testing of equipment and cables. The document identification is always starting with "LOCA-". But the fact is that SR means safety related cable and among these SR1 means not subjected to harsh environment (or may be subjected, but in that case performance of its function is not required as justified ba analysis) and according to this statement these cables must be qualified only for normal operating conditions. That requires artificial ageing, too, of course, but not followed by a LOCA test as it is written in the corresponding lines of annex table.
HU-71 |  | Cables expert group | Hungary | 03. Electrical cables | 39 | The term “severe accident” seems not to be uniquely defined. Is the " SA" an accident beyond plant design basis? Consequently are there cables in Paks NPP qualified for severe environmental conditions different than LOCA/HELB?. | expert group 3 | Yes, that means BDBA. There are certain types of cables qualified for BDBA parameteres (beyond LOCA) which are used for example accident measurement system.
HU-72 |  | Cables expert group | Hungary | 03. Electrical cables | 39 | Are there other non-EQ cables (> 380 V) buried or In trenches, where “significant moisture or submergence” could occur? . if yes, those are likely to be subject to “water treeing”, and require AMP. | expert group 3 | There are no cables with safety functions which are buried. Lot of cables are located in cable ducts/trenches effected temporarily by rain water but these rooms have ventilation and draining system, so there is no submergence or significant moisture.
HU-73 |  | Cables expert group | Hungary | 03. Electrical cables | 40 | Is the TLAA undertaken for the cables? | expert group 3 | Yes, TLAA means EQ in case of active electrical and I&C components and also cables.
HU-74 |  | Cables expert group | Hungary | 03. Electrical cables | 43 | There seems to be no information provided (scope, ageing assessment, monitoring, testing, sampling and inspection activities) related with the not-EQ'd cables in the V-SAMP-12 and V-SAMP-13. Could you please clarify. | expert group 3 | Yes, but the reason of why there is no information about these programs that the types of cables belonging to these programs are not in the scope of this report. But of course the programs are very similar, each of them consists of the ten AMP attributes including these information, too.
HU-75 |  | Cables expert group | Hungary | 03. Electrical cables | 43 | It is stated that periodic assessment of environmental parameters is performed for cables with environmental qualification. What is the frequency of such an assessment? What changes in parameters would lead to a reconsideration of cable qualification? | expert group 3 | We have performed the initial qualification process already under the conditions of operating plant, which means we had to collect the environmental operational conditions by the means of measurment, not calculations or assumptions, so they are very reliable. These conditions are not changing rapidly, so we are performing an evaluation of the environmental conditions in every ten years for the preparation Periodic Safety Analysis Report. So up till now we have not set up a criteria for what is a significant alteration of paramteres which could result in the need of requalification.
HU-76 |  | Cables expert group | Hungary | 03. Electrical cables | 43 | It appears that on the RR, visual inspection is used for detecting cable heating. What about thermos vision, or thermography for cable heating, just visual inspections. | expert group 3 | Just visual inspections.
HU-77 |  | Cables expert group | Hungary | 03. Electrical cables | 48 | On RR, surveillance of the plastic coated cables appears to be performed using instructions and standards related to cables with oil and paper insulation. Is this a mistake or no specific instructions exist for the plastic coated cables? | expert group 3 | There are no plastic coated cables in BRR.
HU-78 |  | Cables expert group | Hungary | 03. Electrical cables | 49 | The cables in the AMP appears to include only primary side cables of the two transformers and 7 nuclear measurement chains, and does not include cables supplying SSCs important to safety? What are the criteria used to select this two types/groups of cables? | expert group 3 | According to IAEA SSG-10 the AMP scope is include the SSCs important to safety. The method for determining the safety significance of SSCs should be based on deterministic methods, complemented by probabilistic methods and engineering judgement.
HU-79 |  | Cables expert group | Hungary | 03. Electrical cables | 49 | What is licensee’s experience of the application of AMPs for electrical cables? | expert group 3 | Up till now we could not observe any significant trends related to AMPs. But as it is written in the document we are rather qualifying cables than managing them with AMPs.
HU-80 |  | Cables expert group | Hungary | 03. Electrical cables | 46 | Section 03.2.3 of NAR describes the OWST tests in 2002 and 2003 for 6 kV plastic insulated cables belonging to the qualification group CG_SZAMK6 undertaken after the cable failure in 2001. OTWS cable measurement was introduced in every case where repair or installation of 6 kV cable was performed. A further decision was made on the replacement of cables within the qualification group CG_N2XS and CG_NTSCgEWöu. Question: What is the design of the original cables? Were the replacement cables of a different design ? Are there any additional activities to maintain qualification of the replacement cables? | expert group 3 | The original cable types were SZAMkrKVM and SZAQkrKVM. The replacement cable types were new types: N2XS cable type family and NTSCgEWöu types. Later we have performed environmental qualification for these new types.
HU-81 |  | Cables expert group | Hungary | 03. Electrical cables | 46 | Did you consider measures to reduce current load (e.g. using of cables with a large cross-section of a conductor or connection of a parallel cable) when replacing the power cables ? | expert group 3 | No, there is no such an intent, because we have not found significant deterioration related to high operational currents. All of the cables are designed according to the standards in relation with load current, voltage drops, etc.
HU-82 |  | EC | Hungary | 02. Overall Ageing Management Programme requirements and implementation | pg. 16 - 02.3.1.3 | Could it be possible to have a description of the program for the structures and buildings? |  | The extent of the structure and building programmes which are applied at the plant are very large therefore they exceed the requested volume of National Report.
HU-83 |  | EC | Hungary | 02. Overall Ageing Management Programme requirements and implementation | pg. 26 - 02.3.1 | Why for the research reactor do you consider the "human factor" as an ageing mechanism in the research reactor? What does it means? |  | Human factor is real problematic area ( Ageing of operating staff, lack of professionals, etc ) but we agree it is not part of AMP. The handling of HOF question is a part of integrated management system.
HU-84 |  | EC | Hungary | 03. Electrical cables | 3.3 | Report says "The strength of the system is the well-based, systematic structure, but attention should be paid to the degradation mechanisms of other areas on the condition of the cables.." Can you please check / clarify this sentence. |  | Other areas reflect to degradation due to design and construction failures, which are out of the scope of AM, may can effect to the condition of cables.
HU-85 |  | EC | Hungary | 03. Electrical cables | Generic Section 3 | The report does not provide any information on ageing assessment of neutron flux instrumentation cables. Does this mean that there are no periodic testing of these cables? |  | No, because there is no such kind of AMP. We have environmentally qualified all of these cables.
HU-86 |  | EC | Hungary | 03. Electrical cables | Section 03.1.3.1 | Environmentally qualified cables have no follow-up of ageing? |  | No, because the evolution of the degradation mechanisms to be managed have already been taken into account by the standard EQ tests.
HU-87 |  | EC | Hungary | 04. Concealed pipework | 55-56 | Budapest Research Reactor: What is the material of the new secondary pipeline (carbon steel with protective coating on outer surface?)? |  | Spiral seam steel tube P235GH, inner coated with 0.05 mm epoxid APIRP 5l.2, outer coated with 2.5 mm PEN according to DIN 30670.
HU-88 |  | EC | Hungary | 05. Reactor Pressure Vessels |  | No information is provided in the report on the possible presence of hydrogen flakes in RPV base material in any of the operating power reactors. How this issue was investigated? |  | We analyzed the manufacturing procedures and operating parameters of Paks RPVs from the point of view of the flaws detected in D3/T2; analyzed the capability of the NDT performed in the entire life of the vessels (including NDT during and after manufacturing, PSI, ISI); summarized the NDT results and, based on these, evaluated the integrity of the reactor pressure vessels. Based on the evaluation results, our position is that the opportunity for developing flaws at Paks RPVs similar to that in D3/T2 vessels can be excluded with high probability. The NDT applied in Paks is suitable for detection of laminar flaws. Examinations performed so far did not detect such flaws that had been detected in the base material of D3/T2 reactor pressure vessels.
HU-89 |  | EC | Hungary | 05. Reactor Pressure Vessels |  | Hungary has participated in the development of the VERLIFE guidelines (Guidelines for Integrity and Lifetime Assessment of Components and Piping in WWER Nuclear Power Plants), but these guidelines are not referenced in the National Report. Is any intention to adopt VERLIFE as part of the ageing management programme? |  | VERLIFE is not directly applied in Hungary but its content was considered during the development of the relavant HAEA guidelines.
HU-90 |  | EC | Hungary | 07. Concrete containment structures | 81 | Section 7.1.3.1. Acceptance criteria are provided in 7.1.2.1, but not for all the mentioned inspections, e.g. building settlement, chemical content of groundwater, leak tests of hermetic lining. What are the acceptance criteria for these tests and what would be the remedial actions in case they would be exceeded? |  | • The acceptance criteria for the buildings’ settlement are varied, depending on the structure of the buildings. In simple cases, the acceptance criteria refer to the maximum settlement value within 3 months (2 mm per 3 months) and to the maximum difference between the values measured at two neighbouring measurement points. In cases of complex buildings, like the main building, a more sophisticated system of criteria is applied. Here the predicted, acceptable settlement values for each measurement points and the measured values at the points are taken into account during the evaluation process.• The criteria for the groundwater chemistry are as follows: pH ˃5.5; chlorides < 500 ppm; sulphates < 1500 ppm.• Permitted leakage rate for the hermetic compartment (leak tightness is ensured by the hermetic lining): 14.7 % per day, at an overpressure of 1.5 bar and at a temperature of 300 K. The above acceptance criteria can be exceeded and the possible remedial actions are as follows:• In case of settlement: calculations for the building structure, strengthening of the improper structures, or implementing ground stabilization.• If the groundwater becomes aggressive, sampling-based condition assessment of the concrete structure is to be performed. When the degradation has been identified, the selection of the method to be applied is based on expert’s opinion. (In case of Paks NPP, groundwater is not aggressive, the values of the groundwater chemistry are considerably more advantageous than the values of the acceptance criteria).• In case of the hermetic lining: the leaking areas are to be identified and the leak tightness should be ensured by the lining’s repair.
HU-91 |  | EC | Hungary | 07. Concrete containment structures | 81 | From the list of inspections performed on the concrete, which are the ones that are intended to prevent corrosion of the reinforcement steel or to detect corrosion? |  | The most important examination for preventing and detecting the corrosion of the reinforcement steel is the visual inspection of the concrete’s surface. Cracks in the concrete structure and defects of the concrete cover on the steel reinforcement can result in the corrosion of the steel. Rust spots developing on the concrete’s surface can also be an indication of corrosion. Information not only on the actual condition, but also on the corrosion rate can be gained by the measurement of pH in the concrete and by the direct inspection of the steel reinforcement.
HU-92 |  | EC | Hungary | 07. Concrete containment structures | 81 | Which portion of the hermetic lining is subjected to US thickness measurement? How is the area to be inspected selected in order to ensure that areas most prone to thickness loss will be covered? |  | Ultrasonic thickness-measurements of the hermetic lining is performed on the following areas: • Wherever spots indicating the corrosion of the hermetic lining occur on the coating’s surface. • Wherever it can be presumed that the contact between the concrete and the lining is improper (a gap is present). Here the concrete cannot ensure the proper protection of the lining against corrosion. • Wherever it can be presumed that the lining's surface is exposed to seeping water, especially borated water. (Leakage and indications of leakage are mapped at each overhaul, and the changes are analysed.) • Additionally, thickness is generally measured in all accessible areas, the number of measurement points is 1 point per 10 m2 surface area.
HU-93 |  | EC | Hungary | 07. Concrete containment structures | 77, 81 | Section 7.1.2.1. How is concrete strength evaluated with reference to the inspections listed in section 7.1.3.1? Are surveillance specimens used? |  | Schmidt-hammer tests are conducted on the spot. Periodic sampling at the 3 inspection hatches of each Unit are made, and laboratory tests of the samples are carried out to determine the compression strength of the concrete. Occasionally, sampling is made at other places, too, and laboratory tests of these samples are also carried out to determine the compression strength.
HU-94 |  | EC | Hungary | 07. Concrete containment structures | general | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | The fulfilment of the leak-tightness function of the containment is ensured by the hermetic lining and other connecting elements, which are only partly accessible for inspection. The fulfilment of the leak-tightness function is demonstrated by the results of the integrated leak-tightness tests.
IT-1 |  | Poland | Italy | 03. Electrical cables | 37, 38 | 1. What type of functional and instrumental tests are performed in the TRIGA RC-1 research reactor? 2. What are frequencies of inspections performed by the licensee of the TRIGA RC-1 research reactor mentioned in a table 8? | Website | 1. Each chain is subject to functional tests; the instrumental test is intended as a measure of the values, for example of current or voltage, in prefixed points. 2. As mentioned in the Report, a formal AMP is not implemented at TRIGA RC-1 research reactor. A large refurbishment programme has to be implemented during the current year; following which the licensee will present a formal proposal to the NRA. Table 8 of the Report summarizes the licensee first proposal of an ageing evaluation program for electrical cables and electronic, timing for inspection will be proposed later.
IT-2 |  | Poland | Italy | 01. General information | 6, 7, 18 | 1. Are the operating licenses issued for unlimited time or are they renewed periodically? 2. Are those „interventions aimed at adapting the SSCs of the TRIGA RC-1 reactor due to ageing” an outcome of this TPR project or has the need for them been identified earlier? 3. How is the dust filtering system efficiency test conducted? Is it meant to check efficiency in catching radionuclides? | Website | 1) The licence is unlimited in time but every five years a periodic review is requested according to th conditions attached to the licence. 2) As reported, in the second half of 2018 the reactor will be put in temporary shutdown condition in order to implement some refurbishment based even on ageing-related evaluations. These interventions have been scheduled due the results coming from the periodic review. 3.The filtering efficiency is made by means of a tracer concentration variation, and it's meant for catching radionuclides.
IT-3 |  | Poland | Italy | 04. Concealed pipework | 42 | 1. Have there been any non-destructive tests conducted on primary circuits at both reactors? | Website | Daily visual inspection and analysis of online monitoring of hydraulic parameters. It must be emphasized that there are no concealed pipework. All hydraulic circuits are directly inspectionable.
IT-4 |  | Norway | Italy | 02. Overall Ageing Management Programme requirements and implementation | 10-35 | How is the operating experience of retiring staff used in AMP? | Website | According to Italian law the retired staff of a Public Administration, as all the current RR Operators are, cannot have a formal work relationship with the previous employer. In any case, it is a well-established practice to turn, on a voluntary basis, to the retired staff in order to use their experience, especially when the memory of past events is useful for dealing with the problems that are seen.
IT-5 |  | Finland | Italy | 05. Reactor Pressure Vessels | § 5 | Schematic drawings with the main parts could be provided for both reactor types. The drawings could be very simple describing only the basic structure. This could help to better understand the constructions of the reactors and the surrounding structures. | Website | See Vertical and Horizontal section of the reactor in attached file “RC-1_figures ageing” See fig. 1 in attached file “LENA_references” | The content of “RC-1_figure ageing” & "LENA_references" is copied in the worsheet "IT_Figs & Refs"
IT-6 |  | Finland | Italy | 05. Reactor Pressure Vessels | 47-48 | There is no information in chapters 5.1.4 and 5.2 about Triga RC-1. Some information could be added concerning also Triga RC-1. If there is no relevant information it could be indicated e.g. “not applicable”. | Website | Not applicable
IT-7 |  | Finland | Italy | 05. Reactor Pressure Vessels | 45-46 | It is recommended to provide some explanation for the word “graduated” in this context? | Website | We are having difficulties in answering this question because we could not find the word "graduated" in the report.
IT-8 |  | Finland | Italy | 05. Reactor Pressure Vessels | Generally | According to Finnish operating experience on a similar research reactor, visual inspections are important in assessing liner condition. What kind of plans are considered for visual inspections in the future? | Website | As far as concern RC-1 endoscopic and camera inspections will be part of the AMP that will be implemented. Frequency will be part of the proposal. In TRIGA MARK II, video inspection of the reactor tank aimed at identifying initial oxidation states of aluminium to mullite [Al (4 + 2x) Si (2-2x) O (10-x)], in order to acquire a database of images for subsequent checks for comparison and verification of parts not visible from the free surface of the liner Periodic tank visual inspection are planned (each 3 years).
IT-9 |  | Switzerland | Italy | 03. Electrical cables | 39 | Table9: Why is replacement complexity of control console higher than for the cabling? Why is there no ageing mechanism 1? Why/how is mechanism 9 (rule change) an ageing mechanism for the console? | Website | Authorization process, quality assurance and technology changes affect more the control console instead of cables shich are also more reachable. About the ageing mechanism 1, only few meters of cable are in a low neutron field and certified as class 1E. New technology and new standards e.g. fire regulation, require requirements changes.
IT-10 |  | Switzerland | Italy | 03. Electrical cables | 41 | Textline11: What (kind of) safety system cables are in core applied? What experience have been made with it? Is only electrical resistance or also signal transmission behaviour measured? | Website | Only the cabling of power channels is considered a safety system; electrical resistance is measured. Up to now no relevant changes in cabling resistance are measured.
IT-11 |  | Germany | Italy | 02. Overall Ageing Management Programme requirements and implementation | 2 | An AMP (ageing management program) for TRIGA Mark II reactor is incorporated in IMS (Integrated Management System) and is based on the IAEA guideline SSG-10 “Ageing Management for Research Reactors”. Regarding the TRIGA RC-1 reactor it is not clear, what is the current status of the AMP. Could Italy elaborate more on this topic? E.g.: Is it still under development or is already being implemented? Is AMP a part of IMS (as it is the case for TRIGA Mark II reactor), or is it an independent comprehensive program? What is regulatory basis for AMP (IAEA SSG-10 or another documents)? | email | Regarding the TRIGA RC-1 reactor a formal AMP is not yet implemented. During the current year wide refurbishment activities are scheduled as stated in the report. Following these activities an AMP will be submitted to NRA for review and approval. No IMS is currently adopted on TRIGA RC-1.
IT-12 |  | Germany | Italy | 02. Overall Ageing Management Programme requirements and implementation | 12 | It states that "For systems with a research reactor power not exceeding 100 kW thermal does not apply the procedure laid down in Articles 38 (Technical Examination) and 39 (Consultation with the Concerned Authorities) [Procedures for licensing process]. According to a graded approach a simplified procedure is foreseen for RRs with power below 100 kWth". Does Italy have any regulatory procedures, which apply for the research reactors with low thermal power (below 100 kW)? Could Italy elaborate more on the graded approach, which is applied for such low power facilities? | email | The licensing procedure provided for by the Italian law for research reactors is the same as that foreseen for NPPs. For research reactors with power below 100 kW there is an explicit provision of the law that simplifies the authorization process according to a graded approach. The simplification consists in skipping some steps of the licensing process as described in the Report. These simplifications concern some aspects of the technical assessment process and the non involvement of other administrations in the licensing procedure. It has also to be mentioned that the construction of new reactors is not currently envisaged in Italy.
IT-13 |  | Germany | Italy | 03. Electrical cables | 40 | Could licensee of TRIGA RC-1 elaborate on their experience with the application of AMP for electrical cables? Chapter 03.2 contains only the experiences of TRIGA Mark II reactor. | email | At present an AMP for the TRIGA RC-1 has not been formally implemented. For this reason 3.2 is "not applicable" for RC-1.
IT-14 |  | Germany | Italy | 04. Concealed pipework | 44 | Could licensee of TRIGA RC-1 elaborate on preventive and remedial actions for concealed pipework? Chapter 04.1.4 contains only corresponding measures for TRIGA Mark II reactor. | email | It must be emphasized that there are no concealed pipework. All hydraulic circuits are directly inspectionable. Development of an AMP is foreseen at the end of the refurbishment activities that should be carried out in the second half of the current year
IT-15 |  | Germany | Italy | 05. Reactor Pressure Vessels | 47 | Could licensee of TRIGA RC-1 elaborate on preventive and remedial actions for RPV? Chapter 05.1.4 contains only corresponding measures for TRIGA Mark II reactor. | email | It should be noted that in the past, even in the absence of an AMP, preventive or recovery actions were carried out on the basis of the results of the periodic checks.
IT-16 |  | Germany | Italy | 05. Reactor Pressure Vessels | 48 | Could licensee of TRIGA RC-1 elaborate on their experience with the application of AMP for RPV? Chapter 05.2 contains only the experiences of TRIGA Mark II reactor. | email | At present an AMP for the TRIGA RC-1 has not been formally implemented. For this reason 5.2 is "not applicable" for RC-1. It should be noted that in the past, even in the absence of an AMP, preventive or recovery actions were carried out on the basis of the results of the periodic checks.
IT-17 |  | Germany | Italy | 07. Concrete containment structures | 50 | Could licensee of TRIGA RC-1 elaborate more on the application of AMP for concrete structures? Were there any measures taken except of the re-assessment of the seismic resistance of the reactor building structures? | email | AMP will be implemented soon: No specific experience in AMPs regarding concrete structures can be highlighted. In the planned refurbishment activities scheduled for the second half of the current year, ordinary maintenance actions are also included for the reactor building.
IT-18 |  | Netherlands | Italy | 02. Overall Ageing Management Programme requirements and implementation | 2.4/p33 | What external /international experience from operation or R&D is used to develop and regularly improve the AMP? | email | Technical meeting and International Atomic Energy Agency (IAEA) e.g.: T3-TM-54962: Technical Meeting on Research Reactor Ageing Management, Refurbishment and Modernization - 30 Oct – 03 Nov, 2017; M6, M Building, VIC, Vienna, Austria International Group on Research Reactors (IGORR) & IAEA Technical Meeting DCC, Daejeon Korea 13 – 18 October 2013 Coordinated Research Projects (CRP's) e.g.: IAEA CRP T-34003 Condition Monitoring and Incipient Failure Detection of Rotating Equipment in Research Reactors According to the first interlocutions with RC-1, the AMP will be developed by means of a graded approach applied to the items explained in the IAEA Specific Safety Guide on " Ageing management for research Reactors", SSG-10, with a particular attention to other TRIGA reactors experiences
IT-19 |  | Netherlands | Italy | 02. Overall Ageing Management Programme requirements and implementation | 2.4/p33 | In what AM-relevant international groups do the operator and the regulator participate? | email | The Competent Authority actively participates in both the European regulators in the WENRA and ENSREG context, and in the IAEA and OECD activities. The licensee are participating to Research Reactor Operating Group (RROG), IAEA - World TRIGA coalition, IAEA - Technical Working Group on Research Reactors (TWGRR)
IT-20 |  | Netherlands | Italy | 02. Overall Ageing Management Programme requirements and implementation | 2.4/p33 | AM experience/events in Italian RR: are these also shared through the IAEA Incident Reporting System for Research Reactors (IRSRR)? | email | The answer is affirmative, for example the last event reported in the IRSRR concerned the loss of integrity of the instrumented element of the TRIGA MARK II reactor in Pavia
IT-21 |  | Netherlands | Italy | 02. Overall Ageing Management Programme requirements and implementation | 2.4/p33 | Has it been considered to invite an IAEA INSARR mission (which also has a module on ageing management)? | email | In mid-2013, LENA hosted the OMARR (Operation and Maintenance Assessment for Research Reactors) mission with experts from the IAEA and other similar plants, as regards peer-review activities on reactor operation and maintenance aspects. It was a "trailblazer" mission for a small research reactor of dimensions like LENA, offering the opportunity to evaluate operational and maintenance processes and to share multiple experiences. Based on the positive results of the above mission, LENA received a further IAEA mission (INSARR, Integrated Safety and Assessment for Research Reactors) on integrated safety assessment for research reactors and the follow up mission as external audit on implementations of INSARR mission recommendations.
IT-22 |  | Netherlands | Italy | 03. Electrical cables | p.6 | In the TRIGA RC-1 section of 3.1.1, it is mentioned that 'low voltage' is one of the focus categories of electrical cables as stated in the Technical Specification. However, low voltage is not part of that list. Please elaborate. | email | The implementation of an AMP regarding the category "electrical cable" correctly starts from the identification of the two types of cables that can be investigated. Both types have to be evaluated by means of features or components functionality or integrity listed in 03.1.1 section. The items included into TABLE 8, in our interpretation include low voltage cables and also signal cables, or better each component of TABLE 8 contains cables operating with low voltage and signals. But, if necessary, it's possible to include a further row regarding explicitly low voltage cables.
IT-23 |  | Netherlands | Italy | 03. Electrical cables | section 03.1.2 | In section 03.1.2 it is stated that: 'The replacement for control rods, cables, connections and insulators is normally considered of high complexity and for SSC and measure/safety detectors of average complexity.' could you please clarify what is meant by this statement? | email | As reported by maintenance service, number, location and type of connections make some replaces more complicated than other does, due to the layout of the plant.
IT-24 |  | Netherlands | Italy | 03. Electrical cables | 03.1.3 | In section 03.1.3 it is mentioned for TRIGA RC-1, that no formal implementation of the ageing management program has been executed over the years. Is the periodic inspection viewed as sufficiently adequate for controling ageing related safety issues? | email | It should be noted that in the past, even in the absence of an AMP, preventive or recovery actions were carried out on the basis of the results of the periodic reviews. In addition to the verifications and controls that are carried out periodically on the plant, the operator must submit to the Regulator an annual report on the activities and a five-year report on the status of the plant. The aforementioned reports make it possible to assess the safety level of the plants even in the absence of a formalized AMP.
IT-25 |  | Netherlands | Italy | 03. Electrical cables | 3.1.3, p.37 | The evaluation of the TRIGA MARK II, as a voluntary participant with P<1MWth, adheres clearly to higher standards than the TRIGA RC-1, which has a power of 1MWth and is formally in scope of the Technical Peer Review. What is the origin of this discrepancy? Does it give rise to concern for the ISPRA in its function as regulator? | email | There are no substantial differences from a safety point of view. The TRIGA MARK II is a structure included in the University of Pavia; the TRIGA RC1 is managed by ENEA, which has undergone profound changes on the mission of the institute in recent years. In the university sector much more study and research activities that involved the reactor have been carried out, giving greater possibilities also for wider development of the management activities of the reactor. In general, the TRIGA MARK II reactor has a large utilization by external customers that require reliability helped by an AM program. ENEA, which originally had a strong mission in the nuclear field, in the last decade has shifted its scope of action on other topics, reducing the development activities in the nuclear field. This context has had an influence on the development of the activities related to TRIGA RC1, mainly after the closure of the TRADE project as the most the TRIGA RC-1 activities were coming from internal projects. Recently it was signed an agreement between ENEA and external partners that foresees the use of TRIGA RC1 for the production of radiopharmaceuticals. ENEA has decided to start a major refurbishment of the plant to allow a future intensive use.
IT-26 |  | Netherlands | Italy | 04. Concealed pipework | Ch.4 | It seems that there is no concealed pipework in the nuclear reactors described in the Italian NAR, visual inspection on all pipework can be carried out regularly. Could you please motivate inclusion of non-concealed pipework into Chapter 4 "Concealed pipework"? | email | Although concealed pipeworks are not present in the plants, considering useful having opinions and revisions in the context of the TPR, it has been considered appropriate to describe the assessment activities of the management of the existing pipeworks, even if they do not fall within the category of the "Concealed pipeworks".
IT-27 |  | Netherlands | Italy | 09. Overall assessment and general conclusions | 7.1.1 | What international codes and standards are used for the assessments of the ongoing programmes? | email | IAEA's Standards and publications, and Italian Technical Guides. See also the documents listed in attached file “LENA_references”. | The content of "LENA_referenceces" is copied in the worsheet "IT_Figs & Refs"
IT-28 |  | RPV expert group | Italy | 05. Reactor Pressure Vessels |  | Schematic drawings with the main parts could be provided for both reactor types. The drawings could be very simple describing only the basic structure. This could help to better understand the constructions of the reactors and the surrounding structures. | expert group 2 | See Vertical and Horizontal section of the reactor. in attached file “RC-1_figure ageing” See fig. 1 in attached file “LENA_references” | The content of “RC-1_figure ageing” & "LENA_references" is copied in the worsheet "IT_Figs & Refs"
IT-29 |  | RPV expert group | Italy | 05. Reactor Pressure Vessels | §5.1.4, 5.2 p47-48 | Some information could be added concerning also Triga RC-1. If there is no relevant information it could be indicated e.g. “not applicable”. | expert group 2 | Not applicable.
IT-30 |  | RPV expert group | Italy | 05. Reactor Pressure Vessels | p45-46 | It is recommended to provide some explanation for the word “graduated” in this context? | expert group 2 | We are having difficulties in answering this question because we could not find the word "graduated" in this context.
IT-31 |  | RPV expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | page 16 | How did you define essential and important SSCs in safety and protection system? Deterministic approach? Engineering judgement? | expert group 2 | The safety classification of SSC is based mainly on deterministic methods; the probabilistic method can be used when appropriate.
IT-32 |  | RPV expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | page 16 | How do you perform control test for passive component? Or what dou you mean by it? | expert group 2 | It's not so clear what is identified with "passive components" in the review. The content of the section 02 "Overall Ageing Management Programme requirements and implementation" starts with the description of the current plan for checks, procedure of surveillance and technical prescription adopted at the TRIGA RC-1 research reactor. Some features needed for implementation of the AMP are listed: 1. a precise hierarchy in management responsibility; 2. classification criteria for SSC relevant for safety; 3. methodologies for evaluating SSC status; 4. processes to ensure an increasing level of Quality Control and declared as used into the current TRIGA RC-1 management system implemented on components described in the same section (pages 16 to 18). In our interpretation passive components can be identified with components such as the reactor block or the liquid discharge system, for example, on which just visual inspections is planned. Also for these components are still valid the features listed before ( point 1 to 4 in page 16 of the NAR)
IT-33 |  | RPV expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | page 17 - 18 | The method enlisted in pages 16 to 18 can show only lost of requested function, usually not development of ageing effect before it influences required function. Are there any other method used in AMP? | expert group 2 | The controls carried out are aimed to verify the correct operation of the system. In the absence of an AMP, the plant obtains indications from the results of routine controls that can be used to verify if there are malfunctions that can be attributed to aging mechanisms in place.
IT-34 |  | RPV expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | page 21 | Which kind of enhanced surveillance program(s)? | expert group 2 | Some examples are the periodic visual inspections establish after the AMP implementation, the periodic check of the water quality in the tank, the installation of an online monitor of the hydraulic circuits.
IT-35 |  | RPV expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | page 22, fig.1 | All SCCs in Safety systems were taken as safety important of were they outscreened by some criterion? | expert group 2 | All the SSCs reported on the final SAR are considered safety systems.
IT-36 |  | RPV expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | page 23, table 6 | Why are some rowes without planned activities? There are really none? | expert group 2 | Empty rows referred to actions and scheduling enclose into the reactor surveillance programme. The rows are listed, in any case, for future discussions and eventual inclusions in the AMP.
IT-37 |  | RPV expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | page 28 | How did you use information about aging of old replaced components? (For AMP?) | expert group 2 | Information on aging of old replaced components are not directly used in the AMP but are discussed within the Plant Safety Committee. An example of such discussion is the assessment of information on the incidence of component failures in order to identify the common root of faults.
IT-38 |  | RPV expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | page 30 | Do you have a plan for further testing of Biological Shield efficiency as it was performed 10 years ago? | expert group 2 | No future actions are planned. Biological shield is checked daily in key points.
IT-39 |  | RPV expert group | Italy | 05. Reactor Pressure Vessels | page 46 | Using ultrasonic testing allowed to verify status of the components subject to the neutron irradiation. What does it mean? How? Do you mean crack initiation? | expert group 2 | The surveys carried out by ultrasonic investigation aim to identify variations into the status of the liner despite of the ageing mechanism that could be induce changes on it. So the scope of the investigation has been just to find a variation of the thickness from the declared or expected one.
IT-40 |  | RPV expert group | Italy | 05. Reactor Pressure Vessels | page 47, tab 13 | The neutron embrittlemet was identified as degradation mechanism, but only visual inspection is performed. Why? It does not seem sufficient. | expert group 2 | TRIGA MARK II is an open pool reactor with possibility to perform direct inspections. Deeper investigations on same reactor type, with same power level, reported in international meetings establish not detectable ageing affects.
IT-41 |  | RPV expert group | Italy | 05. Reactor Pressure Vessels | page 48 | Do you have a value of doses of core structure after for example 40 years of operation? Is there any operational limit? | expert group 2 | TRIGA MK II is an open pool reactor with no fixed limit for structures and with neglectable dislocations. By international experience, another degradation mechanism is identified more important in a TRIGA type reactor; the corrosion due to electrochemical effect with no controlled water quality.
IT-42 |  | Concrete containment PCPV expert group | Italy | 07. Concrete containment structures | 50 | What other parameters (in addition to radiological conditions) are being monitored for the TRIGA Mark II and TRIGA RC1 reactors in order to evaluate their potential impact with regard to ageing of the concrete structures? Have there been any cases identified in which there are differences between the design assumptions and the actual operating conditions for parameters that may affect the performance of the concrete structures? | expert group 4 | No evidences of deviations have been detected in TRIGA MARK II and in addition to radiological condition are performed only visual inspections. The same for TRIGA RC1 where no evidences of deviations have been detected and, in addition to radiological condition monitoring, visual inspections are performed daily. The other parameters being analyzed are those related to concrete structures. Differences from the design data are being verified in the frame of the planned refurbishment activities.
IT-43 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | Inspections by reg. body | The Legislative Decree no. 45/2014 establishes a new competent regulatory Authority in the field of nuclear safety and radiation protection, that is the National Inspectorate for Nuclear Safety and Radiation Protection (ISIN); according to the same Decree, until the establishment process of ISIN will be completed, the functions of competent regulatory authority continue to be carried out by ISPRA, through the National Centre for Nuclear Safety and Radiation Protection. Which one of the authorities gives the license and which one performs the majority of inspections and controls required for granting the license?: | expert group 3 on other topics / expert group 1 | The regulatory body in Italy is a system made up of the licensing body (Ministry of Economic Development- MISE) and the NRA. To date, the NRA functions are carried out by the National centre for nuclear Safety and radiation Protection of ISPRA; when the establishment process of ISIN will be completed, the competences currently in charge of ISPRA will pass to ISIN. The granting of operating licences is issued by the MISE on the basis of the binding opinion expressed by ISPRA (in the future by ISIN) which, by law, cannot be changed by the MISE. The inspections and controls are carried out by ISPRA (in the future by ISIN).
IT-44 |  | Cables expert group | Italy | 03. Electrical cables | 27 | The cables are checked by visual inspections, semi annually. Is this enough to determine the status (integrity) of the cables for TRIGA Mark 2 reactor? | expert group 3 | The periodicity of these tests is defined by the Technical Specifications. Yes, it has been evaluated that is enough for the complexity of the plant and furthermore cables are also checked within the systems operability.
IT-45 |  | Cables expert group | Italy | 03. Electrical cables | 30 | TRIGA Mark 2 the cables / electrical distribution system is not safety related. It this stipulated in the design basis of the reactor? | expert group 3 | It is evaluated in a dedicated reference " ANALYSIS OF THE IMPLICATIONS RELATED TO THE LOSS OF THE POWER SUPPLY NETWORK OF THE PLANT L.E.N.A"
IT-46 |  | Cables expert group | Italy | 03. Electrical cables | n/a | At Triga Mark II where there any cables determined to be subject to overheating due to high intensity current? | expert group 3 | There aren't any cables subject to overheating. All cables are correctly dimensioned and there aren't cables overcharged. All are standard power supply distribution cables.
IT-47 |  | Cables expert group | Italy | 03. Electrical cables | n/a | Were there any cables with paper insulation cables installed at Triga Mark II, which (would) need to be replaced? | expert group 3 | There weren't any cables with paper insulation installed at TRIGA MARK II.
IT-48 |  | Cables expert group | Italy | 03. Electrical cables | 37/Table 8 | What kind of functional and instrumental tests are performed on and what is the frequency of inspections performed by the licensee of the TRIGA RC-1 ? | expert group 3 | 1. Each chain is subject to functional tests; the instrumental test is intended as a measure of the values, for example of current or voltage, in prefixed points. 2. As mentioned in the Report, a formal AMP is not implemented at TRIGA RC-1 research reactor. A large refurbishment programme has to be implemented during the current year; following which the licensee will present a formal proposal to the NRA. Table 8 of the Report summarizes a licensee first proposal of an ageing evaluation program for electrical cables and electronic, timing and frequency for inspection will be proposed later.
IT-49 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation |  | It is not clear what is meant by the continuous review of the safety by the Plant Committee. All documents elaborated by the Plant Safety Committee are approved or reviewed by the Regulatory Body? | expert group 3 on other topics / expert group 1 | The Plant Safety Committee has advisory functions for the plant manager. The NRA (currently ISPRA) approves the composition of the Committee. NRA does not approve the documents produced because, as previously mentioned, this Committee has only an advisory role for the plant manager. The law provides that an expert from the NRA can participate in the meetings of the Committee.
IT-50 |  | General AMP expert group | Italy | 01. General information | 6 | Related to the works performed at the reactor TRIGA RC- 1, after the modifications, was performed any commissioning of the modifications? The results of the tests are not specified. (Are they OK?). The new equipment have all necessary qualifications? | expert group 3 on other topics / expert group 1 | In relation to the changes for the increase in power, the plant has undergone a new authorization procedure. With regard to plant modifications, the legal provisions require that any change to the Safety Analysis Report (SAR) is subject to the same authorization procedure as a new plant. In relation to the refurbishment activities scheduled for the second half of this year, if these activities involve changes to what is described in the SAR, they will be subject to the procedure described above. In any case, the licensee must notify the activities it intends to carry out to the NRA, who has the right to decide if and how to intervene, even at the authorization level.
IT-51 |  | General AMP expert group | Italy | 01. General information | 6 | It is of interest to know if the seismic qualifications are made up to what design basis earthquake (to be speci-fied the peak ground acceleration of the DBE). Also, it would be useful to specify of the building has enough robustness, considering there are some cracks. | expert group 3 on other topics / expert group 1 | As far as concern RC-1 plant, the information about seismic analysis is included in the SAR and also part of the Technical Specification for the external emergency. The seismic analysis carried out aimed mainly to verify the impact of a possible earthquake on the possibility of turning off the reactor. The design basis earthquake (DBE) considered corresponds to a maximum acceleration equal to 0.981 cm/s2. The implementation of the AMP will include a re-evaluation of the building response to the DBE and also an update of this one due to the earthquake events of the last 9 years in the zone close to Rome. Specific chapters of the TRIGA MARK II SAR are dedicated at the seismic assessment based on the National Institute of Geophysics reports. The building and the Reactor structure was built in compliance with the National regulations. After the revaluation of the seismic map of Italy, by the National Institute of Geophysics, a building revaluation was done in 2016 (peak ground acceleration 0.1g). No cracks are present in the building or Reactor structure at the LENA.
IT-52 |  | General AMP expert group | Italy | 01. General information | 6 | The contractor who will be used (or have been used, because the works have been initiated some years ago), for the control room refurbishments, have been some-how authorized or qualified by the regulatory body? | expert group 3 on other topics / expert group 1 | The responsibility for the execution of the works is in any case of the operator. The NRA approves the specifications and the project. When the operator makes use of external contractor, NRA has the right to carry out controls and inspections to verify compliance with the approved project.
IT-53 |  | General AMP expert group | Italy | 01. General information | 6 | For the reactor TRIGA Mark II (Pavia), it is implemented a management system as per ISO 9001 standard, and not according to IAEA standard GSR Part 2. The Aging Management Program is in place also according to ISO 9001. Does the manage-ment system covers also the areas related to safety culture and leadership? | expert group 3 on other topics / expert group 1 | ISO 9001 cover all aspect of GSR Part 2 and is possible to receive an external audit and certification
IT-54 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | 16 | Among the features of the Aging Management Program of the RC - 1, it is not specified beside all these features if the program has enough resources, human and material, to cover all areas. | expert group 3 on other topics / expert group 1 | At present no formal AMP is in place. After refurbishment program foreseen in the second half of the current year an AMP will be established also taking into account the resources, human and material, to cover all areas.
IT-55 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | 18 | In the table 3, there is specified the periodicity of some tests. It is assumed the frequency of these tests is based on experience and good practices at international level. Perhaps these practices have to be documented, or the reference to be indicated. | expert group 3 on other topics / expert group 1 | The periodicity of these tests is defined by Technical Specifications.
IT-56 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | 21 | it is not specified how it is performed the control the supply chain, as it is mentioned in this las paragraph. | expert group 3 on other topics / expert group 1 | A written procedures in compliance with ISO 9001 (control of purchases) is in place.
IT-57 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | 21 | It is specified that the metrological controls are made according the ISO standards. Are there any national or EU standards more stringent than the ISO standards, for this specific field? | expert group 3 on other topics / expert group 1 | ISO 10012 measurement management system is used as guideline.
IT-58 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | 22 | At page 22, is mentioned that the life (lifetime duration) of the LENA reactor (Pavia) was extended. It is not specified with what duration was extended this life period. | expert group 3 on other topics / expert group 1 | The extended life of the plant is not intended as an extension of the duration of the license, as the latter does not have a predefined duration. Since for ageing problems each physical structure has a limited duration in time, the term should be understood as maintenance and updating of systems and components in order to maintain the safe management of the plant.
IT-59 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | 24 | It is mentioned that checks were performed at the liner of the RC - 1 reactor. It is of interest to know if these inspections were performed with the fuel in the reactor, or the reactor was de - fueled. Were special tools used? | expert group 3 on other topics / expert group 1 | The reactor was de-fuelled, everything inside the liner was removed and the inspection was made by camera.
IT-60 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | 33 | It is stated that the overall training process was improved to the best practices. Is this program made according to SAT (systematic approach to training)? | expert group 3 on other topics / expert group 1 | The TRIGA MARK II has developed specific procedures that consider the systematic approach to training.
IT-61 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | All | The overall impression is that the degree of detail for the report related to the TRIGA Mark II reactor is much detailed than the one for the RC - 1 reactor. Is there any reason for this? | expert group 3 on other topics / expert group 1 | The TRIGA MARK II is a structure included in the University of Pavia; the TRIGA RC1 is managed by ENEA, which has undergone profound changes on the mission of the institute in recent years. In the university sector much more study and research activities that involved the reactor have been carried out, giving greater possibilities also for wider development of the management activities of the reactor. In general, the TRIGA MARK II reactor has a large utilization by external customers that require reliability helped by an AM program. ENEA, which originally had a strong mission in the nuclear field, in the last decade has shifted its scope of action on other issues, reducing the development activities in the nuclear field. This context has had an influence on the development of the activities related to TRIGA RC1, mainly after the closure of the TRADE project as the most the TRIGA RC-1 activities were coming from internal projects. Recently it was signed an agreement between ENEA and external partners that foresees the use of TRIGA RC1 for the production of radiopharmaceuticals. ENEA has decided to start a major refurbishment of the plant to allow an intensive use.
IT-62 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | 30 | The overall fire risk was reduced (lowered) but not completely eliminated. Is it any fire risk present? | expert group 3 on other topics / expert group 1 | The risk, by standard definition, could not be completely eliminated. All actions in order to reduce the fire load were taken and active countermeasures are in place. LENA complies with all applicable fire safety standards as required by the national legislation.
IT-63 |  | General AMP expert group | Italy | 02. Overall Ageing Management Programme requirements and implementation | N/A | Was the root casue determined for the increased number of trips at the TRIGA Mark II reactor in 2016 ? Was it due to decreasing reliability of the components (I&C components)? | expert group 3 on other topics / expert group 1 | The conclusion was the obsolescence of log channel that have been substituted according to the evaluations discussed in Plant Safety Committee
IT-64 |  | EC | Italy | 02. Overall Ageing Management Programme requirements and implementation | 34 | Section 2.5: TRIGA RC1: No information. AMP to be established after refurbishment. LENA TRIGA: No details provided on licensee experience on AMP. The text refers generically to the IMS in place. Could you provide details on the licensees experience on the adequacy of its overall AMP? |  | Experience was reported in several technical publications and presented at international meetings such are as e.g.: Technical Reports Series No. 482 - History, Development and Future of TRIGA Research Reactors. Operational experience on Ageing Management at the TRIGA MARK II research reactor of LENA (Laboratory of Applied Nuclear Energy) - University of Pavia (Italy); full paper published as proceeding of the International Group on Research Reactors (IGORR) & IAEA Technical Meeting DCC, Daejeon Korea 13 – 18 October 2013. Implementation an ageing management program at the TRIGA reactor of University of Pavia University of Pavia - Italy (Laboratory of Applied Nuclear Energy) - University of Pavia (Italy)T3-TM-54962: Technical Meeting on Research Reactor Ageing Management, Refurbishment and Modernization - 30 Oct – 03 Nov, 2017; M6, M Building, VIC, Vienna, Austria, proceeding published. At present no formal AMP is in place at TRIGA RC-1. After the refurbishment program foreseen in the second half of the current year an AMP will be established.
IT-65 |  | EC | Italy | 02. Overall Ageing Management Programme requirements and implementation | 35 | Section 2.7: The NAR includes no statement from the regulator on the adequacy of the licensee’s overall ageing management programme and no strengths and weaknesses are identified. This is justified for TRIGA RC1 as no AMP is in place. For the LENA TRIGA, it is indicated that a comparison of the AMP with the IAEA SSG-10 guidelines was performed and implementation of adjustments are monitored by ISPRA. Could you provide details of this analysis in terms of strengths/weaknesses and overall assessment? |  | A comparison between the AMP and the IAEA SSG-10 guidelines is an internal activity of the licensee. There was no formal approval of the AMP. The NRA's duty is to verify the conformity of the results obtained from the application of the AMP to the safety requirements established in the authorization to the operations. The NRA has the power to provide further requirements if the results of the inspections are inadequate compared to the authorizations given. It is up to the NRA to request and demand that the license submit its program for prior authorization.
IT-66 |  | EC | Italy | 02. Overall Ageing Management Programme requirements and implementation | 10-14 | Section 2.1 does not mention any specific requirements or guidance relevant to the AMP. Does the existing regulatory framework foresee the implementation of an AMP? If so, could you specify where and how (e.g. is the AMP taken into account in the licensing basis documents referred to in the NAR?) |  | At present there are no requirements specifically addressed to the problems of ageing. In the recent past, provisions have been made for the implementation of a systematic Periodic Safety Review In which specific aspects related to ageing are also envisaged.
IT-67 |  | EC | Italy | 02. Overall Ageing Management Programme requirements and implementation | 15-22 | Section 2.3.1: TRIGA RC1: the NAR does no reference the methodology for evaluation of the existing maintenance practices, nor for the collection, storage and evaluation of maintenance data. Could you specify how these aspect are taken into consideration? Do they figure in the reactor's management system and, if so, could you specify how? |  | With regard to the collection of data relating to maintenance activities, the plants are required to have specific registers on which are reported both the maintenance activities, and the timing and results of the aforementioned activities. The plants are therefore able to verify both the effectiveness of existing procedures and the presence of trend variations. Relative to TRIGA RC1, since it has not yet implemented a formalized AMP, the assessments are not made in a systematic way but only in the presence of trend variations.
IT-68 |  | EC | Italy | 02. Overall Ageing Management Programme requirements and implementation | 22-24 | Section 2.3.2: TRIGA RC1: A formal AMP is not in place. The NAR mentions that a prolonged shutdown period for maintenance and upgrading will start in the coming months, following which a formalized AMP will be established. It would have been interesting to know to which extent age management was considered in the choice of SSCs that will be maintained or upgraded during this future intervention. LENA TRIGA: Could you provide some more detailed information on standards and acceptance criteria? |  | The General Information section of the NAR, in the frame regarding TRIGA RC-1, listed the main interventions that will be executed during reactor shutdown. In particular, seismic resistance verification, infrastructure-related activities, fire protection compartments and control room console renewal are all based on AM criteria. The acceptance criteria are defined in the surveillance program; the others are discussed in the Plant Safety Committee following the list n. 1 of reference attached.
IT-69 |  | EC | Italy | 02. Overall Ageing Management Programme requirements and implementation | 25-28 | Section 2.3.3: TRIGA RC1: No information on inspection or monitoring program, apart from an experience (TRADE) in 2000 on the status of the reactor vessel. Please can you confirm that no other monitoring, testing, sampling and inspection activities to assess ageing effects to identify unexpected behaviour or degradation during service have been implemented at TRIGA RC1 since 2000. |  | Apart from the instrumental verifications during the TRADE experiments, visual inspections of the reactor block and in particular of the reactor vessel are performed every day (twice a day, at the beginning of the day and in evening) as a part of the surveillance procedure for the plant. So the status of the vessel is monitored continuously. The AMP will include also deep inspection by means of endoscope and dedicated cameras.As indicated in the report ISPRA has requested the Licensee the conduct of the first inspection activities identified in the Ageing Management Programme for Electrical Cables, Hydraulic Circuit and Container in connection with the envisaged prolonged shutdown phase in 2018 finalized to implement planned extraordinary management interventions and upgrading measures.
IT-70 |  | EC | Italy | 02. Overall Ageing Management Programme requirements and implementation | 29-33 | Section 2.3.4: The NAR provides an exhaustive list of major maintenance interventions, though it is not always clear whether they were preventive or corrective maintenance interventions, i.e., if they were the result of a program or plan. Could you specify, both for TRIGA RC1 and LENA TRIGA, the motivation for the interventions listed? |  | Considering the ageing of safety related components many interventions have been done during last years such as, for example the environmental monitoring system replacement, the installation of a data storage manager for signals from all monitoring systems, the structural verification on the core components (instrumental inspection previous to the TRADE experiments), the replacement of the logarithmic amplifier and of the temperature indicators, the fuel temperature indicators, the substitution of the demineralization plant and, at last, the replacement of the secondary console. The full list can be found at page 29 of the NAR. Systems and components substitutions have been decided in order to avoid future unavailability or fault of instrumentation important to safety. All the activities listed for TRIGA MARK II are preventive actions approved by Plant Safety Committee.
IT-71 |  | EC | Italy | 02. Overall Ageing Management Programme requirements and implementation | 33-34 | Section 2.4: TRIGA RC1: No information. AMP to be established after refurbishment. |  | The PSRs and examinations on the conservation of the plant performed every five year show all preventive interventions that have been implemented during last 20 years. All this knowledge and experience on ageing of components will be used to define the future AMP.
IT-72 |  | EC | Italy | 03. Electrical cables | 38 | The table 8 / the footnote refers to Annex 2 for ageing mechanisms and replacement criteria, but Annex 2 does not provide such information. Are the ageing mechanism numbers referring to those under 03.1.2 on p. 37? |  | It's an editing mismatch. The correct reference is to Annex 1.
IT-73 |  | EC | Italy | 03. Electrical cables | 39 | In table 9, are the ageing mechanism numbers referring to those under 03.1.2 on p. 37? |  | It's an editing mismatch. The correct reference is to Annex 1.
IT-74 |  | EC | Italy | 03. Electrical cables | Generic 36-41 | The report lacks a clear description of cable inspection and testing activities, including the frequencies and acceptance criteria. Further, The NAR should list the groups of electrical cables included within the AM. Such list cannot be found, although TRIGA MARK II has implemented an AMP. |  | These activities and list of cables and systems are described in the surveillance programme and not in the AMP. In any case, anyway the AMP groups the cables as listed in the report. In general, cables are checked by resistance measures and the systems by operability test. As far as concern TRIGA RC-1 an AMP will be implemented soon: it will report a clear description of cable inspection and testing activities, including the frequencies and acceptance criteria.As indicated in the report ISPRA has requested the Licensee the conduct of the first inspection activities identified in the Ageing Management Programme for Electrical Cables, Hydraulic Circuit and Container in connection with the envisaged prolonged shutdown phase in 2018 finalized to implement planned extraordinary management interventions and upgrading measures.
IT-75 |  | EC | Italy | 05. Reactor Pressure Vessels | Chapter 05.1.1, page 46 | In page 46 it is mentioned: "As already mentioned in section 2.3.3, these surveys, carried out using ultrasonic techniques, have allowed to verify the status of components subject to particular ageing agents such as neutron and gamma irradiation as well as corrosion phenomena.". Comment: It is not possible to determine the degradation caused by neutron and gamma irradiation using ultrasonic inspection. The UT inspection can only detect defects present in the vessel that may be affected by neutron & gamma embrittlement in greater or less extend. It is needed to irradiate samples representative of the vessel materials to determine the level of irradiation embrittlement. |  | The surveys carried out in TRIGA RC-1 by ultrasonic investigation aimed to identify variations in the status of the liner despite of the ageing mechanism that could have induced changes on it. The scope of the investigation has therefore been just to find a variation of the thickness from the design value.
IT-76 |  | EC | Italy | 05. Reactor Pressure Vessels | Chapter 05.3, page 48 | In page 48 it is mentioned: "For TRIGA RC-1 Reactor in 2000 the status of reactor vessel has been tested to evaluate its integrity and to identify possible ageing phenomena. These surveys, carried out using ultrasonic techniques, have allowed to verify the status of components subject to particular ageing agents such as neutron and gamma irradiation as well as corrosion phenomena.". Comment: It is not possible to determine the degradation caused by neutron and gamma irradiation using ultrasonic inspection. The UT inspection can only detect defects present in the vessel that may be affected by neutron & gamma embrittlement in greater or less extend. It is needed to irradiate samples representative of the vessel materials to determine the level of irradiation embrittlement. |  | The surveys carried out in TRIGA RC-1 by ultrasonic investigation aimed to identify variations into the status of the liner despite of the ageing mechanism that could have induced changes on it. So the scope of the investigation has been just to find a variation of the thickness from the design value.
NL-1 |  | Poland | Netherlands | 03. Electrical cables | 100 | What is licensees experience with using the tool AUREST especially related to analysis and calculations of the end of safe life of cables? | Website | The tool AUREST is very useful to: 1. select the components (including cables) which are during LOCA/HELB situations in a harsh environment; 2. check if every component qualification fulfills the LOCA resistance requirements; 3. calculate the remaining radiological and thermal qualified life of every single component and 4: present the results in a clear overview (page 72, figure 13). The licensees experience with AUREST is positive. AUREST is specifically meant for components, including cables, with a LOCA resistance requirment (harsh environment).
NL-2 |  | Norway | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 43 / 130 | "In case of findings not fulfilling the acceptance criteria, at least a condition assessment has to be performed......" -Does these findings cover all SSCs? "…Further operation with or without repair has to be justified in a written document and approved by the regulator." -What is the regulator acceptance criteria for further operation with or without repair? | Website | EZP (NPP): This part is related to the ISI-programme. The ISI programme is limited to safety classified mechanical structures and components. ANVS: A. Yes, the condition assessment is applicable to all SSCs not fulfilling the acceptance citeria. B. For further operation of an SSC (repaired or not) its condition has to be assessed. For situations where acceptance criteria are clear these are used. In other cases the acceptance criteria with or without additional requirements will be determined by the regulator.
NL-3 |  | Bulgaria | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | chapter 2 | Do you use safety performance indicators for overall ageing management program effectiveness assessment? If yes, could you please describe the system and relevant indicators you are using? | Website | EPZ (NPP): So far we don’t use safety performance indicators (PIs) for overall ageing management program effectiveness assessment. For specific ageing managemement programs we have specific PIs like number of load cycles, usage factor (fatigue) and RTNDT (RPV embrittlement). RID (HOR): There are no safety performance indicators defined to asses the effectiveness of the overall ageing management program. Effectiveness is evaluated on the functional level of an SSC in Plan-Do-Check-Act cycles, based on the RCM methodology. Safety in such cycles is of course the main driver, but also optimised operational times and cost effectiveness is evaluated. NRG (HFR): NRG does not have an explicit SPI dedicated to AM program effectiveness. The AM is an included parameter of the monitored SPIs.
NL-4 |  | Bulgaria | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | p. 59 | The report states that there is an inspection plan for all nuclear installations and ageing management is one of the areas of inspection. Could you please provide more information on what specific inspections on NPP Borssele were fulfilled, their scope, what is inspected in the framework of inspections, main results and if there is any significant findings from the inspections? | Website | Referring to section 2.6 part a, we have explained that the oversight efforts for the NPP in the past few years and some more years to come, were/will be focussed on the implementation of the LTO programme and related licence conditions. In parallel we have invited IAEA SALTO missions in the period 2009-2014. The reports of the SALTO missions have been published and part of the information can also be found in recent CNS-reports. Furthermore we have stated that currently we are starting to develop a new AM/LTO inpsection programme.
NL-5 |  | Bulgaria | Netherlands | 09. Overall assessment and general conclusions | p. 146 | In the report is mentioned that the ANVS will develop a new approach for inspection the AMP, after the completion of the LTO related activities. Is this approach already defined? If yes, could you please present the used concept in more details? | Website | No this is not available yet. Up to 2019 the current inspection programme including additional LTO inspections will be carried out, meanwhile it is in the process of being evaluated. The new approach will be implemented with the new inspection period 2020-2029 (see also answer on Q71). | The reference refers to the line # 71 in the NL response table i.e. question NL-4
NL-6 |  | United Kingdom | Netherlands | 07. Concrete containment structures | 140 | In Section 7.1.4 a description is given regarding the visual inspection of the concrete structures. One of the main subjects of the visual inspection is given as “assessment of the reinforcement”. Please confirm how this is carried out and what the criteria are for taking action? | Website | It is correct that direct visual inspection on the reinforcement is only performed when it is exposed. Inspection of reinforcement that is not exposed rather focuses on damage on the concrete surface, which could result in cracks or exposed reinforcement bars. This is a preliminary inspection, defects are measured, described and upon comparison with acceptance criteria as well as engineering judgment, further investigation is performed. No preventive core drilling is performed by the NPP.
NL-7 |  | United Kingdom | Netherlands | 07. Concrete containment structures | 144 | In Section 7.2 the licensee describes a successful application of the ageing management programme in relation to the replacement of the outside cover of the reactor annulus building due to degradation from chloride ingress. It is not clear whether any additional protection was applied to prevent a recurrence of the problem. Please confirm whether a protective coating was applied to the replacement concrete or whether consideration was given to this. | Website | Yes, the cover of the rebar was repaired to its original condition. On top of the repair, an additional layer of concrete was applied and finally the concrete was protected by the application of a protective coating.
NL-8 |  | United Kingdom | Netherlands | 04. Concealed pipework | 109 | Section 4.1.3.1., table 9 describes the inspection programme for the Bonna-piping at NPP Borsele. Please give an indication of how much of the pipework is inspected during the 3 yearly intervals , how representative these inspections are of the SSC and whether the inspections are speculative or targeted using a risk based approach. | Website | The full length of the Bonna piping is visually examined, using a robotic camera.
NL-9 |  | United Kingdom | Netherlands | 04. Concealed pipework | 110 | Section 4.1.3.1, 'Settlement of cooling water lines VF' - Please provide further information about how the level of the lines is physically measured every 5 years and any further operational experience of where this has been used successfully to identify movement of buried pipework. | Website | Settlement of the VF cooling water lines takes place by measurement of the pipe level at dedicated points (e.g., manholes, monitoring wells, connecting points, etc.), using a leveling instrument. Results are compared with dedicated reference points. These measurements are performed by a qualified third party. For connecting points, acceptance criteria are defined, while the measurements of the pipe in the field are mainly used for trending purposes and to complement any findings of the visual inspection of the inside of the pipes. This is only applicable to the NPP's Bonna piping. No further concealed pipework is inspected using this method.
NL-10 |  | United Kingdom | Netherlands | 04. Concealed pipework | 115 | Flushing would clear contaminants from the pipe internals but would do little to prevent ageing from external types of degradation. Please explain how flushing prevents ageing? | Website | The question refers to the regulator's assessment, where it is stated that ageing prevention of VE is also controlled by regular flushing during periodic testing. Regular flushing would in general prevent ageing by microbiological induced corrosion and by removal of contaminants from inside the pipes. It does not prevent ageing from external types of degradation. However, it is stated in the licencee's text that no relevant ageing mechanisms are applicable to the external surfaces of the backup residual heat removal water cooling system (VE), where this text refers to.
NL-11 |  | Slovenia | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 58 | Regulatory oversight process (Page 58): What kind of requirements did ANVS have regarding Ageing management programs (AMPs) implementation status before the LTO started in 2014. Should all new or modified maintenance programs have been implemented by that time or only systematic phase of AMP should have been established. Did ANVS carry out special inspections or audits dedicated to AMP during licensing procedure for LTO? How is implementation of AMP programs monitored by ANVS during LTO? | Website | The implementation and development of the AMP was a licence requirement with specific deadlines before 2014 for the implementation of most activities, and deadlines up to 2020 for a number of activities - all described in the licence. Up to now NPP Borssele has met the deadlines. The regulatory assessments and inspections during the licensing phase and the implementation of LTO have been described on p.58/59. Also refer to our answers to questions 71 & 72. | The reference refers to the line # 71 and 72 in the NL response table i.e. questions NL-4 & NL-5
NL-12 |  | Slovenia | Netherlands | 07. Concrete containment structures | 142 | Monitoring, testing, sampling and inspection activities for concrete structures (Page 142): Is sampling of concrete material being performed only for damage assessment, or has been sampling and further testing performed also to assess condition of concrete of safety related buildings during plant normal operating lifetime or is planned for LTO? | Website | The sampling of the concrete as described in this section is part of the further assessment of damage and hidden defects in concrete structures, which is conducted after damage is detected during the normal civil maintenance inspections. This was performed as part of the preparation for LTO, which the plant entered in 2014. The normal civil maintenance programme is considered effective for managing ageing during LTO.
NL-13 |  | United Kingdom | Netherlands | 04. Concealed pipework | 113 | Section 4.1.4.1 (and the previous sections) place a lot of emphasis on the suitability of the design to manage any potential degradation mechanisms. As the plants age, are there any concerns that the monitoring/inspection activities will need to change to confirm the ongoing condition of the pipework? Will the need for this be driven by any failures or adverse findings from the current inspection programme? | Website | During preparation for LTO, the NPP conducted an exhaustive review of its ageing management. Any known degradation mechanism for in-scope mechanical, electrical and civil structures and components was evaluated against environmental and operational conditions and existing ageing management activities in cooperation with the Original Equipment Manufacturer (OEM). Additional activities were identified, if considered necessary. There were no concerns about the programmes to confirm ongoing condition of the pipework. This conclusion was substantiated when a large part of the concealed piping was replaced due to the conceptual ageing of the separation concept, which was identified during the PSR.
NL-14 |  | United Kingdom | Netherlands | 07. Concrete containment structures | General | There is no discussion on irradiation effect on the reinforced concrete secondary containment. How are these effects assessed and the long term integrity of the structure validated? Please provide more information on the ageing mechanisms and strategy for irradiation of the concrete containment. | Website | No irradiation effects were considered for ageing of the reactor annulus building, which is outside the primary containment of the NPP and largely outside of the nuclear radiation environment.
NL-15 |  | United Kingdom | Netherlands | 07. Concrete containment structures | 138 | Section 7.1.3 Ageing management of indoor concrete building walls, including specific requirements. Concrete walls experience specific deterioration and are visually examined for cracks. Their coating is to remain compliant with their requirements. Please provide more details of the safety claims made on the surface coatings and the constituent properties of the coating material. What are the acceptance limits for the coating? | Website | The section on the ageing management of indoor concrete building walls provides details of specific safety claims for the coating (i.e., fire resistance, impermeability to fluids, chemical resistance, LOCA resistance, ease of decontamination, seismic resistance, radiation protection, internal flood resistance, external flood resistance, gas tightness and other specific requirements) with their acceptance criteria (e.g., Fluid resistant wall coatings must be fluid-tight and are checked to be undamaged; Chemical resistant walls and their coatings are checked regarding any attack and their full integrity. Slight discolouration is acceptable whereas blistering, separation, softening etc. are not acceptable. Signs of saponification are checked in this inspection but not considered as a significant ageing mechanism; LOCA resistant coating has to be intact and without any damages, and the strength of its bond may not have reduced; etc.). Acceptance criteria for the bond strength are according to ASTM D 3359A.
NL-16 |  | Switzerland | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 23, 54 | According to chapter 2.3.1.1 active SSCs are not part of the ageing management process in NPP Borsele. Instead ageing of active SSCs is managed by preventive maintenance and/or surveillance programs. Do you think that this restricted approach is in line with the overall goal of AMP (see chapter 2.5) to develope from the classic approach to an integral SSC oriented ageing management process? | Website | We don't see a restricted approach here. Based on internal and external experiences it became clear that for passive SSCs like vessels, piping etc. a more coordinated approach is necessary to ensure adequate ageing management. Therefore (extra) coordination is introduced with this ageing manangement process. For active components the ageing management is taken care of by preventive maintenance and surveillance programmes (like periodic testing). These programmes themselves are coordinated too. In case of active components the focus is mostly to (frequently) detect fulfilling of active safety functions while for passive components the focus is on managing potential degradation mechanisms which can compromise the passive safety function integrity. For active components the classic approach is suitable we think while for the passive components more coordination is needed.
NL-17 |  | Switzerland | Netherlands | 03. Electrical cables | 19 | Textline12: Is there any AMP for active electrical components (motors, valves, sensors, etc.)? | Website | Since the commission of the plant active components are part of the preventive maintenance programme. Measures to maintain active components, analysis of results, improvements in the preventive program, etc., are part of this maintenance proces. Specific AMP's are developed for passive components.
NL-18 |  | Switzerland | Netherlands | 03. Electrical cables | 86 | Textline7-(step9): Why are the development and effects of water trees not measurable? E.g. with partial discharge measurement? | Website | At the time of the LTOB-AMR there was no reliable measuring method known to detect water trees in medium voltage cables. To derive water trees out of partial discharges seems not to be possible. Partial discharges may exist short before break down. However nowadays Dielectric Spectroscopy measurement is available as a reliable diagnostic method to detect water trees. At the Borssele plant these measurements were conducted on 6000 V cables in 2017 for the first time (see page 93).
NL-19 |  | Switzerland | Netherlands | 04. Concealed pipework | 103, 107 | According to chapter 4.1.2 (Table 8) the UJ-system consists partly of steel piping. Why are no visual inspections carried out (likewise in the VF-system) although the steel piping may be (potentially) affected by general corrosion (see Table 8)? | Website | The diameter of the steel UJ-lines does not accomodate the application of the robotic camera, used for inspection of VF. Besides this, the trending of the periods of running of the jockey pump in the UJ system to monitor any leakage, and monthly functional testing is considered sufficient for the ageing management of this system.
NL-20 |  | Czech Republic | Netherlands | 03. Electrical cables | 73 | "…will use of a cable deposit, which is located at the main coolant line in a German PWR NPP." The cables in German deposit are the same as in Borssele? | Website | "… with use of a cable deposit…" A part of the cabletypes in the cable deposit, available as test specimen, are used in Borssele as well. Qualification data of these cabletypes are part of AUREST and are used in the qualified life calculations.
NL-21 |  | Czech Republic | Netherlands | 03. Electrical cables | 76 | "in this step, the technical data of relevant materials is investigated…", "…for each material a conservative long term temperature and radiation dose is determined"….."Along term temperature of PP material of 100 °C". 3.1.2.1.2 and Fig.17 It seems that the literature data are used. What does it mean Long term, Is it 20 000 hours or 60 years. E.g. 60 years for PP (polypropylene) at 100 °C and 50 kGy seems to me too long. Are these results from experiments on cables or data from literature on material? | Website | In general, for all the insulation materials used, literature and available experience data is used to determine values for temperature (60 years) and cumulative radiological load. This action was fulfilled by a dedicated company, as a step in the LTOB_AMR, and the results are reviewed by both the licensee and the government. Figure 17 is just meant as an example (for PP a temperature of 60 °C is used in the assessment)
NL-22 |  | Czech Republic | Netherlands | 03. Electrical cables | 92 | "In the calculation model the safe end of life is based on certain maximum allowable degradation. For the insulation material XLPE 80% is chosen, for PVC this is 90 %." (chapter 3.1.3.1) What does it mean? Degradation - decrease of mechanical properties or change of electrical properties? Page 95 says....""in which the elongation at break of 0.5 is checked by winding around own diameter"". Bending is common method to test if 50 % EtB absolute is reached. How does it correspond with 80 % or 90 % degradation." | Website | In the calculation model for medium voltage cables, the degradation rate is based on elongation at break values of test specimens out of cable insulation. In this case 80%/90% is a margin related to the density of the model and the insulation material. On page 95 a (simple) bending test of spreader room wiring is described, which gives information about the brittleness of the insulation: over 50% absolute elongation or not.
NL-23 |  | Czech Republic | Netherlands | 03. Electrical cables | 90 | "…The maximum ambient temperature as specified for the applied type of coaxial cable is 85⁰C. So well within the normal operating environment. In the specification, it is also stated that the MM10/75 cable can withstand at least 7 days of 100⁰…" (3.1.2.3) Maybe it is OK, but did you tested it? Coaxials are often made of pure PE, which can melt at temperature around 100 °C. | Website | MM10/75 cables are high temperature tested in accordance with BS 2316, clause 6.3.1. No further test are executed by RID.
NL-24 |  | Bulgaria | Netherlands | 05. Reactor Pressure Vessels | p.119 | Would you please clarify whether the thermal ageing was considered as well as possible ageing mechanism? | Website | Thermal ageing was in the ageing management review considered as a potential ageing mechanism for the RPV. Particularly based on the specific material constituents (for instance Cu content in the beltline weld and delta-ferrite in the austenitic cladding) in the subcomponents of the RPV, thermal ageing was in the outcome classified as an insignificant ageing mechanism for the RPV of NPP Borssele.
NL-25 |  | Finland | Netherlands | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Website | Both irradiation embrittlement and fatigue do not give big safety and operation challenges for the RPV. For all the other (corrosion-related) potential ageing mechanisms the challenge is to keep the primary water in the good conditon and avoid leakages to avoid borid acid corrosion on the outside of the RPV. In this also safe shutdown conditions are considered.
NL-26 |  | Czech Republic | Netherlands | 03. Electrical cables | 70 | "As long as the jacket is not damaged, ageing degradation is not considered as highly essential for the function of cable". Where this statement comes from - testing or experience? It cannot be generally stated. I know many examples where jacket was OK, but insulation was totally degraded. | Website | This statement is meant for ageing degradation of the cable jacket alone, not for the insulation of cable cores.
NL-27 |  | Czech Republic | Netherlands | 03. Electrical cables | 79 | "….in some cases hot spots in the specific room". (fig. 18) Design temperature is 50 °C and in many positions is more as mentioned in Fig. 18. How the cables are treated in such hot spots? Something is mentioned on page 81 but without details. | Website | See figure 22 for specific temperature areas, all the rooms with hotspots (> 50°C) are known. For use in the assessment measured values were used or, if not available, a margin was added (page 81) on the design value. Cables in these hot spot areas are treated with respect to this environmental temperature.
NL-28 |  | Czech Republic | Netherlands | 03. Electrical cables | 84 | Figure 24 mentions values of thermal endurance for different materials and should cover 60 years. It seems it comes from literature data. Polymer life time depends on stabilizers, on production, pigments etc. It is not possible to use data for life time assessment. What is criterion of end of life for materials in Fig. 24? | Website | For cables with LOCA requirements a dedicated ongoing qualification program with use of a deposit and end of life criteria based on elongation at break is used. For the rest of the cables the design temperature and design radiological dosis of the materials were used as a step in the LTOB-AMR to detect cables which may be in adverse environment. This step was not meant as a safe end of life assessment.
NL-29 |  | Czech Republic | Netherlands | 03. Electrical cables | 84, 85 | Figures 24 and 25 show thermal endurance and radiation stability of materials. But both stressors act simultaneously. | Website | Statement is correct. If the environmental conditions of a cable includes a high temperature and a strong radiation field this should be taken into account in AM of these cables.
NL-30 |  | Slovenia | Netherlands | 03. Electrical cables | 70 | Section 3.1.2 (page 70). Why does not the report consider R&D programmes, objectives, contents, internal and external operating experience? | Website | In chapter 3.1.2.1 (page 70) the ageing assessment of electrical cables for Borssele is described. Applicable operating experience, R&D results, etc, are taken into account in the ageing management (see Figure 3 and 5, page 50).
NL-31 |  | Slovenia | Netherlands | 03. Electrical cables | 91 | Section 3.1.3 (page 91) Why does not the report discuss third party certification organisations? | Website | Third party certification organizations with respect to cables are indeed relevant for qualification/typetesting of cables. However, this is not part of the report.
NL-32 |  | Slovenia | Netherlands | 03. Electrical cables | 76, 88, 93 | The Netherlands’ NPPs have PVC and SiR cables (page 76, 88, 93). Do the Netherlands’ NPPs NPPs intend to replace PVC cables considering the following practices: • IAEA SALTO mission’s recommendations that PVC cables should be replaced because of bad material properties, • some countries have already partly or totally replaced PVC cables (e.g. NPPs in Switzerland, Germany, Nederland…) Additionally, the report on page 87 states: “In the result of the cable assessment it was found that 27 cables with a PVC insulation and jacket installed in the areas T1 or T2 may be critical regarding ageing degradation for the period of LTO…”. | Website | A number of PVC cables, intrumentation and power cables (6000 V), is replaced to serve as test specimens in an ageing investigation program, carried out by a specialized laboratory (page 93, 96). Based on the results of this program actions will be taken, which may include replacement of cables. The IAEA SALTO mission in Borssele didn't reccommend the replacement of PVC cables.
NL-33 |  | Slovenia | Netherlands | 03. Electrical cables | 101 | Are AMPs for cables in Netherlands’ NPPs fully implemented in accordance with national regulation and international standards (IAEA, iGALL…) (page no. 101)? | Website | In Borssele AMP's for cables are implemented in accordance with relevant regulations and standards.
NL-34 |  | Slovenia | Netherlands | 03. Electrical cables | 91 | Why does not the report (Chapter 3.1.3, page 91) consider R&D programmes, objectives, contents, internal and external operating experience? | Website | In chapter 3.1.2.1 (page 70) the ageing assessment of electrical cables for Borssele is described. Applicable operating experience, R&D results, etc, are taken into account in the ageing management (see Figure 3 and 5, page 50).
NL-35 |  | Slovenia | Netherlands | 03. Electrical cables | 96 | How do you know in what condition the cables in conduits are? What methods do you use for inspection of cables in conduits? (page no. 96) | Website | Cables in the conduits are visually inspected where the conduits are attainable, which gives a good overview of the state of the cable. If there are doubts on the state of the cable, measurements will be carried out, e.g. insululation resistance.
NL-36 |  | Slovenia | Netherlands | 03. Electrical cables | 102 | The report mentions on page 102 that 200 cables are critical. Do you intend to replace these cables with new ones? | Website | A result of the assessment (conservative approach) for cables (page 87) is that a number of cables may be critical for LTO. A program has been started to investigate the ageing behaviour of relevant cabletypes, the actual temperature/dose rate at cable locations, etc. If necessary cables will be replaced.
NL-37 |  | Slovenia | Netherlands | 03. Electrical cables | 34 | Why does not the report consider R&D programmes, objectives, contents, internal and external operating experience (page no. 34). | Website | RID (HOR): Page 34 is dealing with the overall ageing management and not with electric cables. The WENRA technical specification does not require to discuss R&D activities in this section. The way R&D programmes, objectives, contents, internal and external operating experience can initiate the procedure for ageing management is described in section 2.4.3 page 53
NL-38 |  | Slovenia | Netherlands | 03. Electrical cables | any | Why does not the report discuss the acceptance criteria frequencies? | Website | EPZ (NPP): What is meant with acceptance criteria frequencies? Examples of criteria for cable inspections & frequencies can be found on pages 94-96. RID (HOR): On p.97 information is provided on monitoring / inspection and an applicable norm. NRG (HFR): The acceptance criteria are based on rules, regulations and guidelines as issued by standards-organisations and involved authorities. For inspection frequencies see table 7 and section 3.1.4.2 which also refers to a test-norm.
NL-39 |  | Czech Republic | Netherlands | 07. Concrete containment structures | general question on civil stractures | Report doesn´t comment civil structures (building parts) status for research reactors. Could you please provide us some details about the procedure for evaluation of the building objects status? Do objects belong to SSC? | Website | RID (HOR): HOR does not have a concrete containment building. No requirement are requested by the WENRA technical specification on other civil structures. NRG (HFR): The HFR does not have a concrete containment building as the reactor dome is constructed out of steel. One of the action points of the 10-yearly evaluation was containment building inspection. This inspection showed a positive result as the dome did not degrade over 50 years hence there was no need to include an additional AM program. In addition the leak tightness of the dome is tested every year according to the preventive maintenance program.
NL-40 |  | Belgium | Netherlands | 05. Reactor Pressure Vessels | 120 | Are there dissimilar welds at the RPV inlet and outel nozzles of Borssele and if so, have they been assessed with respect to ageing issues? | email | No. The Main Coolant Piping is made of ferritic steel. Therefore no dissimilar welds are in the inlet and outlet nozzles of the RPV.
NL-41 |  | Belgium | Netherlands | 04. Concealed pipework | 109 | A visual (video) inspection programme is performed on a 3-yearly basis. To which extent are the burried piping video inspected? Are they inspected on their full length or are sampling zones selected? | email | The full length of the Bonna piping is visually examined, using a robotic camera.
NL-42 |  | Belgium | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 25 | COMSY software is used currently used as a specific ageing management database. Is it only used as an ageing database or a specific software to predict/calculate degradations (FAC, SCC, etc.)? Who in the NPP organization is the responsible/owner of this COMSY-database? | email | COMSY is at NPP Borssele both used as a database for ageing management (incorporating all relevant information for the complete scope of SSC important to safety for all potential degradation mechanisms) and as tool to predict and calculate degradation (reduction of wall thickness) due to ageing mechanims like flow accelerated corrosion. The owner and responsible department of the COMSY database is the technical support department (KTE).
NL-43 |  | Belgium | Netherlands | 03. Electrical cables | 91 | For KCB, could you clarify what are the specific monitoring, testing, sampling and inspection activites related to the termination arangements (connections) ? | email | Cable connections are monitored with thermographic measurements and visual inspections on discoloration. Bolted connections are checked within maintanance activities of active components.
NL-44 |  | Belgium | Netherlands | 03. Electrical cables | 91 | How was the opportunity to trend the different data gathered during the testing and inspection activities (insulation resistance, pictures taken during inspections...) assessed by KCB ? | email | If trending of data is helpful in the AM it is used. For example some wiring in cabinet is periodically inspected because leakage of plasticizer was found in the past (page 99). In this case pictures are taken and the status is compared with previous years.
NL-45 |  | Belgium | Netherlands | 03. Electrical cables | 61 | Were the cables important for safety of the HFR subject to an environmental qualification programme? If yes, which standard was applied? | email | Under the assumption that 'environmental' means cable environment conditions, the following is applicable to the HFR. Emergency power supply cables are not subject to variable conditions (as concluded during soil condition inspections) hence a typical qualification is not needed. Furthermore the redundant cable configuration covers safe and continuous operation. Cables in the installation subject to radiation however are replaced based on preventive maintenance programmes. This maintenance was initiated based on a 10-yearly evaluation. Those cables are safety relevant as they are part of the line of defence (reactor shut down).
NL-46 |  | Belgium | Netherlands | 07. Concrete containment structures | 135-136 | What are the acceptance criteria related to the ageing mechanisms listed? | email | We refer to the response to the similar question from the UK (record no. 266). Acceptance criteria are provided in the text of the TPR report. Also at the plant, the acceptance criteria are listed in the documentation of the test procedures. | The reference refers to the line # 266 in the NL response table i.e. question NL-15
NL-47 |  | Belgium | Netherlands | 07. Concrete containment structures | 135-136 | Can one example of R&D programmes concerning ageing degradations mechanisms be given? | email | One example of the application of R&D programmes concerning ageing degradation was the repair and improvement of the outside of the reactor annulus building, which was performed according to the state-of-the-art in protection of rebar in a marine-based environment.
NL-48 |  | Belgium | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 23 | "This means that active SSCs are not part of the ageing management process. Ageing of the active SSC is managed by preventive maintenance and or surveillance". Could you elaborate on how this applies to all sorts of active components? Are they differences in the ageing management of electrical or and mechanical active components? | email | In general for the elecrical SSC a commodity based approach is used while for the mechanical SSC mostly a component based approach is used. The specific approach is depending on the commodity/component. For instance (electrical) batteries are according to the definition active and the ageing management consists of capacity testing of the batteries. For a mechanical valve with an active opening or closing safety function, periodic testing is in the surveillance programme.
NL-49 |  | Belgium | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 19 | Concerning the definition of active SSCs, is the definition based on the 10CFR54 or is it a specific Dutch definition? | email | The definition is based on 10CFR54.
NL-50 |  | Belgium | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 51 | Could you elaborate on the process set up for updating periodically all the AMPs and for integrating the evolution of the IGALL database? In particular, which is the maximal period between two updates of a same AMP? | email | Borssele: In principle every three years the AMPs are updated based on the normal review scheme. However if a lot of changes are applicable AMPs are updated earlier. When AMPs are updated IGALL updates will be included if applicable.
NL-51 |  | Belgium | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 58 | Could you detail the process for deciding which actions have to be completed before the beginning of the LTO period (2013) of Borssele NPP and which ones have to be finalized before 2020? Can you cite examples of actions of both categories? | email | This was part of the License change process. The LTO assessment including the ageing managent review was used as a basis to change the Safety Report. For this change a licence change was required. In 2012 an application for the Licence change was done. In the beginning of 2013 the new licence became in force. The licence was given by the authority and consisted of 11 requirements related to LTO. Some of the requirements had to be performed before going into LTO meaning before January 1th 2014. An example of such a requirement was to deliver an implementation plan for extra In-Service Inspection activities. In the same licence requirement specific inspections were mentioned which have to be performed before January 1th 2018.
NL-52 |  | Germany | Netherlands | 03. Electrical cables | 68-69 | On p.68-69 the classification of cables at the HOR research reactor based on IAEA guidelines is described. There are no cables in the categories 1-3 at the HOR reactor. For the categories 4-7 a representative conservative example is chosen for each category. Which stressors were part of the assessment in order to decide what constitutes a conservative example? The texts only implies that the dose rate was one of them. | email | RID (HOR): The applied IAEA guide also mentions the stressors to take into account. For a list of the stressors see for example section 3.13 of the IAEA guide. These are considered in the environmental qualification (EQ). It should be realised that the environmental conditions are a lot less harsh in an open pool type 2 MW research reactor, compared to a nuclear power plant for which the IAEA guide is written. Furthermore as there are no cables needed to perform in the categories 1-3 a full EQ (which focuses on DBA conditions) does not necesarily identify cables that are exposed to harsher environment during normal operation or monitoring conditions after an DBA. All stressors mentioned in the IAEA guide are considered, but engineering judgement was used to select the conservative example.
NL-53 |  | Germany | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 15 | A set of regulatory requirements (NVRs) relevant for ageing management of the Borssele NPP is listed. It is understood that these Dutch requirements originating from IAEA Safety Standards. Can The Netherlands explain how the NVRs applied for Borssele NPP will be updated to take into account latest developments at IAEA (e.g. SSG-25 for PSR, SSG-48 for Ageing Managment and LTO)? | email | Yes, the Netherlands have the system of NVRs that are based on the IAEA standards. In 2017 it was decided to start a project to update the current NVRs applied to NPP Borssele. The aim is to have them updated in 2020. The update will implement SSG-25 and SSG-48.
NL-54 |  | Germany | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 50 f., 55 | The consequences of the phase-out of nuclear power in Germany for the ageing managment of the NPP Boessele are addressed in several places of the report. It is outlined that the NPP Borssele will seek international collaboration and information exchange more outside Germany in the upcoming years. Some examples of the current efforts on this issue are given. Against this background, what are the current most important international activities on ageing management of NPPs from the Dutch point of view and how is the Safety Authority (ANVS) controlling the participation in this activities? | email | It is true that the gradual loss of German institutions has led to our initiative to establish the KWUREG club. One of the issues that is discussed is of course AM and LTO. Also the remaining KWU plants will work more closely together with AREVA. The most important international activities, according to ANVS, are taking place in the IAEA (IGALL). The Netherlands (mainly the NPP) has participated in that programme from the beginning. For a long time already, the Netherlands has used international experience through IAEA peer reviews (e.g. AMAT in 2003, SALTO 2009, 2012 and 2014). Also the NPP and ANVS participate(d) in such missions as members of review teams. Just recently (2017), also after consultation with the NPP, we have decided to start participation in the OECD/NEA CODAP programme. Participaption in OECD/NEA CADAK was also intended, but this programme stopped in 2017. What should also be noticed are the R&D activities carried out in several fora. ANVS has the intention to dedicate more attention to that.
NL-55 |  | Germany | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 57 ff. | Different activities such as PSR, assessement of the AMP against IAEA Guideline SR 57, and IAEA AMAT and SALTO missions are mentioned. For future inspections of the overall AMP, it is outlined that there is a need to develop a more detailed multi-year inspection programme. How do you see the relationship between the planned multi-year inspection programme and the PSR? | email | The inspection programme will enable ANVS to determine the strong and weak points of the AMP. This supports the review and assessment of NPP's periodic evaluation reports about the same subject. One of the safety factors of the PSR is ageing management.
NL-56 |  | Germany | Netherlands | 03. Electrical cables | 72-73, 97 | Cable deposits have the advantage of providing cables from an environment where several stressors (radiation and temperature) are the most severe and allow the conduction of destructive tests on these cables. The Dutch NPP has no cable deposit on its own. Instead it relies on cable deposits in a German nuclear power plant and experiments conducted by the German association VGB. As the last German NPP will cease power operation in 2022 additional measures will be necessary (as concluded by the regulator). However KCB entered power operation almost 15 years earlier than the German plants. How are these additional years of operational loading factored into the qualification process? | email | Cables which are not covered by the on-going qualification ageing-data of the deposit cables are replaced. Examples are cables of temperature measurements at the main coolant line. Regarding the cable deposit, is the plan is to move the deposit to one of the non-German NPPs in the "VGB working group".
NL-57 |  | Germany | Netherlands | 03. Electrical cables | 72-73, 97 | In 2014 a cable deposit has been introduced for the HFR research reactor. In principle this is a very commendable effort that is only rarely undertaken for research reactors. However the HFR has been in operation for a considerably longer time than 2014. How has this been accounted for? Were the cables in the deposits "used" cables? | email | The depot will not represent the condition of cables installed before 2014. The cable depot contains new cables used to determine degradation rate for the future. Other older safety relevant cables have been evaluated during previous 10-EVA sessions.
NL-58 |  | Germany | Netherlands | 03. Electrical cables | 91-92 | Lifetime calculations for MV cables are presented on pages 91 and 92. According to the description thermal ageing and ageing due to water trees were considered. What about ageing due to radiation? According to the previous assessment, e.g. figures 26 and 29 PVC medium voltage cables in radiation area R1 are susceptible to ageing. | email | Radiation is not a stressor for safety and safety relevant MV-cables. The cables in the figures 28 and 29 are all LV cables. MV cables are treated in a specific dedicated program (page 91).
NL-59 |  | Germany | Netherlands | 03. Electrical cables | 91-92 | The presentation of the results on p. 92 also mentions that 80 % or 90 % of the maximum allowable degradation was chosen as the safe end of life. What was the physical criteria to determine the maximum allowable degradation? | email | The physical critera was elongation at break of test specimens out of the insulation.
NL-60 |  | Germany | Netherlands | 03. Electrical cables | 94, 91-96 | On p.94 the ageing management activities for low voltage cables are described. Point 3 mentions the testing of mechanical and/or electrical properties when qualitative data of the conditions are necessary. Which properties are measured? Which measuring principles are applied there and how often are those tests usually conducted? | email | In the laboratory investigation (page 96) elongation at break is the property to determine a substansiated lifetime of the cables. For wiring a simplified bending test is carried out on a yearly basis to have an indication of brittleness of the insulation (page 95). In case of laboratory tests elongation at break is the property to detemine a lifetime. Insulation resistance measurements are carried out to monitor the momentary status of LV cables, this in case if visual inspection or other information gives reason for this.
NL-61 |  | Germany | Netherlands | 03. Electrical cables | 94, 91-96 | In general the description of ageing management activities on the pages 91-96 mention regular visual inspection only for LV cables (not for MV cables) and insulation resistance measurements only for the neufron flux instrumentation and the deep well pump cables. This is unusual as those AM methods are very common. Are there no corresponding activities for the other cable types? | email | Resistance measurements are carried out for other cables as well. Neutron flux mesurement cables are mentioned specificaly because they are a specific topic in the technical specification of the TPR. For cable types which may be critical for LTO (outcome of assessment) cables are replaced and used in laboratory investigations to determine a dedicated safe end of life for the excisting cables.
NL-62 |  | Germany | Netherlands | 07. Concrete containment structures | 139 | It is described (page 139) that one important inspection is the LOCA resistant coating, which is examined visually. Why was it not possible to use more sophisticated methods for this task? | email | This is possible and the NPP does indeed use further inspection techniques to examine the LOCA resistant coating. The adhesion of coatings to the concrete surface is tested by sampling on an annual basis, by performing a pull-off adhesion test in accordance with ASTM D-4541 pulling a glued test "dolly" from the substrate.
NL-63 |  | Germany | Netherlands | 07. Concrete containment structures |  | Nothing is indicated in the chapter on 07. Concrete containment structures regarding the inaccessible areas. How are the ageing management programs applied for these areas? What procedures are used to evaluate the ageing phenomena in inaccessible areas? | email | Inaccessible areas for the reactor annulus building mainly exists in the foundation of the building. For these areas, the quality of the protective tar based coating is inspected and the condition (incl. acidity) of the groundwater is monitored.
NL-64 |  | Germany | Netherlands | 04. Concealed pipework | 109 | If no Certified Third Party is involved in the assessment of the buried and underground tanks and pipes, how does ANVS evaluate the inspection programmes for these SSCs and their results? | email | For the NPP Borssele, ANVS used a 2nd party specialist to assist in the evaluation of the programme and the inspection of these pipes and tanks. As this party is not certified for NPPs by ANVS, her advice is taken into account by ANVS and ANVS carries the ultimate responsibility for the evaluation. Somewhat more background information: For equipment under the Dutch nuclear pressure equipment directive, it is the task of ANVS to review and approve the inspection programmes of the licensees. Usually, ANVS will ask the Certified Third Party and/or its TSO GRS for advice in the review proces. The Certified Third Party and the licensees perform their activities based on the inspection programmes approved by ANVS. ANVS is supervising the activities of both, the licensees and the Certified Third Party. ANVS has its own nuclear inspectors with mechanical, material and/or NDO background. ANVS is applying a risk based approach in its supervision activities. For equipment not subject to the Dutch nuclear pressure directive, a graded approach can be applied.
NL-65 |  | Germany | Netherlands | 04. Concealed pipework | 110 | The determination of any settlement of the water lines appears to be restricted to the VF system. What is the reason not to include the VE system in this survey? | email | The reason for not including the VE system in the settlement measuring programme for pipelines is that these pipes largely consist of GRP pipes. These are not prone to settlement in the soil due to their weight. Any settlement is also not as influential on the ageing of the pipe as in the mainly concrete based Bonna piping.
NL-66 |  | Germany | Netherlands | 05. Reactor Pressure Vessels | 120 | Among the ageing mechanisms to be addressed "thermal ageing" is missing. How is thermal ageing of the RPV addressed in the AMP of KCB ? | email | Thermal ageing was in the ageing management review considered as a potential ageing mechanism for the RPV. Particularly based on the specific material constituents (for instance Cu content in the beltline weld and delta-ferrite in the austenitic cladding) in the subcomponents of the RPV, thermal ageing was in the outcome classified as an insignificant ageing mechanism for the RPV of NPP Borssele. Based on this in the AMP of the RPV thermal ageing is not incorporated.
NL-67 |  | Germany | Netherlands | 05. Reactor Pressure Vessels | 151 | The maximum specimen temperature in the surveillance rigs of the HFR remains below 100 °C, while the operating temperature of the vessel is 40 to 66°C. How can it be assured that the surveillance specimens do not deliver unconservative results due to a difference in irradiation temperature? | email | In the design of the surveillance program (SURP) the representative irradtion conditions have been defined in detail. The temperature is one of these conditions. The design and safety report of the irradation facility is based on these irradiation conditions. Therefore the irradiated specimens will always be subjected to conditions representative for the vessel.
NL-68 |  | RPV expert group | Netherlands | 05. Reactor Pressure Vessels | 123 | 5.1.3 According to the information in NAR report (pag. 123), the last specimen for the neutron fluence monitoring will be taken out in 2018 and their assessment will permit to verify if the safety margins for the RPV are still maintained. Considering the long-term operation (LTO), does Borselle NPP have some other additionally monitoring program to surveillance neutron exposure of the vessel materials up to the end of LTO period, i.e an ex-vessel neutron dosimetry program (EVND)?. | expert group 2 | In 2010 the neutron fluence was experimentally determined by taking scraping samples from the stainless steel cladding on the inside of the vessel. The results were compared with the theoretical fluence calculations. It could be shown that the results from experimental and theoretical fluence determination matched very well. Based on this it was concluded that the theoretical calculations are reliable to determine with sufficient accuracy the neutron fluence. If needed scraping samples can be taken again in the period from 2018 until 2034 but based on the experimental validation with scraping samples and the high safety margins in the safety assessment of the RPV we don't see the necessity to this.
NL-69 |  | RPV expert group | Netherlands | 05. Reactor Pressure Vessels | 128 | 5.1.4 In page 128 of your NAR is written “One-Time Inspections are periodically performed”. Do you want to say that one-time random inspections are performed in order to verify the effectiveness of water chemistry program?. | expert group 2 | Yes
NL-70 |  | RPV expert group | Netherlands | 05. Reactor Pressure Vessels | 130 | 5.1.4 In NAR page 130 is written “The ISI-programme at Borssele is based on the ASME XI guidelines …” Are all ASME XI requirements (scope, frequency, examination, acceptance criteria, etc) fully applied?. | expert group 2 | The ISI-programme is based on ASME XI but is not completely fulfilling all requirements. Before every ISI-interval (10-yearly in line with ASME XI) a proposal for the upcoming ISI programme is made and send to the regulator for approval. The accepted programme can have deviations (for instance in scope) from the ASME XI requirements based on both regulatory and licensee proposals (which should be motivated).
NL-71 |  | Concrete containment PCPV expert group | Netherlands | 07. Concrete containment structures | 138, 139 and 140 | 7.1.3 Text of the report: - page 138 "It is important that there is no cracking of any kind in the concrete" - page 139 "Inspection for seismic resistance is executed to confirm the absence of cracks in concrete structures." - page 140 "The concrete is checked for absence of cracks" Question : Since the normal state of concrete is to have at least thin cracks, could the Licensee precise, in terms of crack thickness, the accceptance criterion adopted ? That criterion might depend on the functional requirement of each part of the buildings. | expert group 4 | This is correct. The text that is referred to is from the assessment of the condition of the concrete used in the foundation for equipment. The inspections of these foundations do not focus on the typical hairline cracks of well cured concrete, but rather look for evidence that the support is damaged due to undue force that was applied to the concrete foundation and the anchors. Any cracks in that area that could point to undue force that was applied are unacceptable.
NL-72 |  | Concrete containment PCPV expert group | Netherlands | 07. Concrete containment structures | 135 | 7.1.2 Table 13 Ageing Measures for the Reactor Annulus Building (02) Concerning concrete structures, is the pathology named Delayed ettringite formation (DEF) considered in the AMP ? If not, please explain the reasons that rule out the risk of DEF. If yes, please describe the periodical actions (inspections, sampling, laboratory tests...) carried out in the framework of AMP. | expert group 4 | Delayed ettringite formation (DEF) can damage concrete that has experienced a temperature above about 70°C during the curing process. High temperature heat curing history is not considered due to the concrete specifications during building of the NPP.
NL-73 |  | Concrete containment PCPV expert group | Netherlands | 07. Concrete containment structures | 136 | 7.1.2 Table 13 - Foundations Question 1 : Could the Licensee detail the following : "Inspection of foundations on specific requirements (Seismic)" ? Question 2 : The NPP foundation is supported by piles. Are they reinforced concrete, or metallic ones ? Could the Licensee present the ageing assessment of the piles ? | expert group 4 | Inspection of foundations on specific requirements (Seismic) refer to a specific inspection protocol used at the NPP for this purpose. In this protocol is referred to specific attention for cracks and the connection of anchors. It is also confirmed, during this inspection that the foundation still complies with its design conditions. Piles are made of reinforced concrete and considered part of the foundation of the reactor building, for which the ageing assessment by the OEM formed part of the ageing management review for LTO.
NL-74 |  | Concrete containment PCPV expert group | Netherlands | 07. Concrete containment structures | 132 | Does the report include the concrete structures inside the containment? | expert group 4 | Concrete structures inside the containment were not described in the scope of ageing management for the concrete containment structures in the technical specifications for the National Assessment Reports.
NL-75 |  | Concrete containment PCPV expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 18 | On page 5, 6 regarding scope. What method is used to find non‐nuclear safety classified civil structure having an consequential risk to nuclear safety? | expert group 4 | A combination of (earthquake) classification, plant documentation and plant walkdowns is used to determine which non-nuclear safety classified civil structures should be in scope. Earthquake classification is available. Earthquake class IIB is applicable for civil structures which are themselves not-nuclear safety relevant but which can have an impact on safety relevant SSC in case they collapse.
NL-76 |  | Concrete containment PCPV expert group | Netherlands | 07. Concrete containment structures | 132 | In accordance with Technical Specification for chapter 7.1.2, can you describe the establishment of acceptance criteria related to ageing mechanisms? | expert group 4 | Acceptance criteria are defined in the text for the individual inspection protocols, based on internationally accepted standards, e.g., the ISO 4628 series of standards for the evaluation of degradation of coatings, ASTM D-4541 for coating adhesion and for the inspection and evaluation of concrete constructions, based on the CUR recommendations (Civieltechnisch Centrum Uitvoering Research en Regelgeving - Dutch Center for Civil Engineering Research and Codes)
NL-77 |  | Concrete containment PCPV expert group | Netherlands | 07. Concrete containment structures | 136 | In accordance with Technical Specification for chapter 7.1.3, what are the acceptance criteria for? | expert group 4 | Acceptance criteria are provided in the text of the TPR report. Also at the plant, the acceptance criteria are provided verbally in the test procedures.
NL-78 |  | Concrete containment PCPV expert group | Netherlands | 07. Concrete containment structures | 140 | From reading chapter 7.1.4 it is our understanding that the visual inspections are the preventive actions for concrete structures that you carry out. Is that correct understood? | expert group 4 | Visual inspections are an important part of the inspections to identify ageing. However, in chapter 7.1.4, many examples are provided where other inspection techniques and remedial activities are used in the preventive and remedial actions for concrete structures.
NL-79 |  | Concealed pipework expert group | Netherlands | 04. Concealed pipework | General | Are methods of contactless diagnostics that allow assessment of inaccessible sections used at Dutch NPPs (methods of contactless diagnostics for underground piping: contactless magnetometric diagnostics method; acoustic tomography method. These methods reveal loss of integrity of piping and do not require direct access to piping external surface. Diagnostics is carried out from ground surface above the piping. 100% of piping from all observation groups is inspectable). This information should be added to the Report or corresponding clarifications might be provided as an answer. | expert group 5 | Loss of integrity of relevant underground steel pipework is conducted by trending the effort necessary to remain up to pressure in the applicable system, as described in section 4.1.3.1. Buried piping for the system for essential service water, providing cooling for SSCs that are important to safety does not consist of steel piping at the Dutch NPP, but uses the Bonna piping as explained in the report. Visual inspection of these pipes is considered effective.
NL-80 |  | Cables expert group | Netherlands | 03. Electrical cables | 60/61 | The lead document on cable management, for the NPP, and for the research reactor HFR. There seems to be a difference in the model, because for the NPP it is mentioned that only the importance for nuclear safety which is a the basis for selecting cables for the AM program. In the Table 3, with cables a for HFR, the Junction Boxes are not mentioned. It is not clear whether there are cables with paper insulation, or other types of insulations, such as oil, or other types. | expert group 3 | NPP: In the NPP there are no paper or oil insulated cables. The used insulation materials are listed in Figure 16. HFR: The purpose of table 3 is scoping. The cable types are described by make and type, hence it is possible to find the specification of the insulation. This specification was however not relevant to the table's purpose.
NL-81 |  | Cables expert group | Netherlands | 03. Electrical cables | 61 | just to confirm all the cables to components that are "safety" or "safety relevant" as in the penultimate para on page 61, are included in the scope of AM. That would include all the cables for the support equipment (to safety related equipment) as well? | expert group 3 | Support systems relevant to safety are part of the safety systems. As a result those systems are part of the current AM program. An example is the preventive maintenance of the coax cables of the reactor nuclear channel instruments (which support the safety barrier functions of the reactor). The same applies to the emergency power supply cables (from the emergency generator sets to the reactor). Those cabels are equipped with cable resistance monitoring (which indicates cable damage / degradation). The monitoring system itself is subject to a preventive maintenance program.
NL-82 |  | Cables expert group | Netherlands | 03. Electrical cables | 67, table 4 | The segregation of the cables at HOR, there is not clear whether there are any medium voltage cables in this program. | expert group 3 | RID (HOR): The segregation of cables indicated in the table is the general structure. High volgtage cables for instrumentation is an exception to this general table, with dedicated specifications as mentioned in the text just above the table. More information on these medium voltage cables toward ionisation chambers can be found in section 3.1.2.3, for category 5 equipment.
NL-83 |  | Cables expert group | Netherlands | 03. Electrical cables | 66 | The categorization of cables related to the operating environment (environmental qualifications) is pretty vague. Clarification is needed. | expert group 3 | RID (HOR): As mentioned in section 3.1.2.3 the operating environment at the HOR is mild. Environmental classification based on the IAEA guide NP-T-3.6 would always lead to a mild environment. Engineering judgement is used to select the conservative combination of category classification and environmental classification.
NL-84 |  | Cables expert group | Netherlands | 03. Electrical cables | 78 | Does KCB have any of its own cable deposits, or it relies on German deposits only? Are all the cables used in KBC manufactured in compliance with German standards for NPP cables? | expert group 3 | KCB does not have its own cable deposit, but cables used in the plant are within the German deposit. In a VGB working group this deposit is used for a number of plants, among which is Borssele NPP. A large amount of the cables are qualified in accordance with German KTA standards, some newer cables in accordance with IEEE standards.
NL-85 |  | Cables expert group | Netherlands | 03. Electrical cables | 89/98 | At HOR, high amps cables between containment and low voltage supply room were replaced. Have the new (replacement) cables the same specifications? Were also the medium voltage cable replaced? | expert group 3 | RID (HOR): Cabling between the containment and the low voltage supply room is 380VAC max. According to the WENRA specification 380VAC is defined as the lower boundary for medium voltage cabling. All cabling between HOR containment and low voltage room were replaced. Cables specification is updated to the most recent standards. Main differences include higher isolation and application of halogen free materials.
NL-86 |  | Cables expert group | Netherlands | 03. Electrical cables | 90 | At HOR, the ionization chambers cables are subject to high doses of radiation and high temperatures. Are those cables still (safely) usable? How did you determine this? | expert group 3 | RID (HOR): Dose rates at the position of the boron lined ionisation chambers are actually not high when considering the specification for the applied mineral cables. Nor are the temperatures. Isolation resistance was last tested in 2010, when the signal processing units for these channels were replaced. No degradation was observed. Cables are safely usable due to the fail safe design.
NL-87 |  | Cables expert group | Netherlands | 03. Electrical cables | 93 | The NAR indicates that the " knowledge of the model for water treeing is limited". However there are 13 safety and safety related cables that are either considerable beyond or beyond estimated lifetime. What do you intent to do to gain more confidence in the model? | expert group 3 | In 2017 6 MV-cables are replaced and used as test specimens to tune the model to the specific cables used in the plant (page 91). So the model is now based on the specific cables used in the plant. Also dielectric spectroscopy meausrements are introduced which can detect the presence of water trees.
NL-88 |  | Cables expert group | Netherlands | 03. Electrical cables | 97 | For HRF, could you provide more information on test, measuring and demonstration methods that are used for the monitoring of the ageing condition of the cables. What is the frequency of monitoring, testing and inspection activities? | expert group 3 | HFR: The cables are tested during operational check out procedures (before reactor restart) at least 10 times a year. Whenever failures occur corrective measures are taken. If needed in-depth evaluation and analyses are performed.
NL-89 |  | Cables expert group | Netherlands | 03. Electrical cables | 97 | For HOR, are there specific test for the monitoring of the ageing condition of the instrumentation cables beyond the self-monitoring? | expert group 3 | RID (HOR): The argumentation in the text shows nearly all cables are designed to be fail safe. No dangerous situation can occur due to failure of a single cable. Therefore no specific test are executed on a periodic base to monitor the ageing of instrumentation cabling.
NL-90 |  | Cables expert group | Netherlands | 03. Electrical cables | 100 | What is licensee's experience with using the tool AUREST, especially related to the analysis to estimate the end of the life of cables? | expert group 3 | The tool AUREST is very useful to: 1. select the components (including cables) which are during LOCA/HELB situations in a harsh environment; 2. check if every component qualification fulfills the LOCA resistance requirements; 3. calculate the remaining radiological and thermal qualified life of every single component and 4: present the results in a clear overview (page 72, figure 13). The licensees experience with AUREST is positive. AUREST is specifically meant for components, including cables, with a LOCA resistance requirment (harsh environment).
NL-91 |  | Cables expert group | Netherlands | 03. Electrical cables | 100 | Has a systematic thermographic assessment of cables, to identify possible hots spots been undertaken at KBC? If yes, were any local hot spots affecting the cables found? | expert group 3 | Thermographic measurements are not carried out in a systematic way to identify hotspots for cables.
NL-92 |  | Cables expert group | Netherlands | 03. Electrical cables | 100 | At HRF the most safety relevant buried cables are the emergency power, from DG . It appears that for those cables no comprehensive inspection program to determine degradation exist. | expert group 3 | HFR: The redundant cable configuration covers safe and continuous operation. In addition the cable resistance of both cables is monitored continuously. In case any degradation is measured corrective actions will be taken.
NL-93 |  | Cables expert group | Netherlands | 03. Electrical cables | 102 | At HOR, the majority of cables (safety significant) were replaced 35 years ago, when the control room was moved outside the reactor building. Given the long time interval are these cables are still in good condition? | expert group 3 | RID (HOR): It is good to realise that the environmental conditions of the cables at the HOR can be considered to be mild. Furthermore no category 1-3 cables (according IAEA NP-T-3.6) exist at the HOR. Visual inspection and bending of the cables shows no degradation of the insulation. Safety relevant cabling was last tested on isolation resistance in 2010. No degradation was measured. Together with the fact that no dangerous situation can occur due to failure of a single cable, the cables are fit for purpose.
NL-94 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 4 | it is mentioned also that the Aging management program of HFR is still in progress, and the requirements (input) of the regulatory body are not specified, mentioning that the regulatory body is expecting the licensee to provide the next steps and information on the milestones. | expert group 3 on other topics / expert group 1 | At 29-12-2017 the ANVS received the Asset Management development planning which includes ageing management. In the ANVS official reply it is stated that this planning shall be followed.
NL-95 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 36 | In the presentation of the aging assessment of HFR (High flux reactor), the presentation (specific information) is not quite specific, being more a set of requirements from textbooks, or guides. The presentation should concentrate more on what was really implemented in the reactor. The theoretical part from the textbooks should be skipped, because these are common for each AM program. The report should present fact like the number of repair activities, corrective / preventive maintenance actions, frequency of tests, repairs, equipment in the scope of the program, etc. | expert group 3 on other topics / expert group 1 | HFR: The HFR has many sources of data available which could be used for an AM program. The complete AM program system however needs further development as described in the report. Yet particular monitoring and corrective action programs exist like the primary cooling water pump inspection and the monitoring program.
NL-96 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation |  | Regarding chapter 02 the Netherlans report is following the technical specifications and is well structured with sufficient information to cover the subchapters of Chapter 2. It should be noted that is has incorporated the information about the research reactors in the subchapters accordingly. | expert group 3 on other topics / expert group 1 | Thank you.
NL-97 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 42 - 47 | From the text is not very clear if there are any provisions for identifying unexpected degradation set in place for the NPP and the research reactors. Could you provide more information about that? | expert group 3 on other topics / expert group 1 | NPP: At NPP Borssele an ageing experience feedback procedure is in place in which internal and external ageing events are assessed and if needed the existing ageing management is modified. This procedure is described on page 17 and 18 of the NAR. If unexpected degradation occurs this will be assessed according to this procedure. HFR: During the 10-EVA (10 yearly PSRs) the existing programs are assessed addressing all applicable degradation mechanisms. RID (HOR): By identifying the individual SSCs of the HOR and evaluating the possible ageing degradation mechanismes, unexpected degradation is eliminated as much as possible. If something is truly unexpected it is hard to provide provisions. Only mitigating actions can than be prepared
NL-98 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 33 | Figure 7 is not referred in text. QA coördinator is (correctly) coordinator. | expert group 3 on other topics / expert group 1 | RID: ok, to be corrected in the text
NL-99 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 34 | In case of AM of HOR: RCM is placed into center of AM. RCM as maintenance in general ensures functional integrity of components (it is correct in text, see "RCM focuses on maintaining functionality"). AM, however deals primarily with structural integrity of passive components, and it is not included into RCM, see flowchart of Figure 8. | expert group 3 on other topics / expert group 1 | RID (HOR): RCM is recommended by the NUREG to be used in ageing management. RCM is only guiding a way to do AM. The statement "run to fail" in figure 8 can be replaced by "used till failure" to include passive components in the general strategy to set up the AM.
NL-100 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 40 | Surveillance program: please write unstable crack growth instead of fracture growth, and crack length instead of fracture length (page 41). | expert group 3 on other topics / expert group 1 | HFR: This chapter describes failure analysis, but description in the report could have been more specific.
NL-101 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 40 | ASME BPVC XI is dealing with ISI of NPP components. HFR is a research reactor. | expert group 3 on other topics / expert group 1 | HFR: As there are no guidelines for aluminium systems the ASME BPVC XI is used as a guideline.
NL-102 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 43 | What is the origin of the three extra sets of surveillance specimens? Please explain. | expert group 3 on other topics / expert group 1 | The extra sets are made of original RPV material which is still available in the storage of the plant. More information can be found on page 122.
NL-103 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 43 | NDT system qualification: is it done according to ASME Section XI or ENIQ methodology? Please clarify. | expert group 3 on other topics / expert group 1 | In principle qualification according to ENIQ is done for NDT. The exact qualification procedures have to be agreed upon by the independent certified party.
NL-104 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 48 | Why both mechanical and chemical cleaning was necessary to clean steam generator tubing? | expert group 3 on other topics / expert group 1 | By mechanical cleaning alone the sludge on the tube sheet could not be removed completely. With the combination of mechanical and chemical cleaning a large part of the sludge could be removed lowering the risk of local corrosion as much as possible.
NL-105 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 50 | First para: instead of conformities please write non-conformities. | expert group 3 on other topics / expert group 1 | yes this should be non-conformities.
NL-106 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 50 | Is environmental qualification a TLAA? I do not think it is. | expert group 3 on other topics / expert group 1 | EPZ (NPP): Environmentally qualification is formally not a TLAA according to the TLAA definition but because of the time related aspects it was treated as one.
NL-107 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 57 | Control valve corrosion in HOR: please describe the type of corrosion for better understanding. | expert group 3 on other topics / expert group 1 | RID (HOR): The coating specification of the valve housing did not include requirements on the coating underneath the seat rubber. Due to intrusion of process water behind the seat, corrosion was formed on an uncoated strip on the casted iron valve housing. Corrosion was formed due to oxygen in the process water which intruded behind the valve seating. More information on this specific accident can be found in the IAEA IRSRR database, with IRSRR number 206.
NL-108 |  | General AMP expert group | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 59 | Embedding AMP in organization: instead of "maintenance part of organization" it is advised to put it in enegineering support part, as usual. | expert group 3 on other topics / expert group 1 | According to the ANVS there is no 'one size fits all' solution for all types or sizes of reactors and it does not matter how things are organized as long as the licensee can demonstrate to the satisfaction of the ANVS that the AMP is an effective system.
NL-109 |  | EC | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 18 | 2.3.1: Scope: it seems that only passive components are included in the scope. It is true that these components have a self revealing nature of ageing effects. However, certain parameters (flow, pressure, vibrations,…) could indicate ageing in other (passive) parts of the system. How is this taken into account? How is the complete health of a system assessed (system health reports)? Moreover, certain ageing mechanisms do not discriminate between active and passive (e.g.: effects of water chemistry on valves). |  | Only passive components were part of the Ageing Management Review and in principle the implemented ageing management process is taken into account only passive structures and components. This does not mean that active components have not been reviewed or no ageing management is done. In the LTO assessment the active components also have been assessed. A verification was done to prove that all safety functions of active components are managemd in a preventive maintenance or a surveillance programme. The ageing management of the active components is relied for upon the preventive maintenance and surveillance programme while for the passive SSC on top of that an integration process is implemented combining all the specific activities. It is not clear what is meant with self revealing nature of ageing effects for passive components. This seems more applicable for active components. In Borssele also system health reports are made for critical systems. In this all the components are involved. The ageing management process delivers input for the system health reports (for the passive parts).
NL-110 |  | EC | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 24 | 2.3.2.: Ageing assessment: How are transients (e.g.: SCRAM, thermal shocks, etc.…) included in the workflows fig 4 p24) |  | As part of the fatigue Ageing Management Programme a load catalogue is available in which all transients are specified. Every year all the relevant transients are counted and analysed and brought together in a yearly fatigue monitoring report. This report forms the basis of extra fatigue management measures if needed.
NL-111 |  | EC | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 26 | 2.3.1.: Scope: point e of the WENRA T.S. has not been discussed. Do indicators exist to monitor the process? |  | Specific indicators exist like cumulative usage factors for fatigue, residual lifetime for part of the electrical equipment and RTNDT for the RPV. On the overall level of the process performance indicators still have to be developed.
NL-112 |  | EC | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 30 | 2.3.1: Scope: it seems that the SSC for the scope of HFR have been determined, but that actual completion of the AMP might take some time. Have any deadlines/milestones been identified? |  | The mile stone plan exists and has been submitted by the LH to the ANVS for evaluation.
NL-113 |  | EC | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 32 | 2.3.1.: Scope of the HOR: are any indicators used to assess the effectiveness of the maintenance/ageing process. If so: do these indicators justify a revision frequency of 10year-1? |  | RID (HOR): The newly developed ageing management program will be evaluated in the next Periodic Safety Review round. Changes in ageing management on SSCs are evaluated in their own Plan-Do-Check-Act cycles, which do not have a set period of 10 year.
NL-114 |  | EC | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 36 | 2.3.2.: There are no R&D needs listed in this paragraph. Does that mean that there are no such needs? |  | EPZ: R&D on the use of Film Forming Amines is of interest for Borssele. EPZ is following conferences on this. HFR: There were needs for R&D in the past, like the corrosion of aluminium. Such R&D-programs have been executed. In addition the SURP program is a continuing R&D-type program. RID (HOR) does not forsee any R&D needs for our ageing management program. In case of missing expertise this knowledge is consulted/hired or discussed in the Research Reactor community, as described in section 2.4.3 of the NAR.
NL-115 |  | EC | Netherlands | 02. Overall Ageing Management Programme requirements and implementation | 43 | 2.3.3: leakage management program including walk downs is in place. Please could you indicate who performs those walk downs (field operator, maintenance engineer, design engineer, operations engineer?) and with what frequency. |  | Walkdowns are performed by the field operators as part of their procedures but also leakage rounds are done by the engineering department at the end of the outage. In this rounds also the independent third party is participating to report to the nuclear regulator.
NL-116 |  | EC | Netherlands | 03. Electrical cables | 94 | In relation to AM of LV cables in Borssele: "3. Testing of mechanical/electrical properties when…necessary". What is the criterion for decision? What tests are performed? What are the acceptance criteria for those tests? |  | Criteria for cable inspections are e.g. "discoloration, cracking due to embrittlement, melting and swelling of wire and conductor insulation and cable jacket". In an engineering judgement it will be decided if measures are taken necessary. But also other in- and external operating experiences can be the reaseon for measures. Examples of measures are the laborotary investigations on LV and MV cables mentioned in the NAR to determine a safe end of life based on elongation at break. Insulation resistance measurements may be carried out if there are doubts about the state of the cable as result of visual inspections.
NL-117 |  | EC | Netherlands | 03. Electrical cables | 97 | What is the frequency for taking test samples of HFR cable depot? |  | HFR: This is not defined yet, as the cables have been subjected to radiation for 3 years only, hence this is not a relevant matter at this moment.
NL-118 |  | EC | Netherlands | 03. Electrical cables | Generic 60-102 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found for the Borssele NPP. |  | The groups for Borssele NPP are described on page 61.
NL-119 |  | EC | Netherlands | 05. Reactor Pressure Vessels | Chapter 5.1.3, page 126 | In the page 126 it is stated: "At NPP Borssele Corrosion Fatigue was taken into account in the revalidation of the fatigue analyses for 60 years of operations. To do this a (at that time) draft German KTA guideline 3201.2 (Teil 2)56 was followed." Question: The final version on KTA 3201.2 was issued in November 2013. Has been it verified that the fatigue analysis remains valid? |  | The draft KTA guideline 3201.2 was used to have a criterium for screening on environmental fatigue. In the draft version a CUF of 0.2 was applicable for austenitic steel. In the current version of this KTA this CUF was changed into 0.4. For Borssele this means that the used screening criterium for austenitic steel results in more fatigue locations to be assessed on environmental fatigue. This has no influence on the validity of the fatigue analyses.
NL-120 |  | EC | Netherlands | 07. Concrete containment structures | 133 | Please provide a legend for Figure 33 identifying the numbered items in the diagram (some are obvious, but items 5 and 6 are not) |  | Figure 33 was included as an graphical representation of the written description of the Reactor Annulus Building and the numbered items were not considered important for clarifying this representation. However, the legend for the numbered items is as follows: 1 - Reactor Pressure Vessel 2 - Steam Generator 3 - Safety injection buffer tanks 4 - Polar crane 5 - Access ladder 6 - Installation area 7 - Steel containment sphere 8 - Concrete dome section of concrete reactor annulus building 9 - Fuel loading machine
NL-121 |  | EC | Netherlands | 07. Concrete containment structures | 144 | Crazing, delamination and flaking of the applied coating indicated that in the event of a LOCA, the coating would not have resisted the heat impact. Consequently, it was beyond the end of its life. Has it been estimated how long the coating had been in a condition that it would not perform as designed? Will future inspections be able to detect degradation and anticipate the end of life before the next scheduled inspection? |  | The inspection was performed due to the results of the VGB-Arbeitsgruppe"Gesicherte Sumpfansaugung" in 2000. A root cause analysis at that time identified inappropriate use of nitrogen freezing of pipelines in the area to be the cause of the premature ageing of the coating. Applicable areas were covered by stainless steel sheeting at that stage, to prevent that any damaged concrete as a result of a LOCA would become dislodged. From that point on, annual visual inspections on the remaining coatings have been performed as described in the TPR report, as well as annual pull-off adhesion tests, which is currently considered sufficient for early anticipation of degradation.
NL-122 |  | EC | Netherlands | 07. Concrete containment structures | 135 - 140 (Table 13) and section 7.1.3 | No, or very little, information is provided on the acceptance criteria for the different degradation mechanisms and inspections, as requested in the WENRA Technical Specification. Please could you provide some further details. |  | Acceptance criteria are defined in the text for the individual inspection protocols, based on accepted standards, e.g., the ISO 4628 series of standards for the evaluation of degradation of coatings, ASTM D-4541 for coating adhesion and for the inspection and evaluation of concrete constructions, based on the CUR recommendations (Civieltechnisch Centrum Uitvoering Research en Regelgeving - Dutch Center for Civil Engineering Research and Codes). Acceptance criteria are described in the text of the TPR report. Also at the plant, the acceptance criteria are provided verbally in the test procedures.
NL-123 |  | EC | Netherlands | 07. Concrete containment structures | 135, 136 (Table 13) | It is not clear why 'inspection of foundations on specific requirements (Seismic)' and ' Settlement survey for buildings' are linked with 'Change in material properties' and the three ageing mechanisms associated with it (leaching, carbonation and elevated temperature) in Table 13. |  | This is correct. The programmes 'inspection of foundations on specific requirements (Seismic)' and ' Settlement survey for buildings' do not belong in this table.
NL-124 |  | EC | Netherlands | 07. Concrete containment structures | 137, Table 14 | It is not clear why concrete outdoor walls do not have the same requirements as the roof, e.g. seismic requirements and external impact are not listed as relevant. |  | This is correct. The programmes shown in table 14 are actually examples of existing structures, which in this case have differing requirements. The inspection protocols of the plant do in fact have dedicated sections for all special requirements for foundations, floors, walls, outer walls, ceilings and roofs, i.e., for seismic, security, radiation protection and decontamination requirements, air/gas/fluid containment, explosion, fire protection, LOCA, flooding, airplane crash, chemistry, ionizing and special environmental conditions.
NL-125 |  | EC | Netherlands | 07. Concrete containment structures | 140-141 | Can you provide a bit more information regarding the acceptance criteria for cracks and other damages identified during visual inspection and which circumstances would lead to performing a further assessment with the chipping hammer. |  | Acceptance criteria for cracks concern the location of the cracks, the crack pattern, including orientation, form and depth, if the crack is in the vicinity of rebar, if evidence of rust (colouration) is present, if water is seeping or bleeding from the crack. The crack width is measured with the aid of a crack measurement magnifying glass or crack dedicating map and the crack length is taken into account. Edges are evaluated for erosion and in case of parallel cracks, the distance between cracks is recorded. If it would be decided that the cracks will still be acceptable until the next inspection, photographic evidence is recorded. Similar considerations are made for other damage mechanisms, evaluating the results of the visual inspection.
NL-126 |  | EC | Netherlands | 07. Concrete containment structures | 140-141 | Is any testing performed with the aim of detecting the potential for reinforcement bar corrosion (e.g. tests for carbonation of the concrete) before any visible effects of deterioration are found in the visual inspections or are these tests only performed after finding defects at the surface of the concrete? |  | No preventive core drilling is performed to detect potential corrosion issues. Additional techniques will only be utilized as a result of visual indications.
NL-127 |  | EC | Netherlands | 07. Concrete containment structures | general | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | The scope of the concrete containment structures for this TPR consists of the Reactor Annulus Building, for which there are no areas that are not accessible for inspection of potential degradation mechanisms, with the exception of the foundation below ground level (including piles) as described above.
PO-1 | 1 | Norway | Poland | 02. Overall Ageing Management Programme requirements and implementation | 20 | Have there been any external review of the Ageing Management/Control Program? | Website | There has not been any external review of Ageing Control Programme. Although the new Ageing Management Programme has not yet been developed, the regulatory body issued a set of requirements as guidelines for the proper AMP, the requirements include the external review of AMP. The ageing management programmes for specific SSCs prepared by external organizations are reviewed by independent specialists/organizations, which were not involved in development of these programmes.
PO-2 | 2 | Norway | Poland | 02. Overall Ageing Management Programme requirements and implementation | 22 | • What is the status of the Ageing Management Program that should be developed before the end of 2017? • Have there been any inspections related to ageing after the process of renewed license in 2015? | Website | The Ageing Management Program was finished by the operator of RR at the end of 2017 and now is under the process of assessment by PAA. Yes. The ageing management is one of the topic of standard inspection program for research reactors. This topic has been inspected during standard inspections as well as during the process of license renewal.
PO-3 | 3 | Finland | Poland | 03. Electrical cables | 25 | Report does not clearly indicate if there are cables which have performance requirements in case of accident conditions. If there are such cables how this is considered in the AMP? | Website | Although the ACP does include all electrical cables in MARIA reactor, including cables which have performance requirements in case of accident conditions, there is no demarcation between normal cables and cables with performance requirements. In accordance with the standard PN-HD 60364 all cables are subject to, inter alia, the following measurements: • Electrical continuity test • Measurement of insulation resistance of electrical installation • Inspection of the effectiveness of the indirect contact protection by means of automatic power shutdown • Measurement of short-circuit impedance
PO-4 | 4 | Switzerland | Poland | 03. Electrical cables | 22 | General question: Are there any guidelines concerning ageing/qualification of electrical components/cables for new NPP projects? | Website | No, PAA have not prepared any specific guidelines concerning ageing/qualification of electrical components/cables yet.
PO-5 | 5 | Czech Republic | Poland | 05. Reactor Pressure Vessels | 32 | Even the scope of TPR was aimed on RPV, question is, how the evaluation of current status and residual lifetime of reactor vessel and experimental pressure channels is performed. MARIA has important system of experimental pressure channels - therefore it is expected to evaluate the status of these channels | Website | The pressure channels used in MARIA reactor are either fuel channels or experimental channels. Until 2017 NCBJ was obliged to use disposable aluminium pressure channels with the standard time of irradiation below 5880 MWh (the fuel irradiation limit set in the License). Only experimental pressure channels used for molybdenum production were used several times because of their shorter time of irradiation. There was no need to include the channels within ageing control. Since 2017 NCBJ has been given a permission to use reusable zirconium alloy pressure channels, the permission allows the increase of the standard time of irradiation up to 20000 MWh per channel for channels made from zirconium alloy – resulting in using one pressure channel for about 3 fuel elements. The R&D project including the NDE (visual inspection and leak tightness test) of fuel channels has begun in MARIA Reactor, the tests are scheduled to be performed after each irradiation in MARIA reactor. The leak tightness test of the MARIA reactor is performed as the only activity related to the management of the ageing of the reactor pool. The MARIA reactor staff together with the Materials Research Lab staff started an internal R&D programme in order to prepare the procedure for inspection of steel liner of MARIA reactor and spent fuel pool.
PO-6 | 6 | Germany | Poland | 02. Overall Ageing Management Programme requirements and implementation | 11-12 | As stated in the paragraph, so far there is no regulatory framework for ageing management in Poland. NCBJ developed an AMP and also with respect to an possibly upcoming power plant it still remains unclear, wheather PAA provides more detailed requirements (laws, decrees, regulations, guides) specifically adressing requirements for ageing management to be implemented by the licencee. What is the timeline to establish such requirements? | email | PAA is observing how licensee of RR is implementing AMP. After that PAA is going to assess final result of this process on the basis of current regulation. Final evaluation will let PAA know if any legal amendments are necessary or not.
PO-7 | 7 | Germany | Poland | 02. Overall Ageing Management Programme requirements and implementation | 15 | This paragraph states that document evaluation is performed in accordance with MARIA reactor operating documents. Which are the indicators used to assess the effectiveness of the ageing control process (ACP)? | email | The document evaluation is performed by means of current of procedures. As the paragraph states, the document evaluation is performed once every five years for system procedures and every three years for operational procedures. The process focuses on changes in the reactor design, technological processes, technical standards and conditions, quality assurance programmes or the results of internal and external audits. In Ageing Control Programme none of the indicators related to the effectiveness of ageing management is stated. The Integrated Management System for NCBJ consists of number of indicators, including indicators ageing depended indicators, that are used to assess the general performance of MARIA reactor: • Unplanned Automatic Scrams • Unit capability factor • Operation Factor • Annual cost of operation • Quality assurance of modernization and repairs • Fuel and radioactive waste performance
PO-8 | 8 | Germany | Poland | 02. Overall Ageing Management Programme requirements and implementation | 18-19 | The NAR states that the life time of the Beryllium is controlled by numerical codes. Is there a combination between these calculations and data, i.e. between core monitoring and core calcualtions? How is the ageing of the graphite blocks followed? | email | The neutron fluence core calculations are recurrently verified using, inter alia, nuclear activation measurements, and data from operation. The maximal fluence to beryllium blocks (as of 08/2013) equalled 1.2*1e22 n/cm2 and was almost 5 times lower than the acceptance criteria limit. The series of x-ray measurements of the gap between graphite and upper cap was performed in 2013. The smallest observed gap between the graphite and the upper block cap was 15 mm wide at the initial width of 30 mm. Moreover, the beryllium matrix adjoins the fuel channels making graphite blocks separate with respect to the fuel channels. Therefore the maximal fluence in graphite blocks is lower than in beryllium blocs and equalled 3*1e21 n/cm2 and was almost 2 times lower than the acceptance criteria limit. The NCBJ plans replacement of the beryllium blocks with the highest neutron fluences.
PO-9 | 9 | Germany | Poland | 02. Overall Ageing Management Programme requirements and implementation | 20 | The NAR lists some internal and external sources of operating experience. Which processes are used to incorporate the external information into MARIA's AMP? | email | The regulator assessment of ageing management processes regarding overall ageing management programme requirements and implementation shortly describes the lack of the process of incorporation of the external and internal sources of operating experience. Although the necessity of the use of internal and external operating experience was not established, it was applied to every new procedure – related or not to AMP. The senior management staff was responsible for analysis of past MARIA’s and/or other’s experience. Use of external operating experience was applied especially to broaden the knowledge gained from internal experience of MARIA’s operation or to fill the gap in case of lack of self-reported experiences.
PO-10 | 10 | Germany | Poland | 02. Overall Ageing Management Programme requirements and implementation | 21 | According to EU and IAEA SSG-25, ageing is a safety factor and hence part of the periodic safety review. Could Poland explain how the review of MARIA's AMP and the PSR are interconnected? | email | In accordance with the Regulation of the Council of Ministers of 11 February 2013 on periodic safety review of nuclear facilities, NCBJ is obliged to include AMP review in PSR for MARIA reactor. The AMP review is one of the thirteen safety factors and its scope is developed in accordance with Polish Law and IAEA Periodic Safety Review for Nuclear Power Plants SSG-25. The current status of first PSR for MARIA research reactor is to develop the guidance on reviewing this safety factor. The guidance consists of: • the purpose – short scope of goals of the assessment; • the scope – the list of the required analysis; • the methodology – description of the activities; • the criteria – list of national and international guidelines, requirements, good practices to be used in assessment; • the corresponding internal documentation – the scope of documents used in assessment; and it determines the interference with other safety factors. In the report on PSR for MARIA research reactor NCBJ shall include the necessary and proposed improvements to AMP. The report is then delivered to regulatory body for approval.
PO-11 | 11 | Netherlands | Poland | 02. Overall Ageing Management Programme requirements and implementation | 2.3.1/p14 | For the development of the overal AMP according to SSG10: what external/international experience is used? | email | The overall AMP is prepared using guidelines stated in SSG-10 and in accordance with Polish Law and the regulatory body remarks. The U.S.NRC documents and IAEA TECDOC SERIES and Safety Report Series are used as a source of international experience in ageing management programmes creation; in particular the following documents are used: • Generic Aging Lessons Learned (GALL) Report, Office of Nuclear Reactor Regulation, 2010 • SRS-82, Ageing Management for Nuclear Power Plants: International Generic Ageing Lessons Learned (IGALL), IAEA, VIENNA, 2015 • IAEA-TECDOC-1748, Project Experiences in Research Reactor Ageing Management, Modernization and Refurbishment, VIENNA, 2014 • IAEA-TECDOC-1736, Approaches to Ageing Management for Nuclear Power Plants, International Generic Ageing Lessons Learned (IGALL) Final Report, VIENNA, 2014
PO-12 | 12 | Netherlands | Poland | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2/p18 | Can the use of R&D be described more precisely? E.g. what R&D sources are used and how do they affect the AMP? | email | Although the necessity of the use of R&D in ACP was not established, R&D programmes were used especially to broaden the knowledge gained from internal experience of MARIA reactor operation or to fill the gap in the staff’s knowledge in a particular area. The main sources of R&D in the ACP of MARIA reactor are either internal R&D or R&D programmes established by other countries. The internal R&D projects currently undertaken by NCBJ are, inter alia,: The study on changes of the efficiency of Voke’s filters with time, the R&D project to prepare the procedure for inspection of steel liner of MARIA reactor and spent fuel pool. The main external R&D contributions to current ACP are either IAEA publications or IAEA facilitated publications from test facilities, other reactors and research facilities. The R&D programmes affects the technological and control instructions as well as operation and maintenance manuals – the third level documents changing the acceptance criteria, methodology of detection of ageing effects or surveillance and monitoring programmes.
PO-13 | 13 | Netherlands | Poland | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2/p18 | Please elaborate on the sources of external experience (e.g. which other nuclear instalations, international documents). | email | The main sources of external experience in ACP are IAEA publications, IAEA facilitated publications or other publications. The list is not limited to the below: • IAEA publications (TECDOCs, IAEA Nuclear Energy Series, Safety Reports Series) • Russian publications (Atomizdat, Atomic Energy), as the MARIA research reactor is designed as a twin reactor to Kurczatov MR reactor, which was located in Moscow and operated from 1964 up to 1993. • American publications (Oak Ridge National Laboratory) • Belgian publications (Centre d’Etude de l’Energie Nucleaire) Additionally, the main source of external experience for MARIA reactor staff were peer trips to Kurczatov MR reactor, including the decommissioning of MR reactor.
PO-14 | 14 | Netherlands | Poland | 02. Overall Ageing Management Programme requirements and implementation | 2.7/p22 | Has PAA considered inviting an IAEA SALTO mission? Is there an overview of those SSCs important to safety/reliabilty that have time-limitation? | email | This SALTO mission is strictly dedicated for NPPs not for RRs, that's why it was not considered in Poland yet. Yes, SSCs important to safety with time-limitation are also overviewed and they are also considered in the AMP
PO-15 | 15 | Netherlands | Poland | 03. Electrical cables | 3.1.2 / p.27 | Has any assessment of the current state of the cables been made, which meets the acceptance criteria? This could perhaps be included in the new AMP as a starting point. | email | In accordance with the Polish Construction Law the assessment of the cables shall be held at least once every 5 years. The inspections consist of checking their technical condition in accordance with the standard PN-HD 60364-6, i.e. electrical continuity test, measurement of insulation resistance of electrical installation, inspection of the effectiveness of the indirect contact protection by means of automatic power shutdown, measurement of short-circuit impedance. Although all electrical cables meet the acceptance criteria, the reactor staff is unable to determine the ageing process trends because the measurements have only been tagged as “Acceptable” or "Not-acceptable". The Manager of DEM (The MARIA Reactor Electrical Section imposed on external company new approach to document all new measurements. Future tests will be the starting point of the new AMP for cables.
PO-16 | 16 | Netherlands | Poland | 03. Electrical cables | 3.1.3 / p.28 | (Description of activities) A relatively simple measure, seen in many other NPPs and RRs, is "visible inspections". Has this been included in the new AMP? | email | The possibility of the visual inspection of SSCs was stated in ACP, however no guidelines for visual inspection for particular SSCs were stated in in ACP. Additionally, ACP does not include the acceptance criteria. All of above (if applicable) were stated in control and maintenance procedures that were not included within the ACP. The new AMP includes the visual inspection of the accessible electrical cables together with acceptance criteria.
PO-17 | 17 | Netherlands | Poland | 03. Electrical cables | 3.1.3 / p.28 | (Frequencies) According to 3.1.1, the current 'Act' has a provision that all cables are subject to inspection. For the new AMP: are there any plans to include an analysis or interpretation of historic data in order to be able to detect degradation timely? | email | Although the archiving of the protocols from ageing management tests, inspections etc. is the requirement of ACP, no analysis or interpretation of trending of the data was required. The new AMP will include both of the above mentioned provisions in order to follow the trends and to make the assessment of effectiveness of AMP possible.
PO-18 | 18 | Concealed pipework expert group | Poland | 04. Concealed pipework | P 31 | The report states that despite WNEP piping belong to the 1st safety class, it has not been included in the ageing management programme because of the difficulty to perform testing and the easy implementation of remedial action. Could Poland specify what would be the consequences to the personnel of a leak of the WNEP piping? | expert group 5 | The WNEP piping is encased in biological shield of the MARIA research reactor and they connect the fuel element channels with WNEP room. WNEP room is locked and the entrance is prohibited during the operation of the reactor. The difference of pressures between the reactor hall and WNEP room do allow controlling the possible discharges from WNEP pipes. The vacuum pressure in the WNEP room equals 10 mm H2O, the vacuum pressure in the reactor hall equals 5 mm H2O. Therefore there are no consequences to the personnel due to the leak of the WNEP piping.
PO-19 | 19 | Concealed pipework expert group | Poland | 04. Concealed pipework | 30 | The reactor operates since 1974 and the secondary piping was probably instaled at least one year before. The age of the piping is 45 years now and one would expect a degradation resulting in leaks. These leaks do not affect a safety function of the secondary piping, but they are an indicator of poor condition of piping (leak-before-break). Moreover water leaking from pin hole can remove a sand bed under buried piping and result in break of the line. Are there any measures for pipe condition assesment in place (periodical inspections, corrosion coupons tests, etc.) to get an information on pipe condition? | expert group 5 | The non-buried part of secondary piping is inspected occasionally and the last inspection took place in December 2016. The inspection results were passed to Safety Committee of NCBJ for discussion. The results of ultrasonic thickness measurement of the accessible secondary side piping were not lower than 8 mm. The inspection of the concealed part would require the soil and tar removal, what would result in new stresses to secondary piping creation. Due to foregoing neither periodical inspections nor corrosion coupons tests were assigned to concealed part of secondary piping. The MARIA reactor decided to repeat the examinations in next years in order to obtain broader knowledge about the available part of the piping and internal corrosion.
PO-20 | 20 | Concealed pipework expert group | Poland | 04. Concealed pipework | 30 | A cointainment of radioactivity during heat exchanger tube leak/rupture event is maintained by an insulation of faulty HX by isolation valves. Is a internal leak tightness of these valves included within safety functions of these valves and is this function included in their AMP? | expert group 5 | The ACP does not include the internal leak tightness of the heat exchanger valves. The heat exchanges have 4 valves each, two on primary side and two on secondary side (inlet and outlet respectively). The insulation of faulty heat exchanger can be achieved by closure of any pair. The safety functions of heat exchanger valves: • The heat removal from the fuel • The heat removal from the pool • The integrity of the primary circuit Together with the development of ACP/AMP, NCBJ was asked by regulatory body to make a revision of safety classification of SSCs in MARIA reactor.
PO-21 | 21 | Concealed pipework expert group | Poland | 04. Concealed pipework | 30 | Secondary piping is considered as class three piping, but no radioactivity is expected even in case of heat exchanger tube leak/rupture event. If no radioactivity is expected than there is no reason for class three clasification and introduction of AMP. If a faulty function of isolating valves is expected/possible, then class three is appropriate, but also an AMP/other program should be in place to maintain a function of radiocativity containment. Please explain why class three is appropriate. | expert group 5 | According to the Classification of Structures, Systems and Components of MARIA Reactor the heat exchangers are the boundaries of the primary cooling circuit and therefore are classified as class 1 components. However, low residual power enables the energy dissipation using only the primary circuit and the following auxiliary systems: demineralized water system and the radioactive effluents system. Additionally, there is a possibility of insulation of faulty heat exchanger in case of a tube leak/rupture using primary and/or secondary side valves. Due to the foregoing the main reason for classifying secondary piping as class three components is the fact that the valves are normally open and the heat exchanger is the only border between the circuits. Together with the development of ACP/AMP, NCBJ was asked by the regulatory body to make a revision of safety classification of SSCs in MARIA reactor.
PO-22 | 22 | Concealed pipework expert group | Poland | 04. Concealed pipework | 31 | WNEP system piping belongs safety class one, but it is not included in AMP. What are the safety related functions of this piping? Is it also tightness or medium transport only? What are measures/programs used for monitoring/maintaining of these functions? | expert group 5 | The primary safety function of WNEP system piping is the surveillance of tightness of aluminium cladding, the secondary safety function of WNEP system piping is the tightness of the primary cooling system. The sample from each fuel channel is taken every four hours, the WNEP valves operate at the same time regime. Only the samples from fuel channels manifold are taken in a continuous manner. As it was stated in Polish TPR, the loss of tightness concerning WNEP pipes is estimated as low risk circumstance (continuous or cyclic local leakage from primary circuit and increase in a dose rate of ionizing radiation in aerosols in WNEP room). The WNEP piping is encased in the biological shield of the MARIA research reactor and a leak may occur only in the WNEP room or the pool of MARIA reactor. The main measure used for monitoring the WNEP system condition is increase of the dose rate of ionizing radiation that indicates the leak from the WNEP system to the MARIA Reactor Operator Section and MARIA Radiological Protection Section. Additionally, the WNEP room is locked and the entrance is prohibited during the operation of the reactor. The difference of pressures between the reactor hall and the WNEP room do allow controlling the possible discharges from WNEP pipes. The vacuum pressure in WNEP room equals 10 mm H2O, the vacuum pressure in the reactor hall equals 5 mm H2O. Therefore there are no consequences to the personnel of a leak of the WNEP piping.
PO-23 | 23 | Cables expert group | Poland | 03. Electrical cables | 27 | Are any specific tests carried out on the measurement cables exposed to the high neutron and gamma radiation, as a part of the ageing management? | expert group 3 | Although the measurement cables exposed to the high neutron and/or gamma radiations are not covered in the ACP system procedure, the annual tests of current circuits are performed in accordance with Operation control procedure for MARIA reactor and I&C procedures The tests include: • Electrical continuity test • Measurement of insulation resistance • Measurement of short-circuit impedance
PO-24 | 24 | Cables expert group | Poland | 03. Electrical cables | 28 | What is the role of the “third party certification organisations” in ageing management activities, and which activities are performed by those organisation? | expert group 3 | The activities related to ageing management conducted by the third party certification organizations usually supplement testing, inspection and maintenance performed by NCBJ. The activities performed by the third party certification organizations: • Pressurizer ultrasonic examinations once every two years. The examination is performed by The Bureau of Technical Inspection • Lifting devices inspection by The Bureau of Technical Inspection • Primary circuits welds ultrasonic examination by certified external company • Measurements of parameters of electrical and I&C cables by the certificated company
PO-25 | 25 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 11 | Remark: It would be useful to iclude references for the following regulations: 'the Law of 29 November 2000 called "Atomic Law", 'Regulation of the Council of Ministers of 31 August 2012' and 'Regulation of the Council of Ministers of 11 February 2013'. | expert group 3 on other topics / expert group 1 | Yes. It should be included.
PO-26 | 26 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 11 | In the chapter 2.1. a brief national regulatory framework is described. Requirements and regulations from 2000, 2012 and 2013 are used. Is that means that WENRA RL requirements for existing Reactors (WENRA RHWG, 2014) are not taken in the current regulation? | expert group 3 on other topics / expert group 1 | Mentioned in question regulations from 2000, 2012 and 2013 were based on IAEA safety standards, WENRA Safety Objectives for New Power Reactors and EUR requirements. WENRA RL form 2014 haven’t been taken into account in this requirements.
PO-27 | 27 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 12 | In the text "Regulation of the Council of Ministers of 11 February 2013 on nuclear safety and radiological protection requirements for the stage of decommissioning of nuclear facilities and the content of a report on decommissioning of a nuclear facility" seems the requirements of the decommissioning stage are described. Further in the text: "In accordance with the scope of this Council of Ministers Regulation, periodic safety inspections...". Could you please explain, if this regulation is for the stage of decommissioning or for the operation of RR? | expert group 3 on other topics / expert group 1 | PAA listed all regulations which are linked to ageing issues to describe Polish legal framework in the context of TPR.
PO-28 | 28 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 13 | In the description is stated: ' No ageing management is provided in ACP. It will be supplemented in a new Ageing Management Programme (AMP) being implemented in the MARIA reactor, and also expanded with the missing elements. The Ageing Management Programme is supposed to replace ACP'. Please provide information about when the replacement will take place? | expert group 3 on other topics / expert group 1 | NCBJ made a request to the regulatory body for deadline extension for the new AMP for MARIA reactor. The new deadline for replacement of ACP is 15th June.
PO-29 | 29 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 13 | In the description is stated: ' No ageing management is provided in ACP. It will be supplemented in a new Ageing Management Programme (AMP) being implemented in the MARIA reactor, and also expanded with the missing elements. The Ageing Management Programme is supposed to replace ACP'. Please provide information about when the replacement will take place? | expert group 3 on other topics / expert group 1 | NCBJ made a request to the regulatory body for deadline extension for the new AMP for MARIA reactor. The new deadline for replacement of ACP is 15th June.
PO-30 | 30 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 17 | "Establishment of acceptance criteria for ageing The process of establishing criteria has not been described in the current ACP." Do you have plan to develop the process of establishing criteria for ageing in the ACP? | expert group 3 on other topics / expert group 1 | The process of establishing criteria is being developed and will be implemented with the new AMP. The main document will provide requirements for the particular procedures. The component and method specific criteria will be provided in these procedures.
PO-31 | 31 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 18 | "The process of using research and development projects was not described in the current ACP during its preparation." Please provide information about the future plan regarding this process. | expert group 3 on other topics / expert group 1 | Although the process of using research and development projects was not described in the current ACP, the area will be covered by AMP. NCBJ implements the annual evaluation of AMP in which the effectiveness of each component’s program will be evaluated. The review will include the recommendations of possible R&D programmes. Such tool enables broadening the knowledge of the ageing degradation mechanisms and methodologies for surveillance and control. The reactor manager or a person responsible for AMP will decide whether internal or external R&D programme is needed or is yet available.
PO-32 | 32 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 18 | From the description seems that the current process does not include monitoring programmes dedicated to ageing. Do you have plan to improve ACP process concerning monitoring condition indicators and parameters and trending? | expert group 3 on other topics / expert group 1 | Although the monitoring programmes are not required and covered by current ACP, some ageing related monitoring is covered by operational monitoring. The new AMP will include requirements on SSCs specific ageing management programmes to incorporate (if applicable) the condition monitoring indicators and trending. The new AMP SSCs specific ageing management programmes are structured according to generic attributes stated in IAEA SRS-82.
PO-33 | 33 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 13 | Section 2.3.1 summarises those responsibilities of those persons charged with implementation of the Ageing Control Programme. Please explain the competency requirements and training provided (with respect to ageing management) to members of the Committee conducting periodic assessment of the condition of the facility. What independent advice is available to this committee? | expert group 3 on other topics / expert group 1 | Although the requirements for the heads of the sections are not stated in Quality Assurance for MARIA Reactor, the section heads have to fulfil the requirements stated for the employees of the particular sections, the requirements are summed below: DAM (Instrumentation section) – secondary or higher technical education in the field of electronics or electrical engineering, two years of work experience in NCBJ; DEM (electrical section) – secondary or higher technical education in the field of electronics or electrical engineering, the SEP (association of Polish Electrical Engineers) eligibility for work below 1kV, one year of work experience in NCBJ; DMM (mechanical section) – secondary or higher technical education in the field of mechanical engineering or electromechanical engineering, the UDT (The Bureau of Technical Inspection) eligibility for operating lifting devices, one year of work experience in NCBJ; DDM (radiological protection section) – secondary or higher technical education in the field of electronics, electrical engineering or chemical engineering and eligibility of radiation protection officer, one year of work experience in NCBJ; All section heads have long term experience related to maintenance, periodic testing and inspection of research reactor safety systems and safety related systems. The ACP does not include any independent advice to this committee.
PO-34 | 34 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 14 | Section 2.3.1 [Methods used for identifying SSC within the scope of overall AMP] states that the selection of SSC within the scope of the ACP has been based on operating experience of the MARIA reactor. The relationship between the SSC's identified within the scope of the Ageing Control Programme(ACP) and the facility's safety analysis is not clear. Please explain the extent of the safety analysis undertaken for the facility and how this was used to identify SSC's within the scope of the ACP (or new Ageing Management Programme)? | expert group 3 on other topics / expert group 1 | In accordance with Appendix 2 of the Regulation of the Council of Ministers of 10 September 2015 on the documents required for submitting an application for a license associated with exposure to ionizing radiation or on notification on performing this activity, the SAR of MARIA reactor consists of nineteen chapters including: Introduction and general description of the MARIA reactor, Safety objectives and design criteria, Site characteristics, Buildings and structures, The reactor and its characteristics, Reactor cooling systems, Engineered safety features, I&C, Electric power, Auxiliary systems, Utilization, incl. experimental facilities, Waste management system, Radiation protection programme, Conduct of operations, Quality assurance, Safety analysis, Operational limits and conditions, Decommissioning, Emergency planning and preparedness. The safety analysis is performed in accordance with Polish Law and corresponding IAEA guidelines. The ACP does not provide the information about the use of safety analysis in identify SSCs within the scope of the ACP. The identification of the SSCs within the scope of the new AMP is based on Safety Classification of Structures, Systems and Components of MARIA Research Reactor (hereinafter referred to as Safety Classification). The Safety Classification includes 4 groups: class 1, class 2, class 3 SSCs and nonnuclear class. All class 1 and class 2 assigned SSCs are SSCs identified in AMP. Then the ageing mechanisms assessment is performed to select SSCs within the scope of AMP.
PO-35 | 35 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 18 | Section 2.3.2 [use of internal and external operating experience ] states that external operating experience is analysis to evaluate instructions. Please provide examples whereby external operating experience has been used to develop monitoring, test, sampling or inspection activities, under the Ageing Control Programme. | expert group 3 on other topics / expert group 1 | The external operating experience has been used for one procedure related to ageing management. The BR-2 experience was used to set the limits on beryllium blocks
PO-36 | 36 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 18 | Section 2.3.2 [use of R&D Programmes] states the results of internal and external R&D programmes were used to develop, verify or improve individual instructions. The extent that the facility participates or utilise external R&D of ageing management to inform these instructions is not clear. Please provide some examples of whereby R&D has been used to develop or improve the facility's monitoring, test, sampling or inspection activities. | expert group 3 on other topics / expert group 1 | The results of internal and external R&D programmes are used to develop, verify and improve individual instructions within the scope of ACP. The main examples are: • The R&D project regarding the safe gap between the graphite and the upper cap – use of radiographic method (finished project). • The R&D project regarding the effectiveness of Vokes filters (on-going project) • The R&D project in order to prepare methodology for reactor poll liner control (on-going project) • The R&D project regarding tritium discharges from beryllium blocks (on-going project)
PO-37 | 37 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 19 | Section 2.3.3. summarises the inspection programmes performed under the ageing control programme. The section highlights a number tests to measure water tightness of the reactor and storage pool leak tightness. Please explain if inspection of these components is conducted. | expert group 3 on other topics / expert group 1 | The water tightness of the reactor and storage pool leak tightness is performed at least once a year. The quarterly MARIA reactor operation reports include the list of performed activities related to tests, maintenance, inspection and repairs. The following reports include the references to the tightness test protocols: • The First quarter of 2016 MARIA reactor operation report, • The First quarter of 2017 MARIA reactor operation report, • The Third quarter of 2017 MARIA reactor operation report.
PO-38 | 38 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 19 | Section 2.3.3. summarises the inspection programmes performed under the ageing control programme. The section highlights a number tests to measure the leak tightness of the primary circuit and emergency core cooling systems. Please explain the non-destructive testing regime for these components. | expert group 3 on other topics / expert group 1 | The water tightness of the primary cooling system is continuously measured using the level of water in pressurizer. The little amount of water is constantly replenished in primary circuit due to the leakiness through the pressure channels rubber sealing. The water tightness test of the heat exchangers is carried as a part of the heat exchanger tubes cleaning procedure. The heat exchanger is moved from the heat exchanger support and placed on a special platform in the decontamination hall. After cleaning the heat exchanger pipes are flooded with water and the shell is filled with compressed air. The lack of bubbles and/or change in water level in the pipes fulfils the acceptance criteria. The pressurizer is checked using ultrasonic examinations methods once every two years. The examination is performed by the The Bureau of Technical Inspection and last tests were performed in the second quarter of 2016. There is an annual functioning test of emergency core cooling system (ECCS).
PO-39 | 39 | General AMP expert group | Poland | 02. Overall Ageing Management Programme requirements and implementation | 20 | Section 2.4 explains the systems in place to periodically evaluate the effectiveness of the ageing control programme. SSG-10 highlights that an independent assessment of the adequacy and effectiveness of an Ageing Management Programme should be conducted. Please explain how the effectiveness of the Ageing Control Programme is independently evaluated (including audits). | expert group 3 on other topics / expert group 1 | In Ageing Control Program none of the indicators related to the effectiveness of ageing management is stated. The Integrated Management System for NCBJ consists of number of indicators, including ageing dependend indicators that are used to assess the general performance of MARIA reactor: • Unplanned Automatic Scrams • Unit capability factor • Operation Factor • Annual cost of operation • Quality assurance of modernization and repairs • Fuel and radioactive waste performance The above indicators are used to periodically evaluate the effectiveness of the ACP. Although the Quality Assurance Specialist, who performs audits for MARIA reactor is independent of Operation Division (EJ2), the person designated to this position was Reactor Manager dependent. The person was also employed in Operation Division. Due to foregoing, NCBJ plans to establish the independent (from Operation Division) Quality Assurance Division.
PO-40 | 40 | EC | Poland | 01. General information | 13 | In the current MARIA reactor Ageing Control Programme, included in the System Procedure, there are no particular persons designated to be responsible for its overall implementation. What is planned in the future AMP on the level of responsibilities? |  | In accordance with SSG-10 the management of responsibility will be included in new AMP. On behalf of the MARIA Reactor Manager there will be selected a dedicated person, who is trained in ageing management, to supervise the AMP. The person will be responsible, inter alia for: • Preparing and issuing specifications and procedures for the ageing management programme • Supervising external personnel who perform ageing management activities • Supporting and participating in ageing evaluations • Addressing all relevant regulatory requirements The MARIA Reactor Manager himself will be responsible for ensuring nuclear safety and radiological protection in ageing management activities
PO-41 | 41 | EC | Poland | 01. General information | 14 | The methodologies and requirements used to assess present maintenance procedures and to develop ageing management programmes have not been included in ACP. Please clarify the methodologies and requirements that will be used in the future AMP. |  | The new AMP will set the guidelines for the SSCs specific ageing management programmes. The methodology is based on IAEA SRS-82 Ageing Management for Nuclear Power Plants: IGALL and will require the following (if applicable) chapters of SSCs specific ageing management programmes : Description and scope of the programme, preventive actions, monitoring and trending of ageing effects, detection of ageing effects, acceptance criteria, remedial actions, operating experience and references. The performance effectiveness indicators for the components are planned to develop to assess the present maintenance procedures.
PO-42 | 42 | EC | Poland | 01. General information | 20 | Principles of planning and conducting internal audits are not included in the ACP, however, they are currently included in the Integrated Management System of the National Centre for Nuclear Research. Identified as a good practice, however, this needs to be included in the future AMP. |  | Although the ACP does not include the measures related to internal audits, the new AMP will include the provisions to establish the audits process in accordance with IAEA SSG-10 guidelines.
PO-43 | 43 | EC | Poland | 01. General information | 22 | ACP guidelines do not provide any directives for assessing the quality of ageing control processes, what negatively affects the supervision of its correct implementation. Quality control of all the ACP processes and the forthcoming AMP, should be included in the system process for ageing management. / The absence of system approach to managing ageing processes results in the dispersion of documents used to control ageing and responsibility for individual programmes. |  | ACP does not include the provisions regarding the quality of the process, which results in, inter alia, dispersion of responsibility, documents and resources which should be assigned to ageing management. NCBJ is aware of these gaps and the quality assurance of new AMP will include, at least, the measures to deal with factors mentioned by IAEA SSG-10, i.e. management of responsibility, resource management, process implementation and measurement and assessment of the effectiveness of the processes within the AMP.
PO-44 | 44 | EC | Poland | 01. General information | 22 | Polish regulatory framework is constructed by prescriptive and non-prescriptive way of regulation and ... it doesn’t have precise requirements about AMP. Therefore, after the assessment, the PAA has decided to set up new the deadline for preparation of the AMP by the end of 2017 year. What is the current state of play? |  | PAA made assessment on the IAEA standards which were used by NCBJ as a basis. The Ageing Management Program was finished by the operator of RR at the end of 2017 and now is under the process of assessment by PAA.
PO-45 | 45 | EC | Poland | 01. General information | 35 | PAA identified: - a lack of assigned responsibilities to apply of overall AMP which causes that process is no coherent - the absence of tools in the current Aging Control Programme, a lack of screening and SSC identification methods - that the licensee's inspection are not fully efficient because not taking in consideration all aspects of ageing mechanisms - that the process is not sufficiently covered in existing documents Please confirm that the above issues will be fully taken into account in the future AMP. |  | The Ageing Management Program was finished by the operator of RR at the end of 2017 and now is under the process of assessment by PAA. Till the end of March 2018 the AMP is still under assessment and PAA can't confirm that all mentioned in question topics were fully taken into account.
PO-46 | 46 | EC | Poland | 01. General information | 36 | PAA considers that the effort made by the licensee gives a reasonable evidence that the process of ageing is under control and at a sufficient level - This appears not to be consistent with the content of the NAR which lists all the weaknesses and gaps of the current ACP. |  | PAA has given positive opinion about current situation in relation to ageing issues in the RR. Till now licensee had taken into consideration real evidences like operating experience and observation of SSC condition. Nevertheless PAA is aware that it is not sufficient in point of view of existing safety requirements and objectives. That's why PAA identified gaps which should be eliminated for achieving continuous improvement.
PO-47 | 47 | EC | Poland | 01. General information | 18 + 19 | The current ACP process does not include monitoring programmes dedicated to the management of ageing processes; it does not include surveillance programmes neither any guidelines for identifying all expected and unexpected degradation in the MARIA reactor. In addition, preventive and remedial actions are not included in the current ACP. This should be included in the future AMP. What is the current state of play? |  | The current ACP process does include neither monitoring and surveillance programmes nor guidelines for identifying the expected and unexpected degradation. There are no preventive and remedial actions in ACP. NCBJ is developing procedures, which will require including all of above into system procedure. The detailed guidelines will be included in ageing management programmes for specific SSCs. Although the above, the part of the monitoring, surveillance, preventive and remedial actions are dispersed within the procedures and Operation control procedure for MARIA reactor. One of the gaps identified in the self-assessment is lack of integration of procedures related to ageing management The new ageing management programmes for specific SSCs will consist of (if applicable): Description and scope of the programme, preventive actions, monitoring and trending of ageing effects, detection of ageing effects, acceptance criteria, remedial actions, quality management, operating experience and references. NCBJ made a request to the regulatory body for a deadline extension for the new AMP for MARIA reactor. The new deadline for replacement of ACP is 15th June.
PO-48 | 48 | EC | Poland | 01. General information | 23-24 | PAA already identified a lot of gaps in the official Aging Control Program in an assessment done in 2015. Licensee is aware of their weakness. These topics should be covered in the future AMP. Good practice to be aware of the weaknesses, but this was already known in 2015. What is the current state of play? |  | The Ageing Management Program was finished by the operator of RR at the end of 2017 and now is under the process of assessment by PAA.
PO-49 | 49 | EC | Poland | 01. General information | 5, 13, 22 | No ageing management is provided in ACP. It will be supplemented in a new Ageing Management Programme (AMP) being implemented in the MARIA reactor, and also expanded with the missing elements. The Ageing Management Programme is supposed to replace ACP. The deadline approved by regulatory body for developing the Ageing Management Programme was set for the end of 2017. Is this new AMP now developed and under implementation? Does it comply with IAEA guidelines? |  | The current ACP process does not include ageing management. The new AMP is now under development. NCBJ made a request to the regulatory body for a deadline extension for the new AMP for MARIA reactor. The number of measures is taken to comply with IAEA SSG-10, therefore the new deadline for replacement of ACP with AMP complying with IAEA guidelines is 15th June.
PO-50 | 50 | EC | Poland | 02. Overall Ageing Management Programme requirements and implementation | 13 | The operation Division is responsible for the ACP but nobody is globally responsible. Can you then clarify how it is managed when the inspections program is distributed between the Operations Section and the Maintenance Sections? |  | Although the current ACP does not state the person responsible for the process, in accordance with Organization Rules of Nuclear Facilities Operations Department, the MARIA Reactor Manager is responsible for reactor operation and maintenance. There is no division between the Operations Section and the Maintenance Section. The MARIA Reactor Operation Division (EJ2) is responsible for both: the operation and the maintenance. The EJ2 is divided into sections: • MARIA Reactor Operator Section (DOM) • MARIA Reactor Mechanical Section (DMM) • MARIA Reactor Electrical Section (DEM) • MARIA Reactor Radiological Protection Section (DDM) • MARIA Reactor I&C Section (DAM) • MARIA Chemical Section (PCh) The maintenance of the SSCs is assigned to particular sections of the Operation Division. The quarterly and annual reports on the utilization of MARIA reactor sum up the conducted inspection.
PO-51 | 51 | EC | Poland | 02. Overall Ageing Management Programme requirements and implementation | 17 | Acceptance criteria has not been described. Is the criteria only based on operating experience? Does it mean that only corrective actions are applied? |  | Although the current ACP does not include neither any requirements for acceptance criteria nor acceptance criteria, the acceptance criteria, preventive actions and remedial actions for some particular procedures are stated. The malfunctions of SSCs are subject to system procedure Recording and documentation of the malfunctions of SSCs of MARIA reactor (08-ZJ).
PO-52 | 52 | EC | Poland | 03. Electrical cables | Generic 25-30 | Although cable AMP is not yet in place, current inspection and testing activities are clearly described. |  | Thank you for remarks.
PO-53 | 53 | EC | Poland | 04. Concealed pipework | 30-32 | MARIA Research Reactor: How long is the buried section of the secondary coolant circuit pipework and is the non-buried part inspected occasionally? |  | The buried part of secondary piping starts at the edge of R2/D building (Decontamination hall) up to the buried manifold is placed between cooling towers. Then the buried pipe routing heads to building 32a (pump hall) and the last part of the piping heads to the edge of R2/D building. In accordance with the document Secondary piping for external routing for building R2/C and 32/32d, the length of the buried parts of piping equals about 80 meters. The non-buried part is inspected occasionally; the last inspection took place in December 2016.
PO-54 | 54 | Marcin Harembki, Association 'Common Earth', Poland | Poland | 01. General information | All | Our general, horizontal and overarching remark about the report (NAR) is that the English language employed within it - though seemingly, overall correct, at least at a certain level of usefulness for very advanced experts and specialized engineers - is, at times and at certain important spots, quite poor. Therefore, we made an official request to PAA to obtain a possibly available Polish language version of the document but received a response which claimed that it (NAR) had been prepared in English only with the WENRA requirements given as the reason. However, this particular requirement does not prohibit preparing the NAR also / originally in any other language, including in the national / native language(s). Moreover, we think that parts of the NAR may have been prepared by PAA or by NCBJ ('Maria' reactor licensee) in Polish language anyway, so we should have theoretically received them in one form or another. This (the Polish "feed") can be assessed / scented from a Polish and Polish-specific administrative dull language style which is "surfacing" from the background of the "English" shape of the report. Exactly this style adds to the incomprehensiveness of large parts of the NAR. A poor translation / version of (any) NAR, the Polish one in particular, renders it for us impossible to even effectively try to understand the very complex matter which is operation of a (research, here) reactor and, the more, aging processes which impact it and take place all the way through as well as related issues (on the top of it). This mode of proceeding makes readers of NAR unable also to identify important elements, including names of some documents referred to within, in their original language. e.g. the term "ageing management programme" (this should be solved e.g. through giving the Polish version of the titles of such documents at least in the glossary). In consequence, overall the poor English of NAR runs counter to the objectives of the entire 'Topical Peer Review' within the Polish part. Therefore, we think that NAR should be (and should have been) prepared along a "two languages track", because the nuclear institutions' (regulator's and licencees') working and administrative language, not mentioning that of the society at large as well as of minor public and civic stakeholders, is predominantly their respective native language, which most often is not English. In the Polish particular case, at this stage, we demand that the whole NAR be proof-read by an English native-speaker expert, and, in such an improved form, be presented to the large public for consultations - anew. Also, the final version of the NAR (after consultations) should be presented in the Polish language as well. * Our material comment refers to the installations listed in the NAR. While, of all installations, it is only one research reactor operated ('Maria') which is being assessed in the NAR under the Topical Peer Review's criteria, all the other installations should at least be listed and justifications of them not having been analysed within the NAR should be stated. In the Polish law, among nuclear installations there are also spent fuel pools and NCBJ operates two (so called facilities 19 and 19A): http://nuclear.pl/polska,przechowalniki,przechowalniki-wypalonego-paliwa.html . The pools may not contain any spent fuel rods at the moment, yet, but likely they could do so in the future, because the GTRI agreement, not valid any more, will not function as a vehicle to rid this specific high-level radioactive waste bringing them "back" to "the country of origin", and at the moment, at least part of the assemblies used comes from within the EU (specifically from a French suppplier)", as far as we understand. In that wise, and in that manner, one decomissioned reactor, named 'Ewa', should be treated. It has been dismantled (albeit "to the brown field" only) and should be listed and explained as well. |  | As English is working language for evaluators and mutual discussion, all country reports submitted to the European Commission were in English to avoid translations by the Commission services. The TPR report of Poland exists only in English version. There were two types of nuclear installations agreed by ENSREG to be count in national reports: 1. Nuclear Power Plant, 2. Research reactor with a thermal power of 1 MW or more. Only Research Reactor MARIA (30 MW) at the Research Center in Świerk meets this criteria.
SE-1 | 1 | Slovak Republic | Sweden | 01. General information | Pages - general | Is there a licensee´s ageing management database in place? How is it structured? Does it include acceptance criteria and trending to decide on the required steps for corrective actions? | Website | Forsmark has various data bases, but there is ongoing work to integrate different bits of data regarding ageing management in a consistent way. Oskarshamn states that, the data used comes from different databases/reports. In the LTO-project "databases" is an area that will be discussed to see if its possible to improve this area. Ringhals states that a database exsists where the result from the scoping is located. It is planed to take this information in to the Plant Register (anläggningsregistret). However the analysis is dealt with in SUP's, strategic maintenace plans. The SUP documents contain the commodity group's history, analysis, ageing program, status, R&D and operational experience. The maintenace plans are transfered to the Plant Register (anläggningsregistret) that are the main tool for maintenance activities
SE-2 | 2 | Slovenia | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 9 | Scope of the overall (Page 9): How are PSA analyses used for scoping of SSCs included in AMP in Forsmark and Ringhals? Is scope of SSCs based on PSA added to original AMP scope of SSCs, using IGALL, GALL or similar approach for scoping? | Website | Forsmark states that any component analyzed to have a FC (Fractional Contribution) greater then 10^-3 or a RIF (Risk Increase Factor) larger then 10 is included in the scope of AMP in Forsmark. IGALL and GALL was used as a quality reference when assessing the relevant TLAA:s to be performed for LTO. Ringhals states that each units SAR documentation defines the safety and suporting functions, this is used as a basis. Additional SSC's are found by using both an expert group and the identification of increased risk factors by PSA.
SE-3 | 3 | Slovenia | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 34-35 | SSM experience from regulatory oversight (Page 34-35): Do licensees also periodically report to the SSM, regarding AMP programs implementation or is complete oversight by the SSM conducted through large scope of inspections dedicated to AMP? Does SSM reviews and confirms individual AMP programs and new revisions of the programs? | Website | There are no requirements that indicate that licensees regularly should report aging management implementation to SSM. Surveillance of aging management is performed by SSM based on the inspection program. Outcome from these inspections have resulted in injunctions with requirements for accounting from licensees.
SE-4 | 4 | Czech Republic | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 10, 11 | "Ringhals uses the Preventive Maintenance Basis Database (PMBD) … For components covered by EPRI PMBD the specified degradation mechanisms should be used." Were in Ringhlas used also another information sources for identification of significant ageing mechanisms and appropriate ageing management programmes? EPRI PMBD doesn't contain sufficient information for some pasive components (e. g. pipelines). Which methodology and requirements for evaluation of the existing maintenance practices and developing of ageing programmes appropriate for the identified significant ageing mechanism was used for these components? | Website | Ringhals states that all active mechanical components are managed within the SRCM program (Streamlined Reliability Centered Maintenance) and the EPRI PMBD forms the object specific basis for this program. The ageing management process for active components including the SRCM program ensures that each active component is inspected, serviced or repleced in specified time intervals according to an optimized maintenance program. It is considered that e. g. a valve consist of active parts and a passive part, the valve body is considered as a passive part. All passive parts are managed in a separate process. Passive mechanical components are analysed on an object level, this is documented in component specific Ageing Analysis. The fundamental degradation mechanisms for passive components are retrieved from a number of EPRI documents: - EPRI Materials Degradation Matrix (MDM) - EPRI PWR Issue Management Tables (MRP-205) - EPRI Non -Class 1 Mechanical Implementation Guideline and Mechanical Tools Ringhals uses EPRI knowledge only as a basis regarding degradation mechanisms, a Ringhals evaluation and in-house knowledge are added to this. The final chapter in the Ageing Analysis is an evaluation of applicable ageing management programs. A set of relevant Ageing Management Programs are linked to each mechanical object. The Ageing management programs are based on the NUREG 1801 AMP's but converted to Ringhals specific programs.
SE-5 | 5 | Bulgaria | Sweden | 02. Overall Ageing Management Programme requirements and implementation | p. 31 | In the last two paragraphs the regulator SSM stated that the quality management of the ageing management program was not used in а systematic way by all Swedish licensees. Although the regulator considered this as a weakness, in the report was not clear stated when that will be implemented completely. Would you please give the SSM opinion of when quality management will be implemented fully at all licensees programs? | Website | SSM believes that the systematic in quality management of the aging management program can be developed. SSM does not consider that there is a major deficiency today, but in order to improve the quality management of aging, it is primarily the systematic in quality management who needs improvement.
SE-6 | 6 | Netherlands | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2/p12 | Do manufacturing documents play no role in assessing ageing? | email | All licensees states yes, manufacturing methods and data play an important role in establishing ageing management. For example all material data is taken from manufacturing documents. The licensees have spent lot of resources in gathering manufacturing documentation to make it complete. In several cases it was necessary to contact the original supplier to obtain a complete documentation. The manufacturing documentation and history is an essential part and forms the basis of the the component specific Ageing Analysis report.
SE-7 | 7 | Netherlands | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2/p15 | Unclear is the Swedish participation in or use of results of international R&D programmes. Can examples be provided? | email | Forsmark is a member of EPRI, IGALL-project, ENERGIFORSK R&D. See more examples in F-0053469, section 1.2.2. Oskarshamn is participating in for example, Comrade and IGALL. Ringhals ha a long list of R&D prorammes; EC-Project: SOTERIA, Nugenia. EPRI-Project: BWRVIP, MRP, PSCR – Primary System Corrosion Research, IASCC review panel/expert group, Alloy 690 expert panel, SGMP, Chemistry program, FRP (Fuel reliability Program) Others: ASTM E10, IAC-IASCC, ICG-EAC, IGRDM, Halden projektet, HRP, PWROG, NIWEL, FROG, Energiforsk
SE-8 | 8 | Netherlands | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2/p16-17 | Is external experience from the IAEA IRS database used? Are events shared by contributing to that database? | email | All three licensees states yes. Forsmark use both internal and external experience to establish new and update existing ageing management. Oskarshamn uses the reports from the IRS database in our regular experience evaluation and reports significant events to our authority, SSM, who is then responsible for reporting to the IRS. Ringhals Operating Experience process ensures that several different international OE databases are monitored continuously, the IAEA database is one of them. New event reports are incorporated into Ringhals internal OE databas and processed in the organisation. Ringhals intention is to share internal events and contribute to international OE databases, mainly through WANO.
SE-9 | 9 | Netherlands | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 2.4/p24 | Please elaborate on the strategic participation in R&D forums. E.g. which ones are participated in. | email | Forsmark is a member of EPRI, IGALL-project, ENERGIFORSK R&D. See more examples in F-0053469, section 1.2.2. Oskarshamn is participating in for example, FORSAMP, Energiforsk, Comrade and IGALL. Ringhals ha a long list of R&D prorammes; EC-Project: SOTERIA, Nugenia. EPRI-Project: BWRVIP, MRP, PSCR – Primary System Corrosion Research, IASCC review panel/expert group, Alloy 690 expert panel, SGMP, Chemistry program, FRP (Fuel reliability Program) Others: ASTM E10, IAC-IASCC, ICG-EAC, IGRDM, Halden projektet, HRP, PWROG, NIWEL, FROG, Energiforsk
SE-10 | 10 | Concrete containment PCPV expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 15 | 2.3.1 How to use probabilistic safety analyses (PSA) to identify SSC within the scope of overall AMP ? (especially for containment) | expert group 4 | At Forsmark any component analyzed to have a FC (Fractional Contribution) greater then 10^-3 or a RIF (Risk Increase Factor) larger then 10 is included in the scope of AMP. Ringhals states that buildings that supports and shields systems important for safety are included in the classification list. The selection of building is done based on the classification list. From the beginning only the containment were included within the scope of civil structures important for safety. For the containment there is analyses for highest allowed pressure inside the containment. The analyses is based on that a certain level of tension in the prestressed tendons. Testing of tendons are therefore important.
SE-11 | 11 | Concrete containment PCPV expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 17 | 2.3.1 How to be assured the processing of data with the BiCycle system? (Interesting, and it can be a useful example for everyone) | expert group 4 | At Forsmark BiCycle copies the data once a week from the maintenance database and there is no possibility to corrupt or change the raw-data in BiCycle and there is no transfer of data back to the maintenance database. At Oskarshamn the maintenance information in BI-Cycle is a copy of the quality assured information of the Computerized Maintenance Management System, ODU, which is a Master System. At Ringhals the evaluation is done on data taken from the Plant Register (anläggningsregistret) and Error Reprting (felanmälan). Maintenence for civil structures have used BiCycle to trend doors and surface treatments (coating). The amount of reported errors has also been trended.
SE-12 | 12 | Concrete containment PCPV expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 17 | 2.3.1 Can the cause of failure always be determined, defined? | expert group 4 | SSMs regulations are clear in this case, it is mandatory to make a root cause analysis on safety related mechanical components. The root cause can not always be determined. In Forsmark there is a routine to always investigate the root causes of any significant malfunction. Oskarshamn states that is possible in most cases. Oskarshamn uses an established procedure for root cause analyzes. Ringhals states not always. But if the the cause of failure is not clear for a safety related mechanical component it is not possible to continue operation.
SE-13 | 13 | Concrete containment PCPV expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 17 | 2.3.1 What does KPI mean ? | expert group 4 | Key Performance Indicator is a type of performance measurement. KPIs evaluate the success of an organization or of a particular activity (such as projects, programs, products and other initiatives) in which it engages.
SE-14 | 14 | General AMP expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 35 | 2.7.2: regulation in 2008, but due to regulatory merger same year no clear directions for the operators were given until recently | expert group 3 on other topics / expert group 1 | As a result of the great work with the merger of two authorities in 2008, there were some areas that had less supervision over a few years, of which ageing management was such an area.
SE-15 | 15 | General AMP expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 36 | 2.7.3: two operators have tried to systematize knowledge of components and their conditions as well as experiences gained during operation into a basis for ageing programs, one has taken an overall ageing program “expert system” as a basis for developing an ageing program. | expert group 3 on other topics / expert group 1 | Yes that is correct. Oskarshamn is the licensee that has choosen the "expert system" as a basis for the ageing analyzis. Oskarshamn will in the frame of LTO project take further actions to improve the analyzis.
SE-16 | 16 | General AMP expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 12 | Has a dedicated plant programme to manage technological obsolescence been developed and implemented? | expert group 3 on other topics / expert group 1 | Forsmark states thas they has an established spare parts strategy that clearly defines that the organization should work proactively with obsolescence. This goal is achieved at Forsmark by implementing Rolls-Royce Proactive Obsolescence Management System (POMS) during 2018 and establish methods and tools. At Oskarshamn it was implemented a programme in the end of last year and is now running. The base in the program is POMS provided by RollsRoyce. At Ringhals the programme and a specific group with a dedicated manager are in place since 2 years. The obsolescence program is based on the POMS.
SE-17 | 17 | General AMP expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 4 | Are there established regulatory requirement for the report of implementation of AMP? | expert group 3 on other topics / expert group 1 | Swedish regulations SSMFS 2008:1 Chapter 5 Section 3. The requirement on ageing management states that a programme for management of ageing degradation and damage shall be in place. The programme shall be documented, reviewed and updated in the light of experience gained in science and technology as well as developments. General advice to this requirement further specifies that the programme for the management of ageing degradation and damage should comprise the identification, monitoring, handling and documentation of all the ageing mechanisms that can affect structures, systems and components as well as other devices that are of importance for safety. Additional guidance on maintenance and the management of ageing degradation can be found in the IAEA:s safety standard on maintenance, surveillance and in-service inspection in nuclear power plants. The general advice refers to IAEA’s safety standards with regard to ageing management (NS-G-2.12 and safety report 57
SE-18 | 18 | General AMP expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation |  | Has a dedicated specific ageing management programmes for elements and ageing mechanisms? | expert group 3 on other topics / expert group 1 | Forsmark states that they has a dedicated ageing management program for elements and ageing mechanism. Oskarshamn has developed 30 AMP:s which mostly are devided in component group/ageing effect. Ringhals states that relevant and object specific ageing mechanisms are evaluated and defined in the Ageing Analysis report. The final chapter in the Ageing Analysis is an evaluation of applicable ageing management programs. A set of relevant Ageing Management Programs are linked to each mechanical object to manage the identified ageing mechanisms. The Ageing management programs are based on the NUREG 1801 AMP's but converted to Ringhals specific programs.
SE-19 | 19 | General AMP expert group | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 32 | Concerning establishment of acceptance criteria that the SSCs shall maintain their intended function during design basis events. Is it include the severe accident? | expert group 3 on other topics / expert group 1 | All licensee states yes. Equipment intended to manage severe accidents are in scope of ageing management.
SE-20 | 20 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 9 | Isn't the check that all required systems are covered by the OAMP necessary regardless of LTO preparation? |  | All three licensees states yes. The LTO-preparation consists of an independent review of existing ageing management.
SE-21 | 21 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 9 | The use of a simplified AMP in Ringhals needs to be elaborated on. How does it differ from a normal AMP? What criteria does it have to meet? How often is it reviewed? How is its effectiveness estimated? |  | The wording of this paragraph is incorrect, "simplified Ageing Management Programs" does'nt exist at Ringhals. The final Paragraph at page 9 may be replaced by the following: The Streamlined Reliability Centered Maintenance program (SRCM) ensures that each active component are repleced or serviced in specified time intervals according to an optimized maintenance program. In addition to this answer, please see the answer to question "02. Overall Ageing managment program requiremets and implementation page 10,11". | ref to SE-2
SE-22 | 22 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 9 | In the safety case to be prepared for LTO beyond the design life of 40 years, what additional safety demonstration is required to be provided for the age limiting mechanisms and the criteria to be met? How will the AMP be modified to cover the period of the LTO, for example a increase in ISI frequency? Is a specific scoping of SSCs carried out for LTO as part of the review of the AMP? |  | Forsmark states that to ensure safe operation beyond the original design life (LTO), the current licensing basis documentation is assessed for any existing time limited analysis (TLAA) to be re-evaluated for the extended time frame of operation. An independent assessment for any necessary additional TLAA:s is performed by the evaluation of USNRC GALL-report, IAEA IGALL and Swedish regulator (SSM) reference reports. In general, existing AMP:s will be re-evaluated for LTO to ensure that they are viable in managing of relevant ageing effects for the extended period of operation (LTO). In particular, the ISI program is continuously being re-evaluated in accordance to Swedish regulatory requirements to ensure that any increase in risk of damage due to ageing mechanisms is continuously managed over time, which also includes LTO. For the evaluation of AM for LTO, the scope of SSCs is specifically set in accordance with the criteria specified in IAEA SSG-48 (IAEA SRS No.57). Oskarshamn states that there are no specific regulatory requirements for LTO in Sweden. In OKG the LTO project will verify that the overall Ageing Management will fullfill its tasks in the LTO period. If we find gaps in the verification, update of e.g. component AMP:s could be necessary. The LTO project will also verify that the scope is sufficent regarding the regulatory requirements for ageing management. Ringhals states that the ageing management is a living program regardless if an LTO period is entered or not. The ISI frequency is depending on the needs and regardless of whether you are at the beginning of life or in a LTO period. The ISI frequency is continually reviewed in the Ageing Analysis report and if needed it will be adjusted based on the latest knowledge.
SE-23 | 23 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 11 | Ringhals use of the term Ageing Analysis instead of OAM may lead to some confusion as Management suggests a broader range of activities one of which could be analysis. |  | Ringhals states that in this context the abbreviation OAM is interpreted as the Overall Ageing Management Program (OAMP). The international nuclear industry including authorities has not succeded to establish common and clear definitions within the field of ageing management. The lack of clear international definitions and guidelines results in this kind of confusion. At Ringhals the OAMP exists and it describes how the Ageing Management is implemented in the company at a high level, much like a "general or umbrella program" as described in WENRA Technical Specification, chapter 00.2. The Ageing Analysis report is a component specific document type. These Ageing Analysis reports contain very detailed information about design and manufacturing (for example repair, pre-service inspection), operational and operating information (for example transients, chemistry, defects and repair), ageing analysis conclusions (for example new inspection or maintenance actions). In other words, the Ageing Analysis is not a program. According to the IAEA one of the fundamentals is to "understand ageing". This is in the Ringhals case documented in the Ageing Analysis. When the understanding of ageing is documented down to an object level the next step is to connect a set of relevant Ageing Management Programs to each mechanical object. The Ageing management programs are based on the NUREG 1801 AMP's but converted to Ringhals specific programs.
SE-24 | 24 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 11 | When are the indicators for assessing the effectiveness of the AMP expected to be finalised and applied by Forsmark? |  | Forsmark states that the indicators will be in place by the end of year 2018.
SE-25 | 25 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 11 | It is not clear which parameters are evaluated in the procedure described by Ringhals under the sub-section 'Quality assurance...' |  | Ringhals states that for LER's and production losses, reports are made with analysis of the fault. The KPI's follow LER and production loss.
SE-26 | 26 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 15 | The development of metrics used for measurement of AMP effectiveness is indeed an area with a lot of room for improvement. This is why the relevant new task within the FORSAMP group is highly appreciated. |  | Thank you. We agree! The FORSAMP meatings are held two times a year and there are extra focus meatings when needed. The measurement of AMP effectiveness is one of the current topics.
SE-27 | 27 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 21 | SSM perspective on the topic of licensee audit and inspection findings implementation would be appreciated. |  | SSM has carried out various supervisory efforts and verified how license holders take care of identified measures and improvement opportunities. All license holders have well-developed systems to handle corrective actions, and SSM believes they deal with deficiencies in a satisfactory manner. There are improvement opportunities for all license holders in different areas. These are followed up by the SSM in the supervision program.
SE-28 | 28 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 23 | Establishing a procedure to be applied to a systematic analysis of potential ageing effects at plant modifications is identified by Oskarshamn as an area for improvement. It is indeed worth exploring. |  | Oskarshamn states that the procedure for this will be set during 2018.
SE-29 | 29 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 23 | It would be appreciated if Oskarshamn could provide a reference and their rational for using the performance indicator 'a' as described on page 23. |  | Oskarshamn states that a=number of ageing related fault reports, in percentage
SE-30 | 30 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 27 | It would be appreciated if Forsmark and Oskarshamn could provide the periods at which evaluation is performed. |  | Forsmark states that annual reporting per reactor block will be performed as part of evaluation of key performance numbers. Oskarshamn states that the index is updated monthly as written.
SE-31 | 31 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 31 | Does SSM apply any criteria for evaluating the correctness of relating a certain fault to ageing, as described in Oskarshamn's parameter 'a' ? |  | SSM can in our supervision conduct a sample to check if the errors are ageing-related or not. Experienced experts performs the supervision with knowledge from for example results of R & D.
SE-32 | 32 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 32 | Does SSM intend to issue guidance on the use of more specific criteria for evaluating the need for corrective actions? |  | At present, a major development project is underway, where SSM develops new requirements. To these requirements, guidance text will be supported to support the application of the requirements.
SE-33 | 33 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 33 | Is the implementation of a fully compliant OAMP a condition for regulatory approval of 'continued operation' ? |  | SSM does not give approval for continued operation. The permission for the licensee is unlimited. However, in connection with the PSR that occurs when the facility becomes older than 40 years, adjustments are made in the review of PSR, taking into account that the plant can continue to operate beyond original lifetime. SSM requires the licensees to have an OAMP, and this is checked during the PSR review. SSM takes decisions on action if there are requirements that the licensee does not meet. What kind of action depends on the extent of the deficiency of safety. So if SSM finds that the licensees OAMP is not satisfactory and it does not meet the requirements and this means a serious safety deficiency, then SSM can for example decide on special operating conditions.
SE-34 | 34 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 35 | In light of the realisations listed as reasons for misalignment between SSMs expectations and licensees view regarding ageing management, what does the regulator intend to undertake? |  | SSM assumes that the improvement opportunities identified in this work are addressed by the licensees. This will be followed up by future supervision.
SE-35 | 35 | EC | Sweden | 02. Overall Ageing Management Programme requirements and implementation | 35 | What is the current status of OAMP implementation at Oskarshamn? |  | SSM assessment is that Oskarshamn now has an implemented aging management program for all SSC belonging to safety class 1 and 2. Oskarshamn shall, by 31 January 2019, introduce a complete program for dealing with age-related impairments and injuries for the other SSC included in O3's age management program. Oskarshamn will also take into account how local environments can affect the company's management of age-related impairments and injuries based on analysis of results from more detailed plant utilization, as well as introducing an obsolescence sub-program for all SSC.
SE-36 | 36 | United Kingdom | Sweden | 03. Electrical cables | 47 | Section 3.1.2 highlights that Ringhals find it difficult to find applicable criteria for the requalification of cables but on the previous page Forsmark Unit 3 notes that they completed the self same exercise in 2012. Can this process not be shared between the stations? | Website | Ringhals states that the text "criteria for requalification" in the Swedish NAR report is not correct. Ringhals means here that it is difficult to find applicable acceptance criteria for assessment of cable status with use of non destructive metod (Indenter), which is in correlation to EAB 50%. (Ringhals and Forsmark are cooperating in qualifications or requalifications issues.)
SE-37 | 37 | United Kingdom | Sweden | 03. Electrical cables | 51 | Section 3.1.3 highlights that Forsmark use of pass criteria of insulation resistance of greater than 100MOhm. Does the station take into account cable length or is this ignored? | Website | Forsmark states that its a conservative value and simple to use. It's the same acceptance criteria but more conservative to use then to apply also the actual length of the cable.
SE-38 | 38 | Switzerland | Sweden | 03. Electrical cables | 30 | Textline24: What are the specific requirements/guidelines from the authority to the licences concerning AM? What about specific IAEA guidelines i.e. TecDoc 1188/1402? | Website | Swedish regulations SSMFS 2008:1 Chapter 5 Section 3. The requirement on ageing management states that a programme for management of ageing degradation and damage shall be in place. The programme shall be documented, reviewed and updated in the light of experience gained in science and technology as well as developments. General advice to this requirement further specifies that the programme for the management of ageing degradation and damage should comprise the identification, monitoring, handling and documentation of all the ageing mechanisms that can affect structures, systems and components as well as other devices that are of importance for safety. Additional guidance on maintenance and the management of ageing degradation can be found in the IAEA:s safety standard on maintenance, surveillance and in-service inspection in nuclear power plants. The general advice refers to IAEA’s safety standards with regard to ageing management (NS-G-2.12 and safety report 57
SE-39 | 39 | Switzerland | Sweden | 03. Electrical cables | 51 | Textline4: "OIT is a method used for qualification." - Might it be used for trend monitoring too? | Website | Forsmark does not use the OIT factor for trending degradation. The OIT value could only tell the start of ageing degradation. It's not applicable for trending actual degradation of a cable and does not assess the actual condition of the polymer material.
SE-40 | 40 | Czech Republic | Sweden | 03. Electrical cables | 52 | 3.1.3 Ringhals, p 52 "Outside the reactor proper actions need to be taken when the temperature is above 30 °C on cable raceway. Inside the reactor containment the corresponding temperature is above 55 °C." What is the basis for defining of this temperatures. | Website | Ringhals states that the normal temperature outside containment is 18 to 35 °C. Many of our cables outside containment are of PVC material, which is degrading faster in temperatur higher than 30 °C (KTH Royal Institute of Technology report). The normal temperatur inside containment is 30 to 74 °C. A majority of all cables are in an environment lower than 55 °C.
SE-41 | 41 | Netherlands | Sweden | 03. Electrical cables | 3.1.1 | In section 3.1.1, It is stated that for Forsmark, there is no single document describing the overall processes and procedures of AMP on electrical cables, but that there is ongoing work to establish such an AMP. However, in the next paragraph it is stated that all class 1E cables are considered in the Forsmark AMP of cables. Please explain this discrepancy. | email | Forsmark states that all 1E cables WILL be a part of the scope in the ongoing development of an cable AMP. It is however not yet fully established and implemented
SE-42 | 42 | Netherlands | Sweden | 03. Electrical cables | 3.1.1, p.42 | In table 4, the Forsmark cable group >1kV to 36kV is correlated to the TPR grouping of Medium voltage. As these cables are primary 6kV and 10kV, should they not be correlated with the TPR high voltage cables (>3kV)? Same for Ringhals 6kV cables. | email | No. For Swedish definitions and grouping for AM, this is sufficient.
SE-43 | 43 | Netherlands | Sweden | 03. Electrical cables | 3.1.1, p.43 | For Forsmark, the 400kV power lines are excluded from the scope of the NAR as it is stated that these are not cables due to the lack of an insulating coating. However, as ageing of the conductor itself is part of the scope as specified in the TPR technical specification, and these power lines are vital for the safe operation of the power plant, should they not be included in the NAR? | email | Forsmark states that the 400 kV power lines is not in scope for safety regarding AM.
SE-44 | 44 | Netherlands | Sweden | 03. Electrical cables | 3.1.2 | At Ringhals, the important ageing stressors are temperature, radiation and moisture/water. At Forsmark, only temperature and radiation are considered important. Why this difference, especially as all relevant degradation mechanisms are established nation wide in the FORSAMP framework? | email | Forsmark states that during normal operation, the ASEA BWR design has no safety related cables routed in high humidity or submerged in water, therefore FKA has no focus on moisture as an important degradation stressor. Forsmark does, however include water and moisture/steam as an ageing stressor in all AMR studies of SSCs. Ringhals has 6 kV cables outside in sealed cable trenches, where moisture/water might appear.
SE-45 | 45 | Cables expert group | Sweden | 03. Electrical cables | Chapter 3.1.3 | Are there PVC insulated cables still available at Swedish NPPs? If yes, is there a plan to replace those cables in the future | expert group 3 | Forsmark has a lot of PVC insulated cables. There is no plan for a general exchange of these cables. Forsmark have seen few signs of general degradation of these cables in mild environment. Oskarshamn states yes. we still have PVC cables installed. An analysis of the cables has been made, regarding the actual enviromental values of temperature and radiation. This analysis shows that these cables will continue to function for at least 60 years totally, according to the environmental values . If a change in environmental values is noticed, a new analysis will be made. At Ringhals 1 there are some PVC cables inside containment, but we have no plans to replace those cables. Ringhals 1 will shut down 2020. At Ringhals 2, 3 and 4 there are also PVC cables inside containment, but no one in safety classes. Outside containment there are PVC cables in all 4 unit, but we have no plans to replace those cables.
SE-46 | 46 | Cables expert group | Sweden | 03. Electrical cables | 39/57 | It appears that the AMP for cables Forsmark NPPs and Oskarshamn NPPs are not yet implemented. When will be the AMP for cables be fully implemented for these NPPs? | expert group 3 | The AMP for electrical cables in Forsmark will be in place by the end of year 2018. Oskarshamn states that the AMPs were finished during September 2017, but according to the analysis the main focus will be to measure and analyze the environmental values.
SE-47 | 47 | Cables expert group | Sweden | 03. Electrical cables | 39 | From the National report it appears that the AMP for cables at Forsmark and Ringhals are primarily based on the IAEA Safety Guide NS-G-2.12. This IAEA safety guide is general, and might not contains all the guidance necessary for a comprehensive AMP. Have the documents providing more specifics been used ( e.g. iGALL, NUREGs, NEI/ EPRI documents, etc.…). | expert group 3 | Forsmark statest that the general approach to AM for cables are based on NS-G-2.12, as for all other AM in Forsmark. Specific programs, such as for electrical cables, are based om component specific guidance. Forsmark is continuously following what EPRI, IEEE and IEC are developing with regard to AM / AMP's. Ringhals states that the general approach for ageing management is based on NS-G-2.12. AMP for cables is based on our accumulated knowledge about cables. It includes also internal and external experiencies, guidelines and research results.
SE-48 | 48 | Cables expert group | Sweden | 03. Electrical cables | 52 | The National reports stated that is not possible to perform visual check/inspection of inaccessible cables. Which methods are used in Sweden for the verification of degradation on inaccessible cables? What is a general operating experience with inaccessible cables? | expert group 3 | Forsmark states that inaccessible cables inside containment all have a qualified life. Testing of inaccessible cable are generally performed by TDR (Time Domain Reflectometry) measurements and isolation resistance measuring. General good OE from cable degradation, which also includes inaccessible cables. Oskarshamn states that some of these cables are monitored with closed circuit current, which if interrupted alerts an alarm in the control room. OKG also perform isolation resistance measurement on cables, during maintenance work. Ringhals states that for NIS cables we use insulation resistance and TDR measuring. For other inaccessible cables we use insultation resistance, LIRA or Tan/Delta testing where applicable. We have very few fault reports concerning cables.
SE-49 | 49 | Cables expert group | Sweden | 03. Electrical cables | 60 | Oskarshamn 3 replaced all the cables in containment in 2013/14 . What were the reasons for replacing cables (i.e. observed degradation or precaution)? Have comparable replacements been made at other NPPs. | expert group 3 | Forsmark states that some replacements of safety related cables has been made at Forsmark 1 & 2 due to extended life time qualification inability, but no extensive replacements at Forsmark 3. Focus has been on requalification of existing cables. Oskarshamn states that the reason for the change was precaution, in order to extend plant life time. Ringhals states that a majority of all cables inside the containment at Ringhals 1 and 2 are replaced. At Ringhals 3 and 4 we have plans to replace some cables. The rest of the cables are qualified for the remaining life time of the unit, or will be requalified or replaced when their qualified life time are reached.
SE-50 | 50 | Cables expert group | Sweden | 03. Electrical cables | 45 | The 250 V cables that used for control purposes, appear to be, at Oskarsham, qualified for only 15 years. Are these cables being replaced every 15 years? | expert group 3 | Oskarshamn states that the qualified life time for these cables is 15 years, according to the qualification report. The 15 years are based upon a normal operation environment with temperature at 55°C and radiation at 40 mGy/h. The analysis has shown that such environmental values don´t exists where these cables are installed, so therefore an extention of the qualified life time is made.
SE-51 | 51 | EC | Sweden | 03. Electrical cables | 47 | Oskarshamn does not seem to have AMP for cables, but under development. Is it possible to get any information on the bases and main features for the planned AMP, e.g. regarding monitoring and testing activities, cable deposits? |  | Oskarshamn states that the main activities in AMP for cables: - Visual inspection during normal monitoring - Visual inspection while performing maintenance work on connected equipment - Closed current circuit - Isolation resistance measurement Other activities: - Tests on old cables - Environmental controls (not just for cables)
SE-52 | 52 | EC | Sweden | 03. Electrical cables | 53 | Does Ringhals have any cable deposits for ageing follow-up? |  | Ringhals states that they don´t have cable deposits. Instead we use accelerated ageing of cables.
SE-53 | 53 | EC | Sweden | 03. Electrical cables | 46, 51 | Regarding cable specimens inside containment and EAB measurement for ageing follow-up at Forsmark, could you give further details of the surveillance programme (since when, frequency of sampling)? |  | Forsmark states that the cable surveillance program at Forsmark 3 has come to an end, as specified. Forsmark made a complete re-qualification of the majority of the in-containment cables. Cable specimen surveillance program for Forsmark 3 was in place since commissioning in year 1985. Re-qualification was performed every 10 years until 2010.
SE-54 | 54 | EC | Sweden | 03. Electrical cables | 50, 52 | Could you please be more specific for the inspection and testing intervals For Forsmark and Ringhals? (The report says only that they are managed in the preventive maintenance plan.) |  | Forsmark states that today cables are tested at installation, reinstallation, some condition based test together with installed equipment and observed artefacts, e.g. at visual inspections. However, for Forsmark, the detailed AMP for electrical cables is still under development. The intervals for inspection and testing is not yet defined. Ringhals states that walkdowns inside the containment and in turbin building every second year, in auxiliary system building every third year, other buildings every fifth year. LIRA measuring in conjunction with planed maintenance of MOV every fourth year. Tan/Delta measuring of 6 kV cables every tenth year. Insulation resistance measuring follow the maintenace plan for the component and vary depending on the periodicity of planed maintenace for the component.
SE-55 | 55 | EC | Sweden | 03. Electrical cables | Generic 39-61 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found. |  | SSM can send this typ of information from OKG and RAB if requested. Forsmark states that the AMP for electrical cables is still under development. Further grouping of cables for AM will be considered. Oskarshamn states that this list was an appendix to report WENRA TPR 2017 - Chapter 03. Ringhals states that all cables in Ringhals are registered in a cable database. In this database there are information about type, length, routing, supplier, date of manufacturing, electrical class, safety class, separation, electrical sub, etc. Cables which are used in Ringhals are described in an internal document.
SE-56 | 56 | Slovenia | Sweden | 04. Concealed pipework | 68 | Section 4.1.2, page 68: There are no R&D programmes mentioned in the section that the NPPs could possibly be involved in. Are there any (other than the Oskarshamn NPP, which R&D activities are mentioned in Section 4.1.3)? | Website | The R&D activities that Oskarshamn NPP describes are performed through Energiforsk (in which Forsmark and Ringhals also participates). No other R&D activietes, except the once described by Oskarshamn, are performed by the Swedish licensees.
SE-57 | 57 | Finland | Sweden | 04. Concealed pipework | 74 | What are the corresponding safety and operation challenges, like maintaining safe shutdown condition, flooding risks, etc. connected to AMP? | Website | Forsmark states that the main challenge in connection to the AMP for concealed pipework would be to maintain concreate surfaces in cooling water tunnels from degradation due to iron rebar corrosion from sea water salt intrusion. However, this has no immediate impact on margins for maintaining safe shut-down condition if assessed and repaired periodically. No Licensee Event Report has been filed due to any incidents. (F-0053791, Chap 3) Oskarshamn states that a challenge is to improve nondistructive testings regarding concrete. Ringhals states that the engeneering an maintenence department within civil structures have performed an investigation regarding pressure relife hatches at unit 3 och 4. This has resulted in that the status of the documation and maintenance programme have improved. The acceptance criterias for errors have also decreased, whitch leads to that more details are changed.
SE-58 | 58 | Netherlands | Sweden | 04. Concealed pipework | 4.1.1, p.62-64 | Since all licensees are identifying the ageing mechanisms and using grouping criteria based on the environment, operating conditions, materials, pipe diameter etc., could you please present this information for metallic concealed pipework as well? | email | Forsmark states that there is information in chapter 2.1.3 in Forsmark reference report (F-0053791). Oskarshamn states that they only have the fire-protection pipeline in the scope, and its made of metal. So therefore its not necessary with an own Commodity Group. Ringhals states that for Metallic pipework underground (R-b) conditions are: - environment “Indoor climate, dry and warm, no moister”, - operating conditions “Not applicable for external surface”, - material “Austenitic stainless steel, Low alloy steel, Copper and copper alloys” - potential for chlorides in all systems, pH<10,5”
SE-59 | 59 | Netherlands | Sweden | 04. Concealed pipework | 4.1.1, p.62 | General observation: metal pipework is largely excluded from this NAR, could you please provide a motivation for this? | email | Forsmark states that the motivation for generally excluding metal pipework regarding Forsmark is that the ASEA BWR design does not include any buried or underground (concealed) pipework related to safety functions. Oskarshamn states that the cooling water channels are made of concrete and in solid rock. Oskarshamns scope include the pipe of ring line of the fire protection system, no other pipe are identified in the scope. Ringhals states that metallic pipework that is in-scope of concealed (underground) pipework at Ringhals and are described at page 67. For more information se Wenra TRP 2017.
SE-60 | 60 | Netherlands | Sweden | 04. Concealed pipework | Table 8, p.68 | Could you please elaborate on the acceptance criteria for inspection activities in more detail than currently available in the text and table? | email | Forsmark states that the inspection method of choice is a part of the pre-assessment of the qualified inspector. There is no absolute acceptance criteria for each surveillance activity. The judgement of the qualified building inspector will be the basis for further investigation and reporting. What degradation that is unacceptable is dependent on the structure or component affected.
SE-61 | 61 | Concealed pipework expert group | Sweden | 04. Concealed pipework | 76 | 4.3: the regulator notes an absence of cooperation between the utilities on this issue; has there been any improvement on this matter since ? | expert group 5 | To work with conceled pipework as a category is new to Sweden so no established way to cooperate excist. However the work has been done as part of other categories as mentioned in the text and in this work cooperation exists. The cooperation is limited to joint participating in ENERGIFORSK concrete program doing R&D in ageing degradations in concrete structures. And for example for Oskarshamns cooling water channels made of concrete and solid rock there is an AMP developed, which is based on results from Energiforsk where Ringhals and Forsmark participate.
SE-62 | 62 | Concealed pipework expert group | Sweden | 04. Concealed pipework | 63 | 4.1.1: Water channels and culverts are considered concealed pipework – and included in AMPs. Degradation is generally linked to corroding rebar and concrete chemistry problems. | expert group 5 | Forsmark states that is correct. Oskarshamn states that for the cooling water channels thats correct because the are made of concrete and solid rock. Solid rock doesnt have any ageing phenomena. Ringhals states that today the status of the cooling water channels are good. Work to improve the status of the outlet of auxilary water channels is ongoing. We also investigates dry areas next to the channels because the increased risk of damages in those areas.
SE-63 | 63 | Concealed pipework expert group | Sweden | 04. Concealed pipework | 69 | 4.1.3: Forsmark stresses DC cathodic protection will be an effective protection against rebar corrosion. | expert group 5 | Question was to Oskarshamn, not Forsmark. Oskarshamn states that existing buried / cast pipes do not have cathodic protection. Important to emphasize that this applies to reinforced concrete structures in the cooling waterways.
SE-64 | 64 | Concealed pipework expert group | Sweden | 04. Concealed pipework | 70 | 4.1.3, Ringhals seems to have a comprehensive AMP for piping other than water channels and culverts, but almost entirely relying on visual inspections, being difficult to perform with concealed piping. | expert group 5 | Ringhals: In SSM 2017:36, table 9 at page 70, RAB:s buried piping is missing, (see Wenra TRP 2017 Table 7). For buried piping, performance surveillance of the fire protection pump is also used as detection method in order to detect eventual leaks. For other concealed piping, that are difficult to access for inspections, there are no identified degradations mechanism except for austenitic stainless steel pipes. These pipes are included in the ISI program and surface test is performed to detect identified degradation mechanism. AMP R-XI.M41 is relying on both preventing and detecting actions. Preventive actions are backfill and coating, done according to standards.
SE-65 | 65 | Concealed pipework expert group | Sweden | 04. Concealed pipework | 73 | 4.2, Ringhals: the finding that exchanging the rebar at extra vulnerable locations may cause increased (galvanic) corrosion in nearby ordinary rebar is an important lesson. | expert group 5 | Ok, thats correct.
SE-66 | 66 | Concealed pipework expert group | Sweden | 04. Concealed pipework | 75 | 4.3, Table 10: looking at the table, the concrete at Oskarshamn seems to be very vulnerable, but may we assume, that they use an all-risks approach, whereas the other operators focus on the most important mechanishms? | expert group 5 | Thats correct, Oskarshamn focus on potentional and teoretical degradation mechanisms. An all-risk approach is therefore used.
SE-67 | 67 | Bulgaria | Sweden | 05. Reactor Pressure Vessels | p. 82 | “Current Status and Strategic Plan: • The current object status is documented in table form down to an object level, much like R-GALL, to provide a snapshot. An annual summary report is created and based on the contents in the tables. The report focuses on the objects where the probability and effect on safety and availability is considered to be the greatest, and the most appropriate strategy to manage these risks.” What is the involvement of the Regulator at that stage? Does the operator submit the Annual Summary Report to the regulator for information/approval? | Website | In this specific case theere is no involvement by the regulator.
SE-68 | 68 | United Kingdom | Sweden | 05. Reactor Pressure Vessels | 88 | "Internal and external operating experiences. The shift in transition temperature of RPV shell welds is attributed to high nickel and manganese content. Please give more detail regarding the concentration of these elements and the effect on transition temperature. " | Website | The nickel and manganese content in the weld material are typically about 1.6 Ni and 1,4 Mn (wt-%). The Ni content is thus well above the upper range of 1.2 wt-% for the Regulatory Guide 1.99 trend curve. Results from surveillance tests of high Ni weld materials shows as expected a much larger shift of the ductile to brittle transition temperature (DBTT) than predicted by the RG 1.99. trend curve modell. A bounding curve of surveillance test data for BWR conditions give a chemistry factor for the high Ni weld material of about CF=280°F. Regarding PWR conditions have Ringhals AB performed several investigations and some of the results have been published. Please find further information in the following available references: "Long Term Irradiation Effects on the Mechanical Properties of Reactor Pressure Vessel Steels from Two Commercial PWR Plants” Efsing, Pål Royal Institute of Technology, Dept. of Solid Strength, Stockholm, Rouden, Jenny Ringhals AB, Väröbacka, Lundgren, Martin Epsilon AB, Göteborg, DOI: 10.1520/STP104004 “Flux Effects on Radiation Induced Aging Behaviour of Low Alloy Steel Weld Material with High Nickel and Manganese Content” Efsing, Pål Department of Solid Mechanics, KTH school of Engineering Sciences, Stockholm, Roudén, Jenny Department of Engineering, Analytical Services, Ringhals AB, Väröbacka, Nilsson, Per Department of Engineering, Inspection and Aging Management Services, Ringhals AB, Väröbacka, DOI: 10.1520/STP157220130112 “Extended Mechanical Testing of RPV Surveillance Materials Using Reconstitution Technique for Small Sized Specimen to Assist Long Term Operation” May, J. AREVA GmbH, D-91052 Erlangen, Paul-Gossen-Str. 100 Rouden, J. Vattenfall Ringhals AB, SE-432 85 Väröbacka, Efsing, P. Vattenfall Ringhals AB, SE-432 85 Väröbacka, Valo, M. VTT Technical Research Centre of Finland, Hein, H. AREVA GmbH, D-91052 Erlangen, Paul-Gossen-Str. 100 DOI: 10.1520/STP157620130189 "Analysis of the DBTT shift in a commercial power plant with high nickel containing weld material" P. Efsing, C. Jansson, T. Mager and G. Embring, in ASTM-STP 1492 and Journal of ASTM International (JAI), paper #100719, 2008 "On flux effects in a low alloy steel from a Swedish reactor pressure vessel" M. Boåsen, P. Efsing, U. Ehrnsten, Journal of Nuclear Materials, vol 484, pp. 110-119, 2017 "Evolution of precipitation in reactor pressure vessel steel welds under neutron irradiation" K. Lindgren, M. Boåsen, K. Stiller, P. Efsing, M. Thuvander, Journal of Nuclear Materials, vol 488, pp. 222-230, 2017 "On the analysis of clustering in an irradiated low alloy reactor pressure vessel steel weld" K. Lindgren, K. Stiller, P. Efsing, M. Thuvander, Microscopy and Microanalysis, vol 23, pp. 376-384, 2017 "Post-irradiation annealing of Ni-Mn-Si-enriched clusters in a neutron-irradiated RPV steel using Atom Probe Tomography" Journal of Nuclear Materials, vol 459, pp. 127-134, 2015 “Using complimentary microscopy methods to examine Ni-Mn-Si-precipitates in highly-irradiated reactor pressure” P. D. Edmondson, C. M. Parish, R. K. Nanstad Acta Materialia, 2017 “Atom probe tomography characterizations of high nickel, low copper surveillance RPV welds irradiated to high fluences” M. K. Miller, K.A. Powers, R. K. Nanstad and P. Efsing Journal of Nuclear Materials
SE-69 | 69 | Finland | Sweden | 05. Reactor Pressure Vessels | 78 | On which guide are the ageing management principles based at Oskarshamn 3, IAEA NS-G-2.12 or something else? | Website | As in Ringhals and Forsmark the ageing management program for the RPV is based on NS-G-2.12, and the significant degradation mechanisms have been verified towards NUREG-1801 (as explained in chapter 5.3)
SE-70 | 70 | Finland | Sweden | 05. Reactor Pressure Vessels | 85 | It seems that there are some empty positions in the table 13 where one expects to see a mechanism or acceptance criteria. Is it possible that some mechanisms (relating to HAZ, weld, nozzle to pipe weld) and acceptance criteria (relating to base metal, weld, cladding, nozzle to pipe weld) relating to BWR plants could be missing? | Website | Thank you, there is an error in table 13. The "Significant degradation mechanism" and Acceptance Criteria" shall be shifted uppwards one line from Object "Inner Radius (PWR)" and lower. There is 8 "Objects" and 8 "Significant degradation mechanism" and "Acceptance Criteria". They should match each other.
SE-71 | 71 | Finland | Sweden | 05. Reactor Pressure Vessels | 95 | Is it possible that the system code 415 is not correct. At Olkiluoto 1 and 2 the the corresponding system code (main feed water) is 312. | Website | There are two different system code systems for the Swedish Nuclear Power Plants. One system code system by Vattenfall and one by ASEA-Atom. The main feed water system has code 415 in the Vattenfall system and code 312 in the ASEA-Atom system.
SE-72 | 72 | Finland | Sweden | 05. Reactor Pressure Vessels | 85 | Is there a difference between TLAA and STA (damage tolerance analyses)? How are they applied to assess SSC operability? | Website | Yes there is. According to the Swedish regulation, it is mandatory to develop licensee specific programs for ISI. The programs are since more than 20 years based on detailed knowledge of the degradation mechanisms for each object. It is also necessary to define what type of defect that may occur in the object. When this type of possible degradation is understood the next step is to calculate an acceptable flaw size for each object, this type of calculation is documented in the STA document. Based on the documented knowledge of possible degradation in combination with the calculated acceptable flaw size a relevant inspection interval is defined and an ISI system is developed and qualified accordingly. Ringhals uses the definition of TLAA as they are described by e.g. IAEA and US NRC. An inventory of existing and new TLAAs is completed and all the TLAA's for Ringhals unit 3 and 4 are scheduled to be completed by the end of 2018.
SE-73 | 73 | United Kingdom | Sweden | 05. Reactor Pressure Vessels | 87 | "Section 5.1.2, R&D programmes - Ringhals is running a thermal ageing research project from samples extracted from a replaced pressuriser from Ringhals 4. These results give valuable input for possible risks of thermal ageing during LTO. Please provide details of any results of this programme." | Website | So far experiences of Thermal Ageing are disseminated within the research community, for example the networks within FROG, IGRDM, PWROG and so on. Within these networks, data that are presented, are discussed and scrutinized by the research community. The results being a better knowledge and suggestions on how to proceed with testing and analyses. As of know we have a plan on how to proceed, and a very limeted amount of R&D results are available.
SE-74 | 74 | United Kingdom | Sweden | 05. Reactor Pressure Vessels | 96 | "Section 5.1.4 - On Ringhals 3 and Ringhals 4, the outlet nozzles safe end welds were repaired in 2003 and 2004 due to defects being found. a. Who carried out the repair? b. Are there any lessons to be learnt from the repair technique?" | Website | Westinghouse as main contractor. Subcontractors: Uddcomb for manufacturing of all necessary auxillary equipment and inlay welding, Westinghouse PCI performed machining of nozzles. The process was semi automated and a lot of equipment was developed to make it possible to acess the nozzles. Ringhals states that many lessons learned during this first of a kind project and it is not posible to present them in this format, it requires separat presentations. However, the project was succesfull and the repair of 3 outlet nozzles required 30 days of work in the vessel (on critical path). Many lessons learned during the development and qualification of the welding processes. Several ISI have been performed and so far there are no indications of degradation of the weld inlay. Additional information: After Ringhals and VC Summers OE with defect in outlet nozzles, MHI developed and performed fully automated inlay welding of PWR RPV Nozzles in Japan.
SE-75 | 75 | Switzerland | Sweden | 05. Reactor Pressure Vessels | 84 | Is a fatigue monitoring system used in Swedish NPP’s? If yes, does it include parts of the RPV? Is the influence of environmental effects (FEN-factors) taken into account? | Website | Forsmark Answer: No, Oskarshamn Answer: Transients are followed and noted by the operational department. Marginal against each transient limit is evaluated and documented at least once per year. The system is based on ASME-criterias for tensions etc., RAB Answer: No general and automated fatigue monitoring system is used at Ringhals. Temporary systems are used to monitor critical areas or areas of specific interest. No specific fatigue monitoring system in use on the RPV. All transients are documented by the operational department and the engineering department compare the accumulated number of transients with the allowable number of transients. Yes, the influence of environmental effects (FEN-factors) are taken into account at Ringhals.
SE-76 | 76 | Switzerland | Sweden | 05. Reactor Pressure Vessels | 86 | Is acceptance of neutron embrittlement considered by screening criterion according to PTS rule 10 CFR 50.61. What is the highest RTNDT? | Website | Yes, the PTS screening criteria is considered as a fracture toughness requirement for protection against PTS-events. With conservative assumptions Ringhals Unit 3 reaches 149 °C at EOL (60 years).
SE-77 | 77 | Belgium | Sweden | 05. Reactor Pressure Vessels |  | Could you elaborate on the results of the RPV TLAA performed for the LTO periods of Swedish NPPs? | email | The scope of the TLAA for the RPV includes an integrity review according to the US regulation. This consists of P-T Limit Curves and USE requirements according to 10 CFR 50, App. G and the PTS screening criteria in 10 CFR 50.61. In addition to this, the Swedish Regulator requires both a deterministic and probabilistic PTS analysis of the RPV. Also, it shall be confirmed that the P-T Limit Curves for the beltline area covers all the materials in the RPV, including the inlet and outlet nozzles. Both Ringhals unit 3 and 4 fulfill the requirements for 60 years of operation and this is documented in an extensive "RPV TLAA Package". The TLAAs for the RPVs for Forsmark 1-3 shows that operation in excess of 60 years is possible. Formally, Oskarshamn 3 enters into LTO-operation in 2025, and therefore the work with the TLAAs is presently ongoing. It is too early to show/deliver any results at this stage.
SE-78 | 78 | RPV expert group | Sweden | 05. Reactor Pressure Vessels | 83 | 5.1.1 Table 12 includes examples of objects (subcomponents) within the RPV that are subject to ageing management. Could you confirm if the thimbles are included in the scope of the aging management programs for RPV of PWR plants?. If is included, are thimbles subjected to any surveillance or monitoring inspection program?. | expert group 2 | "Thimble" = Thimble Tube Yes the Thimble Tubes are included in the scope of Ringhals PWR aging management. A specific Thimble Tube Ageing Analysis is available. A specific Thimble Tube Ageing Management Program is available in R-XI.M37. Yes, ISI is performed regularly on the thimble tubes due to wear issues. A replacement program is also in place and based on calculated fluence levels the Thimble Tube is replaced when the acceptance criteria is reached.
SE-79 | 79 | RPV expert group | Sweden | 05. Reactor Pressure Vessels | 85 | 5.1.2 Table 13 Summary of significant ageing mechanism of the RPV objects. Could you clarify if boric acid corrosion caused by primary leakage is considered as a degradation mechanism? Is there an inspection program, i.e. periodic visual examination type VT2, to monitor the external surfaces that could be affected by this mechanism in case of long periods of leakages from flange connections or through wall cracking? | expert group 2 | Yes, boric acid corrosion caused by primary leakage is considered as a degradation mechanism and a BAC Ageing Management program exists. Yes, external bare metal visual ISI of vessel head and bottom dome are performed regulary. In addition, full volumetric inspections of reactor vessel head penetartions and bottom penetrations including attachment welds are part of the ISI program. The PWR vessel heads are replaced as a preventive action to avoid through wall cracking of alloy 600 penetrations.
SE-80 | 80 | RPV expert group | Sweden | 05. Reactor Pressure Vessels | 92 | 5.1.3 Chapter 5.1.3. Could you provide more information about the in-service inspection programs established?. What is the scope within each group?. What is the frequency of the activities performed to components within the scope?. Which standard is applied in the ISI program?. | expert group 2 | The scope regarding ISI for RPV is divided into four different groups (A, B, C and F) with regard to known damage mechanisms and failure consequence. Group F means prescribed testing by regulatory body and is mandatory. Examples of Group F components are; butt splices (8 years interval), part of feed water nozzles (8 years interval). Examples of Group A components are; feed water nozzle inner radius (maximum 10 years interval). Examples of Group B components are; moderator tank stand attachment (welds core shroud support welds) (3 years interval). Examples of Group C components are; neutron detector nozzle (20% tested, no fixed interval). Further information regarding damage index and consequence index, see FKA report F-0051000 Chap 3.3.1. See also table 15 and further information given in the reference document OKG report 2017-06804 rev.2.
SE-81 | 81 | RPV expert group | Sweden | 05. Reactor Pressure Vessels | - | 5.1.3 Is there a periodic inspection program applicable to the new vessel head, in particular on the penetration nozzles?. | expert group 2 | Yes, during the first 20 years bare metal visual inspections are performed on external surfaces with 3 years interval. The inspections are focused on the area around the penetrations. After 20 years of operation a full volymetric inspection is performed on the penetrations and attachment welds. This inspection was performed at Ringhals Unit 2, no defects reported.
SE-82 | 82 | RPV expert group | Sweden | 05. Reactor Pressure Vessels | - | Is the consumption of usage factor monitored for the components considered in design with high usage factor?. | expert group 2 | Yes. Forsmark, Oskarshamn and Ringhals performs transient monitoring programs regarding components with high usage factors. RAB Answer: No general and automated fatigue monitoring system is used at Ringhals. Temporary systems are used to monitor critical areas or areas of specific interest. No specific fatigue monitoring system in use on the RPV. All transients are documented by the operational department and the engineering department compare the accumulated number of transients with the allowable number of transients. Yes, the influence of environmental effects (FEN-factors) are taken into account at Ringhals.
SE-83 | 83 | RPV expert group | Sweden | 05. Reactor Pressure Vessels | - | 5.1.3 In accordance with WENRA Technical Specification, chapter 5.1.3, can you describe the main activities related to fatigue and water chemistry for RPVs? | expert group 2 | Forsmark answer: The activities monitoring chemistry for primary system components is governed by EPRI WCG. Fatigue is managed by TLAA and has no monitoring program. Oskarshamn answer: Beside the yearly transient evaluation the ISI-program is used to detect indications of fatigue induced defects. The chemistry manual used in Oskarshamn is based on EPRI guidelines, authority regulations and specifications from the suppliers. Trend analyses are done for certain key parameters that have been identified as important to ensure the integrity of the materials and radiation levels in the systems. RAB answer: The influence of environmental effects (water chemistry) are taken into account for the RPV. Ringhals Ageing Management Program Water Chemistry (R-XI.M2) is an extensive program. In all essential parts it is based on EPRI Water Chemistry Guidelines.
SE-84 | 84 | EC | Sweden | 05. Reactor Pressure Vessels | Chapter 5.1.1, page 82 | The information concerning processes/procedures for the identification on ageing mechanisms provided for Forsmark is to generic. More details should be given. For instance, good information is provided for the case of Ringhals |  | Chapter 5 of the the Swedish NAR is a compilation of the aging management activities of the different Swedish RPVs. Detailed information about individual RPVs are given in the base reports from the licensees which are published at the SSMs webb site, https://www.stralsakerhetsmyndigheten.se/publikationer/rapporter/sakerhet-vid-karnkraftverken/2017/201736/ . Informatiom about ageing management of the RPVs at the Forsmark site can be found in report F-0051000.
SE-85 | 85 | EC | Sweden | 05. Reactor Pressure Vessels | Chapter 5.1.2, page 89 | Ringhals RPVs were UT inspected for possible presence of hydrogen flakes. But for Forsmark 3 and Oskarshamn 3 only a review of the manufacturing documentation and inspection records (presumably UT inspection carried out before RPV operation) was performed. Why this difference in criteria?. |  | Regarding the possibility of hydrogen flakes in the RPV material SSM follow the WENRA recommendation, issued in 2013, to verify the material quality and integrity in a 2-step approach: 1. A comprehensive review of the manufacturing and inspection records of the forgings of the RPV, 2. Examination of the base material of the vessels if considered necessary. Sample of the beltline and nozzle rings were inspected for Ringhals 2 in 2012, for Ringhals 3 in 2016 and for Ringhals 4 in 2014. The results from the inspections were: No reportable indications similar to hydrogen flakes. Step 1, the review of the manufacturing and inspection records, for Forsmark 3 and Oskarshamn 3 were reported to SSM 2015. The results showed that there were no indications of possible hydrogen flakes similar to the defects found in Doel 3 and Tihange 2. Based on the performed inspections of Ringhals 2-4, the outcome of the review of the manufacturing documentations for F3 and O3 and that hydrogen flakes have not been found in any other RPV reported to WENRA or else were, SSM consider that inspections of the base material for the RPVs of Forsmark 3 and Oskarshamn 3 is not necessary. However, if new information indicate the possibility of hydrogen flakes in forgings similar to the RPV material in Forsmark 3 and Oskarshamn 3 SSM may revised its standpoint and request inspections of the two RPVs.
SE-86 | 86 | EC | Sweden | 05. Reactor Pressure Vessels | Chapter 5.1.2, page 90 | Ringhals RPV Unit 3 has a large predicted Reference Temperature after about 42 years of operation. What about the Upper Shelf Energy (USE) of the critical material?. Is the USE greater than 68 joules for the same operation period? |  | Correction: When it was discovered that the reference temperature was predicted to exceed the PTS Screening Criteria after 42 years of operation, Ringhals decided to install Generation II of the Shielded Fuel Assemblies. The latest predictions show that Unit 3 will fulfill the PTS Screening Criteria after 60 years of operation, as stated later in the same paragraph. Surveillance testing of Unit 3 weld material show that the Charpy Upper Shelf Energy will be greater than 68 J for fluence levels beyond EOL fluence.
SE-87 | 87 | Slovenia | Sweden | 07. Concrete containment structures | 124 | Regulator assessment and conclusions on ageing management of concrete structures (Page 124): Regarding acceptance criteria related to ageing mechanisms; it is stated in the report that individual licensees uses different acceptance criteria. Acceptance criteria postulated on which standard or guidance does SSM prefer for licensees to use? | Website | In our general advice on the application of our regulations the regulatory prefer the licensees to use ASME XI, Subsection IWE and IWL and Regulatory Guide 1.35 for inspection of mechanical integrated parts. Other than that the regulation doesn’t state which standard or guidance the licensees must use for acceptance criteria. It is the licensees responsibility to choose and to show the regulatory that there are sufficient safety margins against structural failure as well as against such leakage and other defects that may affect the safety under the nuclear power plants intended operating time.
SE-88 | 88 | United Kingdom | Sweden | 07. Concrete containment structures | 119 | Table 24 mentions that Ringhals in 2014 discovered extensive corrosion at the bottom slab that required extensive repairs. There is no discussion on the root cause of these defects, please provide more information on this event and how it informed subsequent AMP. | Website | According to Ringhals the bottom slab at Ringhals Unit 2 has a uniqe construction and it is hard to in short terms describe this. At the bottom plate a layer of LECA-blocks (Light Expanded Clay Aggregate) is placed to decrease the gradient of temperature. The area with LECAs is also filled with lime water to make a good environment for the steel plate. There is a variety of conditions with regard to corrosion mechanisms from the construction process until today. It is not possible to distinguish the contribution from different corrosion mechanisms. By analyzing the different mechanisms, however, it is possible to understand and explain the attacks that have taken place historically and to conservatively predict future damage development. The combination of corrosion mechanisms that is discussed for the bottom plate is Active / Passive corrosion cells, Microbial corrosion, Corrosion caused by aeration cells and Corrosion in high alkaline oxygen-free water.Through the aging management work and through technical inspections and tests and analyses it was concluded that with the extent of the identified corrosion and with the repairs carried out, the carbon steel liner integrity is however considers to not threatened the requirement for leak-tightness. The Swedish Radiation Safety Authority (SSM) considers that Ringhals's damage investigation and mapping, which has been the basis for their repair strategy, contains such uncertainties that there still may be holes due to corrosion in the bottom plate. However SSM made the overall assessment that Ringhals demonstrated that sufficient safety margins were in place against ruptures and the kind of leakage that might have an impact on safety during the intended period of operation, which is until the end of 2019.
SE-89 | 89 | Bulgaria | Sweden | 07. Concrete containment structures | p.124 | It was written that: “..SSM finds that lack of acceptance criteria can lead to miscalculation of the structures condition assessment”. Would you please share your opinion about possible SSM intention to require from all utilities development of the scope of acceptance criteria for those structures? | Website | The licensees themselves states that their ageing management programs are based on IAEA NS-G-2.12 in where acceptance criteria is one of nine generic attributes an ageing management program should have. SSM has accepted the licensees use of IAEA NS-G-2.12 and therefore expect them to have defined acceptance criteria against which the need for corrective action is evaluated. We intend to cover acceptance criteria in our ordinary supervision of the ageing management program.
SE-90 | 90 | Bulgaria | Sweden | 07. Concrete containment structures | p.124 | SSM concluded lack of regular trending of the 07. Concrete containment structures degradation. Is there SSM intention to change that condition to better? | Website | The licensees themselves states that their ageing management programs are based on IAEA NS-G-2.12 in where trending is included. SSM has accepted the licensees use of IAEA NS-G-2.12 and we intend to cover trending in our ordinary supervision of the ageing management program.
SE-91 | 91 | Netherlands | Sweden | 07. Concrete containment structures | 7.3 | Is a periodic pressure test included in the programme (other than a leak test) ? | email | There is no requirement that the license holder shall carry out any pressure test in addition to the pressure tests to be carried out before commisioning of the NPP. The requirement for leakage test is according to 10 CFR Appendix J to Part 50 and should be carried out three times in 10 years. At Oskarshamn the operation department is performing a pressure test which is included in the leakage testing process. At Forsmark all periodic pressure tests are performed at the design pressure including the leak tests. At Ringhals pressure test were carried out before commisioning of the NPP. The containment air test that is performed only includes measurement and leakage at LOCA-pressure.
SE-92 | 92 | Netherlands | Sweden | 07. Concrete containment structures | 7.3 | Operators like the one of Ringhals state that the programme is based on a number of codes/programmes (IAEA, EPR, NRC, GALL). How does the regulator assess the programme as a whole and the choices made by the operator regarding which code(s) to choose? | email | The Swedish regulatory now assess that all liceencees have an implemented ageing management program but that further work need to be done. The licensees themselves states that their ageing management programs are based on IAEA NS-G-2.12 which SSM has accepted.
SE-93 | 93 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 118 | 7.1.3 Oskarshamn: What features are recorded of the crack in the crack map ? | expert group 4 | There are no features stated when cracks are mapped, it is up to the involved inspection personnel to decide if the crack shall be noted. The inspection personnel’s knowledge of this is based on experience of the structure.
SE-94 | 94 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 118 | 7.1.3 Has there been a discussion between the power plants about the cause of the various frequencies of inspection activities ? | expert group 4 | There has been a discussion on a basic level and the discussion will continue. Within civil structure, Ringhals, Forsmark and Oskarshamn will do a review of the programmes chosen intervals.
SE-95 | 95 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 121 | 7.1.3 CAT - containment air test - Is it a integral leak rate test (ILRT) ? | expert group 4 | Yes
SE-96 | 96 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 123 | 7.1.4 I suppose the other power plants are also using the EN 1504, just did not give it ? | expert group 4 | Oskarshamn plans to implement the standard in their formal instruction that handles defects. Forsmark states that repair of concrete structures are performed in accordance with the procedures in EN1504 but that the standard is not explicitly cited in their AMP.
SE-97 | 97 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 124 | 7.2 What test frequency is required to determine trends? (Oskarshamn) | expert group 4 | Oskarshamn states that since the detailed demand for trending is not yet stated, the question can not be answered.
SE-98 | 98 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 124 | 7.2 Can we say that there is enough 5-10 year test frequency of concrete structures, due to the slow degradation mechanisms of containment concrete structures ? (Ringhals) | expert group 4 | Ringhals reports that inside the containment an inspection is performed 3 times during 10 years. Outdoors the inspection is carried out every 5:th year. There is no environmental conditions accelerating the ageing of the structure. ACR has not been identified in concrete core samples at Ringhals. Inspection every 5:th year is therefore enough.
SE-99 | 99 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 125 | 7.2 Oskarshamn (service openings): Do I understand well that visual inspection and leak test are both required? | expert group 4 | Yes, that is correct.
SE-100 | 100 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 125 | 7.2 Trend analyzes require a large database, and more accurate forecasting requires more data. How could the database expansion can be achieved ? Maybe with more frequent data collection or by national or international co-operation? | expert group 4 | A project within Energiforsks R&D programme is looking at the database BATMAN (that Swedish Transport Administration uses) to see how parts of this can be used within civil maintenance at NPP. Oskarshamn thinks the Swedish plants together needs to investigate if a national database is needed. Forsmark reports that according to the TLAA for the pre-stressing systems trending analyses are only performed for the loss of tendon forces. Sufficient amount of data on measured tendon forces are available from earlier performed measurements. After each consecutive ISI the trend analysis/prediction models are updated based on the new data.
SE-101 | 101 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 131 | 7.3.3 In SSM's opinion: Can the Swedish licensees' AM practice be considered as a good example? | expert group 4 | The AM practice various between the Swedish licensees. But since the end of January 2018 it is concluded that all licencees have an implemented ageing management program. There are parts of the programs that can be considered good examples and other areas where further development are needed.
SE-102 | 102 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | All | Is there a working group, besides Energiforsk which is mainly R&D, with representation from the three Licensee to exchange information and OPEX in ageing management? | expert group 4 | There a common forum FORSAMP for experience exchange in ageing management programme between Oskarshamn, Forsmark and Ringhals. Oskarshamn and Forsmark also process national and international OPEX.
SE-103 | 103 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 102 & Table 20 | Description of ageing management programmes for concrete structures - The text in page 102 states "The reactor buildings that surround the BWR containments are made of reinforced concrete". Table 20 - Ringhals reactor building does not have a degradation mechanism for steel reinforcements. Please clarify. | expert group 4 | Ringhals chose to report reinforced concrete as a concept. They do not inspect reinforcement bars, but there are inspections of concrete surfaces that can show problems with the reinforcement.
SE-104 | 104 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 110 | Forsmark and Ringhals - Two Licensees divide the reactor containment into four different climatic zones.Is there a process to assess how a change in theses conditions affect the degradation mechanism? How does this approach compare with the ageing management results from the third Licensee? | expert group 4 | At Oskarshamn there is an ongoing work to investigate local changes regarding temparature, humidity and radiation in Oskarshamn 3. Ringhals reports that if the conditions are changed the strategic maintenance plan will be updated. At the update the new conditions will be evaluated which, for example, includes to see if the inspection programs and intervals needs to be revised. Forsmark reports that the zones have been identified in the ageing management report for the reason to assess how this affects each degradation mechanism in the different zones.
SE-105 | 105 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 110 | Oskarshamm - One Licensee states the importance of concrete coating in preventing ageing. Could you provide information on the inspections, degradation mechanism and accepting criteria? This information is not included in Table 23 for this Licensee | expert group 4 | Oskarshamn reports that since inspections of for example civil structures are performed the protective coating is then being evaulated. The acceptance criteria of degradtion of the surface protection is set by the experience of the inspector. Protective coating makes the concrete structure resistant regarding for example carbonation.
SE-106 | 106 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | Table 23 & 24 | Tables 23 & 24 - Could you provide more information on the seals, gaskets, water stops AMPs for all Licensees? | expert group 4 | The licensees reports that seals, gaskets and water stops are all subject to environmental qualification for managing of ageing, including periodic inspection.
SE-107 | 107 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | Table 23 | Table 23 - One Licensee has not defined an acceptace criteria, so how do they confirm the condition of the containment structures as acceptable? | expert group 4 | Forsmark and Ringhals reports that acceptance criteria are used for the assessment of the pre-stressing system and the leak tightness of the reactor containment. For the pre-stressing systems the acceptance criteria are that the tendon forces should exceed the forces needed for fulfilling the structural integrity of the containments at LOCA-pressure. The acceptance criterion for the leak tightness of the containments is that the leakage during a period of 24 hours should be less than 1 % of the containments inner volume. The containments condition is verified if the acceptance criteria for the pre-stressing systems and the leak tightness both are fulfilled. Oskarshamn reports that when the extent of an ageing effect is considered significant, a decision is made regarding further analysis, examination or repairs. If a damage occur then we make a fault report and of that a decision is taken what to do next.
SE-108 | 108 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | Table 23 | Table 23 - Please could you provide the following information/clarifications: the NAR-example on steel reinforcement for all three Licensees & the frequency of inspections for all the examples in Table 23 and all the Licensees | expert group 4 | Forsmark reports that inspections of service openings, fastening systems, seals, gaskets and water stops are performed annually. Oskarshamn reports that no third party organisations are used during inspections. Visual inspections are performed in cooperation with a han-held hammer to clarify if there is some delamination from corroded reinforcement. The frequency of the visual inspection is performed annually. Ringhals reports that they don´t have an inspection programme for reinforcement bars but for the reinforced concrete.
SE-109 | 109 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | Table 23 | Table 23 - Can you please confirm if all the Licensees with un-grouted tendons carry out grease tests? | expert group 4 | Ringhals and Forsmark have un-grouted tendons. It is only Ringhals who has grease as protection against corrosion (Forsmark has dried air). Ringhals performes grease test every 10:th years together with the lift-of-test.
SE-110 | 110 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 115 & Table 24 | Oskarshamm & Table 24 - It is stated that trending is not performed on a regular basis, however lift-off tests of tendons are carried out. Do the Licensees carry out trending analysis for the prediction of loss of tension in tendons? | expert group 4 | Forsmark reports that prediction of loss of tension have recently been done in a TLAA using data from prior inspections. Their recommendation from the ageing management report is to update the TLAA after new inspections is carried out. Oskarshamn has grouted tendons and a deformation test pursuant to Regulatory Guide 1.90 was carried out in 2017, and they plan to make a follow-up test in 2020. Their evaluation of the test is not yet analysed so they cannot provide any trending results yet. In their TLAA for the reactor containment an analysis has been done and the results shows that the loss of tension is lower than compared to the predicted one. Ringhals has collected all results from the tendon tests in a strategic maintenance plan for tendon-system. In connection with the test an evaluation is done to ensure that the result is as expected. Ringhals has not previously predicted the tendon force for another 20 years. But an evaluation is made in connection with the test that there is no problem operating until the next test (another 10 year). In connection with the development of TLAA, trend will also be introduced.
SE-111 | 111 | Concrete containment PCPV expert group | Sweden | 07. Concrete containment structures | 117 | Preventive and remedial actions for concrete structures - Have any remedial actions been carried out by any of the Licensees? Can you provide examples? | expert group 4 | Forsmark reports impregnation of concrete surface affected by sprinkled water in wet-well Forsmark 3. Not for the concrete containment according to Oskarshamn. Ringhals reports that a lot of remedial actions has been carried out regarding concrete structures and that the actions are mainly connected to the cooling water channels/structures.
SE-112 | 112 | EC | Sweden | 07. Concrete containment structures | 114 | Containment Air Tests are performed to validate leak tightness, but no acceptance criteria for the leak tightness is provided for Oskarsham. Are the CAT implemented also at Oskarsham (it is stated on page 119 in Table 24 that 'they conduct integral leakage testing...')? Please can you provide information on the acceptance criteria for the leak tightness tests at Oskarsham. |  | Yes the CAT are implemented at Oskarshamn. The acceptande criteria is based on 10CFR50 Appendix J och GDC 52, 53 och 54. Maximum allowed leakage is 1 (one) % during 24h.
SE-113 | 113 | EC | Sweden | 07. Concrete containment structures | 118 | If understanding of the descriptions provided in section 7.1.1 is correct, the pre-stressing tendons in the BWR containment walls at R1 and O1-3 are grouted, whereas those at F1-3 are not grouted. Do the AMPs contain any provisions for testing or assessing the adequacy of the pre-stressing forces at those units with grouted-in pre-stressing tendons? On page 118, under 'Pre-stressed tendons', it is stated that a way to monitor the pre-stressed containment structures by deformation during pressure test will be evaluated for permanent implementation at Oskarsham NPP in 2017. Please could you provide an update on the result of the evaluation. Is such a measure also considered for implementation at R1? |  | Oskarshamn reports that only visual inspections are performed if they see any damages. Then they decide what the next step will be. In 2017 they performed a global deformation test which did not show any abnormal behaviour of the containment, but the formal evaluation has not yet been done. Ringhals reports that no such measurements has been carried out at Unit 1. The containment air tests are performed at half loca pressure. According to analyses the tendon force should be good but there has not been any possibilities to compare performed analyses with reality. Since Unit 1 only is going to operate until 2020 no more measurements will be performed.
SE-114 | 114 | EC | Sweden | 07. Concrete containment structures | 112-116 | Section 7.1.3: Are there any surveys performed to detect settlement at the different sites? |  | At Forsmark relative movement between buildings are measured. Oskarshamn and Ringhals buildings are grounded on bedrock. Geological surveys that was performed when Ringhals were constructed reports that unbroken cracks with an age of over 100 miljon years shows that no movement of concern has happened.
SE-115 | 115 | EC | Sweden | 07. Concrete containment structures | 118 - 120 | According to the report, the ageing management approach practiced at Oskarsham is less well developed than at the Ringhals and Forsmark. In the section on the licensee's experience of the application of AMPs, the text concerning Oskarsham is more about plans for the future than it is about experience. Are there any timelines associated with all these plans to improve the ageing management programmes at Oskarsham? |  | Oskarshamn reports that during 2017 they implemented the results from the AMR which means that the OAMP is now implemented. During 2018 Oskarshamn will also do some additional measurements regarding potential local environments to assure the data used in the AMR is conservative. They report that their aging management program is a living program which will be continuously improved based on experiences gained.
SE-116 | 116 | EC | Sweden | 07. Concrete containment structures | 120 - 124 | In section 7.3.1, SSM proposes some suggestions for improvement of the ageing management programmes for concrete containment structures at Swedish NPPs. It proposes better cooperation between licensees for identification of potential degradation mechanisms, considers that acceptance criteria need to be more developed and that trending on a regular basis would help making informed decisions. SSM expects that the programmes will be updated accordingly. Has this expectation been manifested in any specific requirements placed on the licensees, with associated timetable? |  | No, this was conclusions from the TPR work.
SE-117 | 117 | EC | Sweden | 07. Concrete containment structures | general | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | Forsmark reports that due to the inner concrete wall the steel liner is not accessible for inspection. The status of the steel liner is verified through the periodic leak-test. Since the function of the steel liner is to secure the leak tightness of the containment an approved leak test is an indirect confirmation of the function of the steel liner. Oskarshamn reports that grouted tendons and liner cannot be visually inspected, but that they use the integral leakage test and the deformation test as a method to evaluate the status regarding corrosion. Ringhals reports that the parts of the liner that is inside concrete cannot be inspected. However, if the construction work has been performed correctly, the environment for the liner should be good. External experience shows several examples where the design has not been properly executed, such as forgotten material and improper design in the after-cast areas. At present, we have no NDT of controlling these parts. The containment air test shows that we have sufficient leak tightness of the containment. A project has begun at Ringhals to develop a long-term strategy regarding the leak tightness of the containment and its liner. The project will include to look at what actions may be possible to achieve in order to better control the status of the liner.
SE-118 | 118 | EC | Sweden | 09. Overall assessment and general conclusions | 127 | It is mentioned that the licensee of Oskarshamn 3 shall have implemented an overall programme for ageing management before the end of January 2018. Please can you provide an update of this? |  | SSM assessment is that Oskarshamn now has an implemented aging management program for all SSC belonging to safety class 1 and 2. Oskarshamn shall, by 31 January 2019, introduce a complete program for dealing with age-related impairments and injuries for the other SSC included in O3's age management program. Oskarshamn will also take into account how local environments can affect the company's management of age-related impairments and injuries based on analysis of results from more detailed plant utilization, as well as introducing an obsolescence sub-program for all SSC
SK-1 |  | Poland | Slovak Republic | 01. General information | 11 | Is there a possibility of flooding NPP Mochovce in case of damage to the dam on the Hron river?(NPP Bohunice, Vah). Can you explain it more widely? | Website | Dams damage scenario on the Váh (Hron) river and its effect on NPP safety operation is described in Chapter 2.4.2 "Flooding" of FSAR. Culmination of dam break wave in all analysed cases does not have an impact on safety of SSCs inside the NPP site. This is an external hazards subject, it does not concern ageing management.
SK-2 |  | Poland | Slovak Republic | 03. Electrical cables | 36 | What standards for storage conditions must be met by electric cables during the construction of NPP Mochovce? | Website | According to technical conditions for cables.
SK-3 |  | Poland | Slovak Republic | 04. Concealed pipework | 50 | What technical standards must meet the conditions for storing pipes and pipelines during the construction of NPP Mochovce? | Website | Storage conditions for pipelines during the construction of NPP Mochovce are given in quality assurance plans and technical conditions, where all the standards and rules for NPP safety operation which are valid throughout the construction period are given.
SK-4 |  | Poland | Slovak Republic | 05. Reactor Pressure Vessels | 61, 70 | 1. Is it possible to quantify damage caused by corrosion in NPP Mochovce in first and second safety classes? Please explain. 2. Is there a SG management program in the Slovak NPP? Can you explain it more widely? | Website | 1. There are many components included in safety class 1 & 2 and quantification of damage caused by corrosion is difficult to be explained to be able to adress this issue by a quantification. It is important to say that we do not have any significant events with corrosion. 2. SG ageing management is fully adressed by the SG AMP.
SK-5 |  | Bulgaria | Slovak Republic | 03. Electrical cables | p.43 | Could you provide more information about the ageing management of neutron flux I&C cables with mineral insulation and also about the ageing management approach to other I&C cables (for measuring temperature, pressure, etc.)? | Website | As for cables with mineral insulation no degradation mechanisms were identified, ageing management for these cables is not required. Condition of other I&C cables is assessed through the AMP activities (cable deposit programme, measurement of cables in operation), maintenance templates and calibration of measurement circuits.
SK-6 |  | Bulgaria | Slovak Republic | 03. Electrical cables | p.45 | Could you please clarify are the corrective actions, such as cable repair/replacement if the status indicator value does not meet the acceptance criteria, visual inspection of the route in case of abnormalities detected during TDR and others, excluded from the AMP and if so, what are the reasons for the exclusion? | Website | For example, if value of insulation resistance does not meet the acceptance criterion or trending shows decline of insulation resistance, then appropriate actions are taken (cable splice / parts of cable / whole cable replacement). In case of abnormalities detected on TDR, primarily visual inspection is performed. Then corrective action to be taken depends on kind of abnormality (e.g. if cable splice is detected, there is no need for action; in case of mechanical damage local repair of cable is done, i.e.). Also within other activities related to cables (maintenance templates, technical revisions) appropriate corrective actions are taken if a non-conformance is identified. Licensee has implemented Corrective Actions Programme in all active NPPs where all relevant roles, responsibilities and procedures related to management of corrective actions are described.
SK-7 |  | Bulgaria | Slovak Republic | 07. Concrete containment structures | chapter 7.1.2 | In conjunction with chapter 7.1.2 ASSESSMENT OF CONTAINMENT CONCRETE STRUCTURES AGING, please, clarify the acceptance criteria related to ageing mechanisms. | Website | The acceptance criteria are related to the type of test. For allowable crack thickness in the concrete Eurocodes is applicable. The concrete humidity is satisfactory up to 2%. The strength of concrete is compared with the result of protocol tests carried out during construction. General corrosion damage is inadmissible on steel constructions, etc. For test results evaluation, acceptance criteria are used according to the relevant standard and design documentation. When clear criteria are not specified, they are determined on the basis of an engineering judgement (See the answer to question #1290, as well). | ref to line in source file corresponding to SK-51
SK-8 |  | Bulgaria | Slovak Republic | 07. Concrete containment structures | chapter 7.1.4 | In conjunction with chapter 7.1.4 PREVENTIVE AND CORRECTIVE ACTIONS FOR CONCRETE STRUCTURES OF THE CONTAINMENT, please, clarify the criteria for taking actions. | Website | See the answer to question #1291. | ref to line in source file corresponding to SK-52
SK-9 |  | Bulgaria | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | p. 30 | Do you use safety performance indicators for assessment of effectiveness of the AM activities and Overall AM Program? If yes, could you please describe the relevant indicators you are using? | Website | Ageing management performance indicators are developed and evaluated for each NPP for the following main components: RPV (irradiation embrittlement and low-cycle fatigue) and steam generator (low-cycle fatigue). These indicators are included in NPP operational safety performance indicators.
SK-10 |  | Bulgaria | Slovak Republic | 05. Reactor Pressure Vessels | p. 40 | “To this end, a working group is set up to analyse the causes of increased effect of degradation mechanism, and to propose effective measures to reduce the trend of degradation …” Could you please provide more information about the organisation of work? What is the Regulator’s involvement in the decisions for the measures to be applied? | Website | Working group consists of representatives from all the involved departments. Group task is to determine causes of higher degradation and to propose corrective actions for mitigation of degradation. Working group members are informed about the current status of corrective actions fulfilment by the time when a particular issue is being resolved. In case of SSC higher degradation rate tha usual (on an average based of long term evaluation ), licensee shall inform the regulator. Corrective measures that have been taken are subject of an approval by the regulator. NRA SR staff doesn´t directly take part in the authorisation holder´s Working Group proceedings but in the case of resulting impact on In-Service Inspections or in the need of repair or modification these are submitted to the Regulatory Body for approval and implementation authorisation according to the Atomic Act No. 541/2004 Coll. and Decree No. 431/2011 Coll. on a quality management system.
SK-11 |  | United Kingdom | Slovak Republic | 07. Concrete containment structures | 76 | Section 7.1.2 states that the licence holder in cooperation with the supplier has developed and implemented a methodology for assessing used lifetime of the containment. This approach to ageing management appears to be good practice. Please provide an example of how it has been implemented. | Website | For assessment of civil structures we use methodology which is based on procedures used in judical assessment. That methodology is adjusted for NPP purposes.
SK-12 |  | United Kingdom | Slovak Republic | 07. Concrete containment structures | 77 | It is stated in Section 7.1.3 that the evaluation of the results of monitoring is carried out according to the acceptance criteria for the acceptability of the degree of degradation and its further development over time. It is not clear what acceptance criteria are used for concrete degradation. Please confirm whether there any specific concrete crack width criteria before remedial action is considered and if so what these criteria are. | Website | See the answer to question #1285. | ref to line in source file corresponding to SK-46
SK-13 |  | United Kingdom | Slovak Republic | 07. Concrete containment structures | 79 | It is noted in Section 7.2 that the use of geo-radar has been successfully implemented in the inspection of steel reinforcement. It is claimed that geo-radar allows non-destructive tests of the possible corrosion attack on the concrete reinforcement. Please provide more information on the technique used and what its accuracy is for determining the degree of reinforcement corrosion. | Website | Measurement of the reinforcement by the geo-radar is primarily focused on verification of the reinforcement correct distribution in the concrete structure, i.e., design vs. real condition. When high humidity locations in the concrete are identified, the geo-radar measurement is used for elimination of a higher corrosion damage to the concrete reinforcement structure. Results of measurements are just informative without a quantified degree of accuracy.
SK-14 |  | United Kingdom | Slovak Republic | 07. Concrete containment structures | 79 | Section 7.3 provides the regulator's assessment and conclusions on the ageing management of concrete structures. This section should present the main strengths and weaknesses of the SSC specific AMP. Please clarify any particular strengths or weaknesses that were identified during the review? | Website | NRA SR together with external TSO identified in the framework of unplanned inspections following weaknesses in concrete structures ageing management: - insufficient concrete carbonatisation inspection - missing qualification of environment with increased humidity and temperature for some parts of Reactor Building - missing time-schedule for building technical survey - incomplete of concrete crack passportisation. Recommended was preventive measures approach to building ageing management. As matters strengths it is needed to mention achieved results of hermetic zone tightness results of all units validated by Periodic Integral Tests (PERIS): EBO3 - Ld150 = 13%/24h. - measured value 4,39 %/24 hours EBO4 - Ld150 = 13%/24h. - measured value 4,07 %/24 hours EMO1 - Ld150 = 5%/24h. - measured value 1,459 %/24 hours EMO2 - Ld150 = 5%/24h. - measured value 0,6456 %/24 hours
SK-15 |  | Switzerland | Slovak Republic | 03. Electrical cables | 18 | Textline9: What design life time duration is foreseen for MO3&4 long-life-cables/equipment? | Website | Required qualified life of cables installed in NPP MO34 is 40 years.
SK-16 |  | Switzerland | Slovak Republic | 03. Electrical cables | 44 | Textline8: "Outside of the AMP …" - is AMP coupled with operational maintenance process? | Website | No, AMP is not coupled with maintenance activities. Within AMP specific tests are carried out on cables which are not the same as tests (inspection) carried out within the maintenance process.
SK-17 |  | Switzerland | Slovak Republic | 03. Electrical cables | 46 | Textline34: Why had surveillance specimen inadequate value of elongation at break? | Website | Deficiency in manufacturing process was the reason of EaB value below the acceptance criterion.
SK-18 |  | Switzerland | Slovak Republic | 07. Concrete containment structures | 76 ff. | How are acceptance criteria for the inspected concrete structures defined? (crack width and depth, crack patterns, carbonation depth, prestress loss, ...) | Website | Acceptance criteria for inspected concrete structures are determined based on technical standards and methodologies.
SK-19 |  | Switzerland | Slovak Republic | 07. Concrete containment structures | 76 ff. | How is the collection and investigation of concrete and reinforcing steel from structural interventions (reconstruction, partial demolition ...) organized? | Website | Intervention to the structural elements with the need to remove part of the original material is very rarely performed. We know that it is a unique opportunity to carry out the laboratory tests for concrete and reinforced steel or another structural elements. On the basis of the planned intervention details AM staff makes decision whether the original material will be used for the tests or not.
SK-20 |  | Switzerland | Slovak Republic | 07. Concrete containment structures | 76 ff. | How are the structures and the structural elements assessed which are inaccessible for visual inspections (indirect/indicative methods)? | Website | The integrity of the all hermetic steel liner (accessible and inaccessible) is indirectly controlled by the integral leakage test and pressure test. Reinforcement degradation is associated with signs of concrete damage and it can be observed by set up inspections. Geo-radar technique is used for monitoring of moisture intrusion, reinforcement, cracks and cavities.
SK-21 |  | Switzerland | Slovak Republic | 07. Concrete containment structures | 76 ff. | Different types of structures and structural elements are normally under AMP assessment, such as secondary structures, anchorage elements, waterproofing sealings, drainage, coatings, fire-retarding sealings, etc. Are all these types included in the inspection programs? | Website | Licensee is responsible for performance of the listed SSCs inspections. Inspections of some structures are performed on the basis of a quality assurance plan and/or manufacturer's recommendations. The additional tests are set as a result of the AMP implementation. All the inspections are included in the inspection programmes with appropriate intervals.
SK-22 |  | Switzerland | Slovak Republic | 07. Concrete containment structures | 76 ff. | Are there specific testing and inspection requirements for safety related anchorage elements? (e.g. pull-out tests with acceptance criteria) | Website | Licensee has developed methodology for assessment of anchorage elements. Anchorage elements are inspected by visual test.
SK-23 |  | Switzerland | Slovak Republic | 07. Concrete containment structures | 73, 77 | Which is the area in the containment which is equipped with a steel liner and its tightness is checked with the periodic integral leakage test? | Website | The entire volume of the hermetic part of containment is periodically tested by the integral leakage test.
SK-24 |  | Czech Republic | Slovak Republic | 03. Electrical cables | 36 | Are all safety cables and all safety related cables included in the AMP, or only a representative sample of them is included in the AMP? | Website | Only representative samples of all safety related cable types are included in AMP.
SK-25 |  | Czech Republic | Slovak Republic | 03. Electrical cables | 36 | Could you please provide the complete list of all types of cables included in AMP? | Website | AYKY 3Bx4; 1-AYKY 4Bx16; 1-AYKY 3 x 95/185/240 + 70/95/120 6-AYKCY 3x150, 3x180, 3x240 10 AXEKVCEY 1x500/35 6-CHKCE-R 3x150; 6-CHKCH-R 3x150; N2XSEY 3x150; NHXHX 12Cx2,5 1-CXKE-V/LOCA 14x2,5; 1-CXKE-V/LOCA 7(12,24)Cx1,5; 1-CXKE-V/LOCA 4Bx25; 1-CXKE-V(J) 4x4/o/HELB; 6- CXKFE-R 1x240/LOCA 1-CHKE-V/LOCA 4Bx25; 1-CHKE-V/LOCA 4(7,12)Cx1,5; CHKE-V J 4 x1,5 LOCA 1-CHKE-V/LOCA 3 x 95/120/185 + 50/70/95 1-CHKH-V180 12Cx2,5 PvVG 1x240; PvVng 4x10 1-CYKY-J 3x185+95; 1-CYKY 3 x 95/240 + 120 CYKY 3x4; CYKY 12Cx2,5; CYKY 7Cx1,5 JYTY 7/14/19/30 x 1 KMPEVEVng 4/37 x 0,35 KPETI(-XA) 1/7 x 2 x 0,7 KPoEVng 4/7/14/27 x 1,5; KPoBVng 27 x 1,5 KMTVEV-M 8x2,5; KMTVEV-M 4x1+4x2,5 KVVGE 10x1,5 KPOSG 14x1,5 - only in deposit (no more used installed in NPP) JXFE-R 1x2x0,8 LOCA JC2(5)XF(O)E- R(V)/LOCA 4x2x1 / 8x2x0,35 / 12x2x0,35 Radox 3 GKW 300V
SK-26 |  | Czech Republic | Slovak Republic | 05. Reactor Pressure Vessels | 90 | Please, can you specify the AMP for reactor internals? | Website | A specific reactor internals AMP has been developed for all active NPPs in Slovakia where all the relevant issues related to the indentified degradation mechanisms are adressed.
SK-27 |  | Czech Republic | Slovak Republic | 05. Reactor Pressure Vessels | 63 | You mentioned, that one of the materials included in improved surveillance specimen program was material representing reactor internals. Can you specify, how do you use the obtained results of material tests in the next steps? | Website | Austenitic material 08Ch18N10T was included into surveillance specimen programme for assessment of irradiation resistance of reactor internals materials. Reactor internals material can be used for comparison with results obtained from other research projects.
SK-28 |  | Czech Republic | Slovak Republic | 07. Concrete containment structures | 77 | Which non-destructive examination methods do you use for thickness testing of hermetic steel liner? How many places are tested? Have you found corrosion on the back side of the liner? If so, what is the acceptance criterion for remaining liner thickness? | Website | For thickness testing of accessible hermetic steel liner ultrasonic thickness measurement is used. There are 150 tests points for containment in each unit. The integrity of the all hermetic steel liner is indirectly inspected by the integral leakage test.
SK-29 |  | Finland | Slovak Republic | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Website | Ageing management process is applied to standard operational conditions according to NPP design. As matters RPV operational average coolant temperature Tavg (95OC ≤ Tavg < T180) in MODE 4 (HOT SHUTDOWN) is directly connected to brittle fracture temperature of RPV. For realization of primary circuit tightness pressure test (13,7MPa) and strength pressure test (16,8MPa) is required to heat primary circuit coolant to temperature corresponding to reactor pressure vessel temperature higher than brittle fracture temperature. This is achieved by cold legs temperature higher than SOT (cold overpressure limit) what corresponds to average primary circuit coolant higher than 95OC. Allowed trend of heating is 15OC. SOT (cold overpressure limitation system) has direct impact on work of high injection pumps, boron concentrate pumps, pressurizer safety valves, relief valves and heaters.
SK-30 |  | Netherlands | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation |  | No questions. | email
SK-31 |  | Netherlands | Slovak Republic | 03. Electrical cables | 3.1.1 | It is recognized that in section 3.1.1, attention was focussed on the detection of ageing, though not on the identification of ageing mechanisms. Could you please elaborate on how the ageing mechanisms were identified? | email | Identification of ageing mechanisms was carried out based on: - R&D project "Evaluation of qualified life and ageing assessment of electric and I&C equipment" performed in Slovakia in late 90s; - operational experience; - IGALL international project.
SK-32 |  | Netherlands | Slovak Republic | 03. Electrical cables | 3.1.1, p.37 | In the tech specs of the TPR, it is stated that one of the focus groups of cables is medium voltage cables buried or in trenches. From the NAR, it is unclear which of the 0.4/1kV cables, if any, are buried or in trenches. Please state which, if any of these cables are buried or in trenches. | email | Citation p.39 last section: "Group 2 in TPR (Medium voltage cables concealed or in trenches) corresponds in terms of voltage level, to 0.4/1 kV cables. There are no buried 0.4/1 kV safety cables at the Slovak NPPs. The 0.4/1 kV cables are laid in trays in external cable ducts or in cable trenches and on the trays inside the buildings and are accessible for visual inspections."
SK-33 |  | Netherlands | Slovak Republic | 03. Electrical cables | 3.1.1, p.38 | For the EMO NPP, 43 individual I&C cables were selected for inclusion in the AMP. For the EBO NPP (Table 3-3), no I&C cables are included in the AMP. How is this justified? | email | Original safety I&C cables installed in containment (for NPP Bohunice) have been replaced within the modernization project for new qualified cables. Condition of I&C cables in NPP Bohunice is primarily assessed through the cable deposit programme. Sample deposit includes both original Russian type of cables and also new installed types. Other activities applied for condition assessment of I&C cables includes maintenance templates and calibration of measurement circuits.
SK-34 |  | Netherlands | Slovak Republic | 03. Electrical cables | 3.1.1, p.40 | In table 3-5, it is listed that Armour/shielding is not subject to any of the AMP activities. How is ageing of these cable elements monitored.? | email | For the proper shielding functionality its proper grounding is monitored within the maintenance activities.
SK-35 |  | Netherlands | Slovak Republic | 04. Concealed pipework | 4.1.1, p.47-49 | It would be beneficial to provide information about what type of steel (including standard number) is used for each concealed pipework considered in the AM, as well as pipe diameter and operating conditions. Could you please provide this information? | email | Sections between fan cooling towers and central pumping station are equipped with 1220x10mm pipes made from carbon steel STN 11 375.0. Replaced ESW pipes section from ESW outlet to concrete monolith and return pipes from concrete monolith to fan cooling towers are equipped with 813x14mm pipes made from carbon steel STN 12 022.1.
SK-36 |  | Netherlands | Slovak Republic | 05. Reactor Pressure Vessels | Ch.5 | The information provided in this NAR in its chapter 5 on ageing management of reactor pressure vessels, is to a great extent qualitative. However in the Technical Specification for the NARs, the countries are requested to report in their NARs on the acceptance and action criteria for the various ageing phenomena. Apart from indicating those criteria, it is obvious that the NARs must discuss the compliance of the reactors with these criteria. Could you please provide this information? | email | Acceptance criteria are determined for the main degradation mechanisms (irradiation embrittlement and fatigue).
SK-37 |  | Netherlands | Slovak Republic | 07. Concrete containment structures | 7.1.1 | What international codes and standards are used to build the Ageing management Programme? Reference is made to IAEA and GALL, but are other design guides also used? | email | Except for IAEA guides also international standard (EN, ISO) were applied.
SK-38 |  | Netherlands | Slovak Republic | 07. Concrete containment structures | 7.1.4 | How is trending of the results of the previous inspections/analyses used to improve the AMP programme? | email | If the trend shows a tendency to negative change of the measured parameters, the additional tests are suggested and implemented. The interval of tests and the number of inspection locations set up by the AMP are upgraded.
SK-39 |  | RPV expert group | Slovak Republic | 05. Reactor Pressure Vessels | 58-71 | The document makes no mention of using annealing as a mitigation against irradiation embrittlement. It is my understanding that the VVER-440 uses a mid-life anneal to maintain safety margins against brittle failure. Why is this not considered in the document? | expert group 2 | In time frame 60 year we do not expect annealing of RPV in Slovak NPPs based on the AMP results.
SK-40 |  | RPV expert group | Slovak Republic | 05. Reactor Pressure Vessels | 66 | The inspection techniques are referenced out to operating documentation. Are the requirements of these documents liked to the aging management system, and, if so, what structures are in place to facilitate this feedback. | expert group 2 | In-service inspection programmes are the same for all the RPV in Slovak NPPs and they are subject to regulator approval. Qualified inspection technique are used within ISI programmes.
SK-41 |  | RPV expert group | Slovak Republic | 05. Reactor Pressure Vessels | 58-71 | I understand from the documentation presented that the boundaries of the aging management are fundamentally informed by the design code. What is the strategy for dealing with threats to the Safety Case that are outside of the design code? | expert group 2 | Ageing management process is applied to standard operational conditions according to NPP design.
SK-42 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | par. 7.1.2 | 7.1.2. The title is not correct | expert group 4 | A mistranslation. Correct title should be 7.1.2. Assessment of concrete containment structures ageing.
SK-43 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | par. 7.1.2 | The content of the par. 7.1.2. do not cover the content of the WENRA document. Please clarify | expert group 4 | See the answer to question #1290. | ref to line in source file corresponding to SK-51
SK-44 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | par. 7.1.2 | The point in the par. 7.1.2. of wenra specification are not enough reported. Please clarify | expert group 4 | See the answer to question #1290. | ref to line in source file corresponding to SK-51
SK-45 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | par. 7.1.3 | It is not clear if there are “third part certification organizzation”, during the monitoring, testing, sampling and inspection | expert group 4 | The inspection tests are performed by a third party certification organization. That organization carries out all tests defined by the AMP for concrete containment structures.
SK-46 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | General | From the 7.1.3 untill the end the content are almost different from the wenra tecnical specifications. Please clarify | expert group 4 | Complementary information, which extends the thext in NAR is provided bleow. Inspections of some structures are performed on the basis of a quality assurance plan, manufacturer's recommendations and regulatory authority decisions. The next inspections were set as a result of the AMP implementation. All inspections are included in the inspection programmes with appropriate time periods and acceptance limits. The schedule is divided as follows: Inspections performed every year: - Settlement (precise levelling) - Condition of hermetic doors and hatches (visual inspection) - Local leakage tests at selected locations - Condition of containment structure surface (visual inspection) - Condition of anchorage elements (visual inspection) Inspections performed every two years: - Integral leakage test (allowable limits NPP Bohunice 13%/24hod, NPP Mochovce 5%/24hod.) - Condition of reinforced concrete (visual inspection) - Condition of steel structure (visual inspection) - Condition of coating system (visual inspection) - Condition of inside and outside containment (visual inspection) Inspections performed every four years: Reinforced concrete structure: - Concrete strength measurement (NDT inspection) - Carbonisation measurement (NDT inspection) - Concrete cracks measurement (NDT inspection) - Concrete moisture measurement (NDT inspection) - Inspection of reinforcement by geo-radar (NDT inspection) - Condition of reinforced concrete (visual inspection) Steel structure: - Condition of hermetic liner (visual inspection a UTT measurement) - Condition of non-hermetic liner (visual inspection) - Condition of anchorage elements (visual inspection) - Condition of coating system (NDT thickness measurement)
SK-47 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | 76 | The report states that "supplier has developed and implemented a methodology for assessing used lifetime of the containment. The methodology, based on weighting factor established for each assessed degradation mechanism, makes it possible to evaluate the current state of containment structures with respect to design assumptions or to compare the status on individual units". Please explain the concept of "used lifetime" | expert group 4 | For assessment of civil structures we use methodology which is based on procedures used in judical assessment. That methodology is adjusted for NPP purposes.
SK-48 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | 76 and 78 | The report suggests that visual inspections are undertaken every 4 years, but pressure tests every 2 years, periodic integral tests or once in 10 years for the integral strength test. Please explain the link between these different periodicity activities | expert group 4 | The integral leaktightness and integral pressure tests of the containment are performed in the given intervals based on decision of the regulator. Visual inspections and NDT tests are performed every 4 years according to AMP. Some tests, such as settlement measurement (geodetic methodical guide), inspection of hermetic doors and hatches is performed once a year (maintenance template). The inspection interval depends on the predicted rate of deterioration of the observed characteristics and its influence on the safety function of the structure component.
SK-49 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | 78 | The report states that "Despite that, work is constantly being carried out to improve the containment tightness", can you indicate the nature of this work | expert group 4 | For example: For NPP Mochovce, the allowed leakage is 5% / 24h. The current value of leakage is around 1%. If the change is more than 30% compared to the previous measurement of leaktightness, we need to take corrective action. As a preventive measure some improvements were done to be able to achieve the best possible result for containment leaktightness during each outage.
SK-50 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | 73 - 74 | The content of para “7.1.1 Scope of ageing management for 07. Concrete containment structures” of the Slovak Republic NAR in general corresponds to the requirements listed in section 07.1.1 of RHWG REPORT TO WENRA, but comprises quite general information on the process/procedures for the identification of ageing mechanisms. At the same time, there is no information on the methods and criteria used for selecting components within the scope of ageing management (see item “a” of para 07.1.1 of RHWG REPORT TO WENRA). There is no information on the processes/procedures for the identification of ageing mechanisms for different materials and components of 07. Concrete containment structures and associated methods and criteria (see item “b” of para 07.1.1 of RHWG REPORT TO WENRA). This information should be added to the Slovak Republic NAR or corresponding clarifications might be provided as an answer. | expert group 4 | Methods and criteria used for selecting components within the scope of the ageing management Concrete containment structures belong to Safe Class 2 according to the Atomic Act. For safety-related SSC, it is advisable to process AMP in accordance with regulatory authority and IAEA guides. The specification of the conditions for SSC selection into AMP is detail described in Chapter 2. Processes/procedures for the identification of ageing mechanisms for the different materials and components of the concrete structures There is mentioned in NAR para. 7.1.1, the basic for AMP for concrete construction structures were results of the project "Ageing Management and Optimization of NPP lifetime" in Slovakia. One part of that project was focused on selected civil structures including containment. Within the project, individual structures of the containment were identified and based on knowledge of their function, load and environment, a real set of degradation mechanisms were identified. Those degradation mechanisms can affect the functionality of each element of the structure. The obtained set of construction elements were validated with IAEA and IGALL guides and international standards. Based on the result of the listed project, the following containment constructions were included in AMP: - Concrete, - Steel reinforcement of concrete, - Steel liner, - Anchoring elements, - Steel structures, - Penetrations, hatches, hermetic doors, - Seals and sealing elements, - Protective coating.
SK-51 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | 75 - 76 | The content of para “7.1.2 Assessment of containment concrete structures ageing” corresponds to the requirements listed in section 07.1.2 of RHWG REPORT TO WENRA and comprises general information on the ageing management programmes that are applied in the Slovak Republic. At the same time: · information on the establishment of acceptance criteria related to ageing mechanisms is absent (see item “b” of para 07.1.2 of RHWG REPORT TO WENRA); · information on the use of basic standards, design, manufacturing and operating documents was taken in the ageing management of 07. Concrete containment structures; · information on the use of national and international experience is absent either (see para 07.1.2 of RHWG REPORT TO WENRA). This information should be added to the Slovak Republic NAR or corresponding clarifications might be provided as an answer. | expert group 4 | For the project referred to chapter 7.1.1, the following inputs were used: - As-built documentation of the individual Unit construction - Operating documentation, the results of maintenance programmes and operational inspections - IAEA guides and regulatory authority requirements and recommendations - Experience of an external organization The results from that project were the basis for the AMP development. Due to the fact that AMP was applied after 20 years of EBO NPP operation, a wide of operating experience - including information on corrective actions - was also used. Based on these inputs, the degradation mechanisms specified in the NAR were defined for each type of construction.
SK-52 |  | Concrete containment PCPV expert group | Slovak Republic | 07. Concrete containment structures | 78 | The content of para “7.1.4 Preventive and corrective actions for concrete structures of the containment” does not correspond to the requirements listed in section 07.1.4 of RHWG REPORT TO WENRA. This chapter should include: - criteria for taking actions; - procedures for taking actions; - description of the actions to be taken, but actually there is only general information. This information should be added to the Slovak Republic NAR or corresponding clarifications might be provided as an answer. | expert group 4 | Preventive actions Base on suggestion for realization the preventive actions can be dividing to several groups. First group includes the periodic exchange of components parts requirements, respectively requirements for periodic verification of their functionality. For example it is: - Periodic replacement of seals of hermetic doors and hatches - Verifying the proper functionality of the door locking system - Local leakage tests of hermetic doors, hatches, penetrations in order to realize prevent corrective actions in case of problem is indicated Next group of preventive actions consists of realized projects, which were not implemented as preventive measures due to the effect of degradation mechanisms, but their implementation was result of some containment components renewal. That group includes the activities performed in the framework of strengthening of construction structures to extreme external hazards. Remedial actions The proposal of corrective measures are based on the assessment results of the individual degradation mechanisms in line with acceptance criteria. The acceptance criteria are defined by the standards and licensee`s internal guides. Remedial actions are prepared by a working group whose composition and scope is defined in the licensee`s internal guides. The corrective actions are implemented timely to result of the continued degradation mechanism's non-impact the safety function of containment structural element.
SK-53 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 48 | The report states that concealed pipes situated in the main generation block are not included in the ageing management program. Could Slovakia justify this choice in relation to safety? | expert group 5 | Ageing management of these SSC is performed also through the other programmes on NPP, like In-Service Inspection, In-Service Testing, Maintenance Templates and Chemical Regimes Management.
SK-54 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 48 | Could Slovakia provide Ref. 76 of the Report, ie. the ESW pipes ageing management program? | expert group 5 | It is not possible to provide Ref. 76 (AMP of ESW pipelines). It is licensee holder document for internal use only.
SK-55 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 50 | May Slovakia justify the restriction of the ageing management program to ESW pipes only in relation to safety? | expert group 5 | For selection of pipelines to AMP a graded approach was applied (safety classification, EQR process, service conditions, PSA, materials used, operation experience). Ageing management of other pipelines is performed through the other programmes on NPP, like In-Service Inspection, In-Service Testing, Maintenance Templates and Chemical Regimes Management.
SK-56 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 51 | Could Slovakia specify if all its NPPs' ESW pipelines are equipped with corrosion loops? | expert group 5 | Pipelines on ESW at all three redundancies on both active NPPs are equipped with dedicated corrosion loops.
SK-57 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 53 | Could Slovakia indicate whether the non rehabilitated ESW pipes at NPP EBO V2 are equipped with cathode protection? Could Slovakia specify the proportion in length of the concealed ESW pipes that are currently equipped with cathode protection at EBO V2? | expert group 5 | Non rehabilitated ESW pipelines include pipelines buried in concrete monolith and pipelines equipped with PE protection. These pipelines does not have cathodic protection. Buried rehabilitated ESW pipelines from fan cooling towers to central pumping station are equipped with cathodic protection. Total length of pipelines protected with cathodic protection is 955m.
SK-58 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 53 | Could Slovakia detail how the data monitoring from the cathode protection system is used to monitor the concealed pipes? | expert group 5 | Condition of cathodic protection is carried out through the standard operational procedure. A detailed analysis of data acquired from cathodic protection system is not performed.
SK-59 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 53 | The report states that the measuring points and the inspection intervals are specified in IQAP. Could Slovakia indicate the typical inspection intervals and the types of inspection (visual, manual UT, automated UT etc.) at EBO V2 for both rehabilitated and non rehabilitated ESW pipes? | expert group 5 | Both rehabilitated and non rehabilitated pipelines are evaluated through the BPWORKS software tools. Based on BPWORKS results, interval of UTT thickness measurement is determined. For replaced pipelines visual inspection and ultrasonic test (once per 4 year) is applied. Inspections are carried out at given locations in the central pumping station and in the inspection shaft at the fan cooling towers.
SK-60 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 53 | Could Slovakia provide examples of IQAP for inspection of ESW concealed pipes at its two active NPPs? | expert group 5 | In NPP Mochovce ESW pipeline inspection is carried out according to In-service Inspection Programme which is based on a quality assurance plan (wall thickness measurements are performed once a year). In NPP Bohunice non rehabilitated pipelines placed in concrete monolith are indirectly monitored using geo-radar technique in a five year interval.
SK-61 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 54 | Could Slovakia specify on which basis the minimum allowable wall thickness of the ESW pipes is established? | expert group 5 | Minimum allowable wall thickness is established based on the calculation described in quality assurance plan. Calculation takes into account the thickness of corrosion addition to the nominal thickness of pipeline.
SK-62 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 54 | The report states that the results of the sampling, analysis and evaluation of the Fe and Cl content into the transported medium are recorded in a specific data base. Could Slovakia specify if this information is eventually provided to the BPWORKS-based ageing management system? | expert group 5 | Conservative (default) content of Cl=150 ppm is used in BPWORKS computational code. This value is higher than limit value of Cl in ESW in both active NPPs. The code does not consider the calculation with Fe content; however, it is possible to manually put both the Fe and Cl content into the calculation.
SK-63 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 55 | Could Slovakia elaborate on the relevance of the corrosion loops to assess the corrosion rate of the ESW pipe systems. Are the coupons representative of all the steel types and nuances constituting the ESW pipes? Is the environment of the corrosion loops representative of that of all the ESW pipes in terms of aggressiveness? | expert group 5 | Effect of water aggressiveness to ESW pipelines condition is evaluated through the corrosion loops. Based on the coupons weight loss in specified time period, an average corrosion rate is determined. Values obtained from corrosion loops are compared with UTT wall thickness measurements. Coupons are representative for all the steels used in ESW pipelines and environment in corrosion loops is also representative for all ESW pipelines.
SK-64 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | P 56 | Could Slovakia specify if plans exist to perform inspections in the long term of the buried pipes at EBO V2 other than that performed at the two inspection shafts? | expert group 5 | Sections of buried pipes which are not accessible for inspections through the inspection shafts are evaluated by BPWORKS software tools. Non rehabilitated pipelines placed in concrete monolith are indirectly monitored using geo-radar technique in a five year interval. Pipelines integrity is tested in a three year interval.
SK-65 |  | Concealed pipework expert group | Slovak Republic | 04. Concealed pipework | 53 | What voltage is used for decision on UTT of elbows? | expert group 5 | Technical parameters of test equipment are not presented in test protocols and they are not used in ageing assessment of ESW pipelines.
SK-66 |  | Cables expert group | Slovak Republic | 03. Electrical cables | 38 | The report list the materials used for the jacket insulation. There are no jackets made of steel or paper, or other types of materials. | expert group 3 | All the old Russian safety and safety related cables with lead (Pb) jacket originally installed in Bohunice NPP were replaced by cables with polymer jacket. At the present time there are no safety and safety related cables installed in Slovak NPPs with steel jacket. Paper insulation / jacket is not used on safety (safety related cables) in Slovak NPPs as well.
SK-67 |  | Cables expert group | Slovak Republic | 03. Electrical cables | 39 | Are there any inaccessible cables or cables in conduits (safety or non-safety cables), where visual inspection is not possible? If yes, what kind of AMP is applied for such cables | expert group 3 | All safety cables are accessible for visual inspection. Cables are installed in cable ducts, cable trenches and on the trays inside the buildings. There are no safety cables buried. The only buried cables are non safety 6kV cables to pumping station Pecenady (service water). These cables are monitored through the maintenance template activities (measurement of insulation resistance and leak current) and there is a plan for replacement of old cables to new types.
SK-68 |  | Cables expert group | Slovak Republic | 03. Electrical cables | 39 | Could you please explain the "EQR process as well as the " SMS. What is the status of the Equipment (environmental) qualification for cables on NPPs in Slovakia? | expert group 3 | Licensee has implemented Equipment Reliability Process, where NPP is divided to particular systems. For each system a System Maintenance Strategy is elaborated. For each components group within the system a Maintenance Template is elaborated where all the activities (including inspection intervals) related to maintenance of component are described. Equipment qualification was carried out for NPP Bohunice in late 90s and for NPP Mochovce in period 1998÷2003. SSCs which had not passed the qualification were replaced by the qualified ones. Safety cables and safety related cables installed in / outside containment are environmentally qualified for normal and accident conditions that are considered in place of their installation. Environment monitoring is being performed for confirmation that real conditions (temperature and radiation dose) are in line with conditions used in initial qualification. Condition of cables is periodically tested within cable sample deposit programme where qualified condition of cables in terms of elongation at break is carried out.
SK-69 |  | Cables expert group | Slovak Republic | 03. Electrical cables | 41 | The effect of the moisture on dielectric strength and insulation conditions is described, but it is not specific whether any curves, to determine the capacity of the cables reflecting the age and moisture penetration were used. | expert group 3 | As the moisture has impact on insulation conditions, effect of moisture on cables is monitored through the periodic measurement of insulation resistance on cables in operation. Measurements are performed in specific intervals and trend of insulation resistance is obtained.
SK-70 |  | Cables expert group | Slovak Republic | 03. Electrical cables | 47 | Are there any regulatory inspections focused on ageing management of cables undertaken? What is the frequency and the type(s) of regulatory inspections performed? | expert group 3 | Cables ageing management was part of following unplanned inspections: - No. 235/2014 - Long-term Operation of NPP V2 - No. 216/2016 - LTO NPP V2 Action plan - No. 215/2017 - LTO NPP V2 Action plan - No. 905/2017 - NPPs EBO & EMO AMP programs Planned inspections will be included in the 3 Year Inspection Plan for Years 2019-2022.
SK-71 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 19 | Capability of systems, structures and components relevant in terms of nuclear safety to fulfill their safety functions is considered by UJD as secured.” It is not specified although for what period of time is secured, for the period of the license, for the next PSR? | expert group 3 on other topics / expert group 1 | Generally to the next PSR (10 years), but exact (shorter) period can be determined by actual state of NPP.
SK-72 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 20 | It is mentioned that the “Generation” is a method for identify the degradation mechanisms. It should be mentioned what is meant by “Generation”. (power production?). Also, material, and supplier could be considered as inputs for identifying degradation mechanisms. | expert group 3 on other topics / expert group 1 | Generation in this paragraph means "Manufacturing" (incorrect translation). Impact of "Material" is included in "Basic Design" (quality assurance plan for safety SSC, technical condition) and also effect of "Supplier" is included in "Manufacturing".
SK-73 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 21 | The 4th paragraph, it should be clarified what are the acceptability criteria for the individual degradation mechanisms already established. | expert group 3 on other topics / expert group 1 | Acceptability criteria are described in particular AMPs for condition indicators accounted to main degradation mechanisms.
SK-74 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 31 | Numerous modifications were implemented at NPPS. It is not specified by whom were these modifications reviewed and approved, if they were reviewed by the original designer of the plant. | expert group 3 on other topics / expert group 1 | Modifications implemented on NPPs are reviewed and approved according to valid national legislation and licensee procedures for "Management of NPP modifications".
SK-75 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 28 | It is not specified whether for the update of the AMP any independent verifications and peer reviews are reqiured | expert group 3 on other topics / expert group 1 | Update of AMPs is performed according to licensee internal procedures for management of process model documentation. Independent verifications and peer reviews are not required in national legislation and licensee internal procedures.
SK-76 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 19 | Do the indicators are used (quality assurance) of the overall AMP to assess the effectiveness of the process? | expert group 3 on other topics / expert group 1 | According to the licensee internal procedures, assessment of AMP is carried out through the quality assurance internal audit once per 3 years (last audit performed in 2017 on overall AMP, AMP of RPV and AMP of SG).
SK-77 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 26-27 | Do the activities/ inspections are performed by 'third party certification organisations' ? If so, please give more details about that. | expert group 3 on other topics / expert group 1 | Activities connected to surveillance programmes are performed by organizations with acredited laboratories (VUJE, ÚJV Řež), universities (STU - testing of fire-proof coating). Environmental monitoring is partially carried out by NPP staff. Programme of In-service inspections is performed by licensee department. Part of ISI results is reviewed by "third party organization" (according to the NPP Quality Assurance Plan for Operation). Monitoring of NPP operation (In-service testing (SUP), Operability tests...) are performed by NPP staff.
SK-78 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 15 | Section 2.1 states that UJD SR requires regular reports to be submitted in accordance with Decision 1012/2013. Please confirm how often these reports are submitted and explain the approach taken to their regulatory oversight. | expert group 3 on other topics / expert group 1 | Decision No. 1012/2013 contains apart from others reports concerning ageing management: - Time-schedule of In-Service Inspections during outage (1 month before the outage) - Report on classified equipment operational modes history limited by design (2 months after the outage) - Report on reactor pressure vessel and other classified equipment life-time expenditure (2 months after the outage) - Final Report on RPV brittle fracture temperature based on RPV chain specimens tests (1 month after finalisation of the report) - In-service inspection Records (preliminary evaluation of ISI for ISI Evaluation Commission/ (before physical commissioning) - In-Service Inspections report (1 month after the outage) These reports are under competency of NRA SR and help in decision making process of the Authority.
SK-79 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 16 | Section 2.3.1.1. establishes the roles and responsibilities for ageing management. Please explain the competency requirements and training provided for personnel responsible for development of AMPs. | expert group 3 on other topics / expert group 1 | Requirements on qualification of personnel with impact on nuclear safety are given in national legislation and licensee internal procedures. "Training Programme for Preparation of Selected Personell" is developed for job position "Lifetime Management Specialist" including training and short term practice on work place.
SK-80 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 17 | Section 2.3.1.2 states that the licence holder has Ageing Management Programmes for each of the individual SSCs listed in Annex 3. It is not clear that whether the SSC's listed in Annex 3 cover all SSCs important to safety. Please explain the basis for selection of the systems identified in Annex 3. Please explain if these AMPs cover SSCs such as the fuel storage pool, and the reactor control and protection systems. | expert group 3 on other topics / expert group 1 | For each NPP the "List of SSC for Ageing Management" is developed. According to national legislation safety related SSC are included in this list. Individual Ageing Management Programme is not developed for each SSC. Ageing management of SSC is performed also through the other programmes on NPP, like In-Service inspection, In-Service Testing, Equipment qualification, Maintenance templates, management of Chemical regimes and Technical inspection activities.
SK-81 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 17 | Section 2.3.1.3. states that equipment to help mitigate certain types of events are screened into the process. Please explain whether equipment provided to mitigate the consequences of severe accidents are included within the ageing management programme. | expert group 3 on other topics / expert group 1 | Individual Ageing Management Programme of SSC for mitigation of SA consequences is not developed. Ageing management of these SSC is performed also through the other programmes on NPP, like In-Service inspection, In-Service Testing, Equipment qualification, Maintenance templates, management of Chemical regimes and Technical inspection activities.
SK-82 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 18 | Paragraph 5 on page 18 describes the process used to develop maintenance templates for critical and non-critical components. Please explain the criteria used for classifying components as critical or non-critical and provide an example to demonstrate the implications of this categorisation for inspection maintenance and testing. | expert group 3 on other topics / expert group 1 | For identification of critical components licensee holder has developed methodical guide "JE/MNA-341.01 Scoping and Identification of Critical Components" which is based on INPO AP 913. According to this guide Critical component is a equipment which failure is unacceptable and has an impact to nuclear safety or power generation. Critical component shall be monitored and included in continuous equipment reliability improvement process.
SK-83 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 26 | Section 2.3.2.6 explains that the license holder utilises benchmarking and self assessment processes (as part of its wider operating experience programme) to inform development of the AMP. Please provide an additional example where the operator has conducted benchmarking to support continuous improvement of the AMP. | expert group 3 on other topics / expert group 1 | List of benchmarking focused on ageing management conducted from 2011: 2017 - Elaboration of National Assessment Report on AM (NPP Paks, NPP Dukovany, Temelin) 2016 - AMP of civil structures (partner NPP Dukovany, Temelin) 2016 - AMP of reactor pressure vessel (NPP Dukovany) 2015 - AMP of reactor coolant pump (NPP Paks) 2015 - Fatigue assessment of primary pipeline (NPP Dukovany, Temelin) 2015 - In-service inspection of SG dissimiliar welds (NPP Dukovany) 2015 - Equipment qualification (NPP Dukovany, Temelin) 2014 - AMP of cables (NPP Paks) 2013 - AMP of reactor coolant pump (NPP Paks, NPP Dukovany) 2012 - AMP of reactor pressure vessel (NPP Dukovany) 2011 - Overall AMP (NPP Dukovany, Temelin)
SK-84 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 27 | Section 2.3.4 explains the process by which remedial actions are developed in response to findings from the licensee's monitoring, testing and sampling programme. The implementation of corrective actions (such as replacement or repair) of long life SSCs can involve significant technical challenges, lead times and costs. Please explain the process used to prioritise the implementation these remedial actions to ensure timely action is take to arrest ageing and degradation effects. | expert group 3 on other topics / expert group 1 | Licensee holder has developed an internal procedures for implementation of corrective actions within the Management of SSC modifications. Prioritization of corrective actions implementation is approved at Equipment Reliability Commission.
SK-85 |  | General AMP expert group | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 30 | Section 2.4.2 states that the effectiveness of ageing management for individual SSCs is evaluated based on the assessment of defended status indictors and acceptability criteria. Please explain the relationship between these status indicators/acceptability criteria and the reliability claims made in the station's safety analysis. | expert group 3 on other topics / expert group 1 | In probabilistic safety analysis the real status of SSC is considered based on the equipment reliability process outputs.
SK-86 |  | EC | Slovak Republic | 01. General information | 9 | Please specify frequency of regular reports to regulator on the results of ageing management programs |  | According to Decision of NRA No. 2012/2013, results of ageing management are periodically submitted to regulator as follows:: - evaluation report on lifetime RPV and selected equipment including RPV critical embrittlement temperature (2 months after outage) - final report on evaluation of RPV critical embrittlement temperature based on surveillance programme (1 months after specimen evaluation), - in-service inspection schedule of selected equipment (1 month before outage), - preliminary evaluation of in-service inspection programme (before physical start-up), - evaluation of in-service inspection programme (1 month after outage), - annual in-service inspection programme (annualy before 28 Feb).
SK-87 |  | EC | Slovak Republic | 01. General information | 10 | Please could you provide information regarding the frequency of Regular inspections carried out by ÚJD SR at the licensee |  | There was carried out set of inspections concerning ageing management: - No. 235/2014 - Long-term Operation of NPP V2 - No. 216/2016 - LTO NPP V2 Action plan - No. 215/2017 - LTO NPP V2 Action plan - No. 905/2017 - NPPs EBO & EMO AMP programs Planned inspections will be included in the 3 Year Inspection Plan 2019-2022. NRA SR inspectors also take part in In-Service Inspections Evaluation Commission.
SK-88 |  | EC | Slovak Republic | 01. General information | 14 | "The NAR was prepared on the basis of Slovak legislation and documents provided by the licence holder, the contributions from the members of the working group, the results of activities of ÚJD SR, as well as external assessments." Please specify which stakeholders were involved in the external assessments. |  | During the processing of the Topical Peer Review report, the evaluation of relevant documents has been performed by independent external experts from Slovakia and the Czech Republic . The invited high experienced external experts from the leading engineering, design and research organizations involved in the assessed fields (STU Bratislava - Faculty of Civil Engineering, Welding Research Institute, TES Třebíč s.r.o.) have been included in the purpose-based inspection team.
SK-89 |  | EC | Slovak Republic | 01. General information | 6 and 8 | "The NAR report was prepared by ÚJD SR in close collaboration with SE…documents provided by SE, a. s.": Are all these documents included in the references in section 10 of the report? |  | Chapter 10 References of NAR provides a list of documents directly referenced in the text of NAR. It does not document complete set of documents used in AMP or produced in AMP implementation.
SK-90 |  | EC | Slovak Republic | 01. General information | 9 and 10 | Specific AMP guides are mentioned for cables, pipes of Essential Service Water System, RPV,and Main Generating Unit. Are all these documents included in the references in section 10 of the report? |  | All these AMPs are included in section 10 Reference as follows: - [67] JE/NA-311.09-11 Cable Ageing Management Program, - [76] JE/NA-311.09-09 Ageing Management Program for the ESW piping, SE, a. s., 2015, - [83] JE/NA-311.09-02 Ageing Management Program for the reactor pressure vessel, SE a. s., 2014, - [86] JE/NA-311.09-12 Ageing Management Program of the main generating unit including containment, SE a. s., 2015.
SK-91 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 15 | 2.1 National regulatory framework The basic requirements of "ÚJD SR for the development, introduction and implementation of SSC ageing management programs are set out in ÚJD SR Decree No. 430/2011 [19] and the safety guide [5].This guide is based on recommendations of the IAEA requirements [9], safety guide [1] and WENRA requirements [2]." A more elaborative description would assist understanding of the actual national requirements for the AMP. |  | The Authority, within the scope of its competence under Atomic Act, approves the documentation of the quality management system for applicants for authorization holders.Each change of this documentation which includes quality plans and the requirements for aging management of the classified facilities (according to UJD Decree No. 431/2011 on Quality Management) is approved by NRA SR. In addition, the aspect of plant aging management is assessed in the frame of PSR, too. The rules and requirements for the PSR are laid down in the Decree No. 33/2012 dedicated to PSR. All documents mentioned above are published on the web site of NRA SR in English.
SK-92 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 15 | 2.1 National regulatory framework "For the ageing management, ÚJD SR requires regular reports according to the Decision [3] from NPP EBO V2 and NPP EMO concerning:" Please specify the frequency of these reports |  | According to Decision of NRA No. 2012/2013, results of ageing management are periodically submitted to regulator as follows:: - evaluation report on lifetime RPV and selected equipment including RPV critical embrittlement temperature (2 months after outage) - final report on evaluation of RPV critical embrittlement temperature based on surveillance programme (1 months after specimen evaluation), - in-service inspection schedule of selected equipment (1 month before outage), - preliminary evaluation of in-service inspection programme (before physical start-up), - evaluation of in-service inspection programme (1 month after outage), - annual in-service inspection programme (annualy before 28 Feb).
SK-93 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 15 | 2.2 International standards 1st parag: Shouldn't the WENRA safety Reference levels be also listed here as they are used a basis for the UJD SR safety guide [2] BNS 1.9.2/2014 setting the national requirements for AM for NPPs? Also this section should describe the way the licensee uses (as implied in the summary pg 9 second parag: "The licence holder is involved in the following international projects: IAEA IGALL,..." ) the IAEAs IGALL programme in the development of the overall AMP . |  | Yes, the WENRA sefety reference levels had to be included in the list of international standards provided in NAR as they were used as a basis for setting the national requirements for AMP for NPPs. Licensee (Slovenske elektrarne, a.s.) is a member of IAEA IGALL project since 2011 in WG1 (mechanical components), WG2 (electrical, I&C and EQ group) and WG3 (civil structures). IGALL is used as a support reference document for update of AMPs.
SK-94 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 20 | 2.3.1.3 "Based on assessment ... the “Report on the State of the Power Plant Equipment” is developed" how often is the report updated? |  | Quarterly - three month interval.
SK-95 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 30 | 2.5.2 According to the WENRA Specifications the licensee should add in this section its conclusion on the adequacy of the overall AMP and its application to the plants. |  | Adequacy of overall AMP is assessed within PSR each 10 year. Results of PSR are reviewed by a third independent party. Scope of assessment is given in Decree No. 33/2012 and its amendment No. 106/2016.
SK-96 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 32 | 2.6 Please specify in this section all the reports, apart from PSR and new or updated AM documentation specified already, in the area of AM which the license is required to submit periodically to the regulator including the respective frequency. In addition please describe also here the regulatory inspections of the implementation of the AMP and their frequency. For example the 1st parag under the title 2.7 could be further completed and moved under 2.6. |  | According to Decision of NRA No. 1012/2013, results of ageing management are periodically submitted to regulator as follows: - Time-schedule of In-Service Inspections during outage (1 month before the outage) - Report on classified equipment operational modes history limited by design (2 months after the outage) - Report on reactor pressure vessel and other classified equipment life-time expenditure including RPV critical embrittlement temperature (2 months after the outage) - Final Report on RPV brittle fracture temperature based on RPV chain specimens tests (1 month after finalisation of the report) - In-service inspection Records (preliminary evaluation of ISI for ISI Evaluation Commission/ (before physical start-up) - In-Service Inspections report (1 month after the outage) - annual in-service inspection programme (annualy before 28 Feb).
SK-97 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 33 | 2.7 "In the second half of 2017, ÚJD SR carried out an inspection of ÚJD SR No. 905/2017 with the participation of external experts. The inspection was focused on check of ageing management programs in NPP EBO V2 and NPP EMO." please specify the external experts participating the inspection |  | During the processing of the Topical Peer Review report, the evaluation of relevant documents has been performed by independent external experts from Slovakia and the Czech Republic . The invited high experienced external experts from the leading engineering, design and research organizations involved in the assessed fields (STU Bratislava - Faculty of Civil Engineering, Welding Research Institute, TES Třebíč s.r.o.) have been included in the purpose-based inspection team.
SK-98 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 16 vs 88 | 2.3.1.1 and Annex 1: The title of Annex 1 is referring to Lifecycle management "Group" which group is not shown in the following "organisational structure". If the group refers to the yellow highlighted parts of the scheme please clarify. Note that the "Lifecycle management group" is referred to as "Ageing management group" in section 2.3.1.1. Please clarify. |  | The correct name of group should be "Ageing Management Group" as it is in section 2.3.1.1, not "Lifecycle Management Group". This group refers to yellow highlighted parts in Annex 1 (designation 23131 on right bottom side of chart).
SK-99 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 16,88,89 | 2.3.1.1 and Annexes 1 and 2 It appears not so easy for the reader to follow the responsibilities and organisation of the AM process and the correspondence between description in section 2.3.1.1 and in Annexes 1 and 2. Please clarify. |  | Annex 1 shows the place of Lifecycle Management Group in the licensee organization chart and Annex 2 shows the detail description of AM activities including all the departments and groups involved in AM process. There is a correspondence between section 2.3.1.1 and Annex 2.
SK-100 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 17 vs. 9.10 | 2.3.1.2 "For units in the construction phase, NPP MO3&4, the relevant AMP will become effective as of the date of physical start-up of unit 3 of NPP MO3&4." On the other side in the Summary (pg. 9 and pg. 10 ) the AMP for essential service water system (incl. concealed pipes) and the one for Main generating unit (incl. containment) are mentioned to become effective for the new units before their commissioning while the AMP for cables and RPV appear to be already valid also for the new units. Please can you clarify these apparent inconsistencies. |  | Regulator requirement on ageing management of MO34 units is that the individual AMPs for NPP MO34 shall be valid before their first commissioning. Some individual AMPs are already valid for NPP MO34 (like Overall AMP, AMP for cables...). Implementation of AMPs on NPP MO34 is linked schedule of NPP MO34 commissioning.
SK-101 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 19,20 | 2.3.1.3 Are there indicators included, as recommended in the WENRA specifications, for assessing the performance of the AMP process? |  | Performance of the AMP process is assessed within PSR each 10 year. Results of PSR are reviewed by a third independent party. Scope of assessment is given in Decree No. 33/2012 and its amendment No. 106/2016.
SK-102 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 2.7 and pages therein | 2.7 Regulator´s assessment of the overall ageing management program and conclusions It appears that the regulator has performed a comprehensive assessment of the licensee's AMPs for the four operating units based on the documents provided by the licensee and the performed inspections. The overall assessment concluded that the overall AMP in Slovakia is appropriate and acknowledges among its strengths the maintenance of a AM database by the licensee highlighting the need to continuously update it. One identified weakness concerns the accuracy of the SSC drawings vs actual status. |  | No answer is provided. The item 2185 is considered comment, not the question. | ref to SK-102
SK-103 |  | EC | Slovak Republic | 02. Overall Ageing Management Programme requirements and implementation | 88 vs 89 | Annex 1 and 2 : the group 23100 appears with different (translated) name between Annex 1 and 2 i.e. Nuclear Design Engineering and Engineering for nuclear projects, respectively. To avoid confusion please use consistent group titles . Similar inconsistency in (translated name ) between ANNEX 1 and 2 is observed for department 23150. Other departments listed in ANNEX 2 are not visible in the organigram of ANNEX 1 e.g. the Maintenance, revisions and metrology chemical control diagnostics. please indicate in Annex 2 in which department these services belong. Showing the department numbers is good and supports clarity. |  | Yes, the text in NAR and Annex 1 and Annex 2 is not consistent. Correct name of group 23100 should be Nuclear Design Engineering as it is in Annex 1. Correct name of group 23150 should be Technical Revisions and Services as it is in Annex 1. Annex 1 and 2 does not represent the same subject. Annex 1 shows the place of Lifecycle Management Group in the licensee organization chart and Annex 2 shows the detailed description of AM activities including all the departments and groups involved in AM process. That is the reason why all departments presented in Annex 2 are not visible in Annex 1.
SK-104 |  | EC | Slovak Republic | 03. Electrical cables | 36 | Does the surveillance specimen program have samples of all cable types included in the AMP? |  | Surveillance specimen program includes representative cables which cover all cable types (from the material point of view) installed in containment.
SK-105 |  | EC | Slovak Republic | 03. Electrical cables | 39 | It would be helpful to have the insulation material indicated for the cable types. |  | Insulation material of cables listed in Table 3-4 is as follows: - No. 2,3,8,9,16,17,20,28 - Polyvinylchlorid PVC - No. 1,4,5,6,7,13,14,15,21,22,23,24,25,26,27 - Crosslinked Polyethylene XPE - No. 18,19 - Polyethylene PE - No. 10,11 - Etyhylene Propylene Rubber EPR - No. 12 - Flame Retardant Non Corrosive polymer compound FRNC
SK-106 |  | EC | Slovak Republic | 03. Electrical cables | Chapter 4 | Frequency of in-service inspections is missing. |  | Probably the question is addressed to the topic 04. Concealed pipework. Frequency of In-service inspections of ESW pipelines is determined in programmes for In-service inspections. In NPP Mochovce ESW pipeline inspection is carried out according to In-service Inspection Programme which is based on a quality assurance plan (wall thickness measurements are performed once a year). In NPP Bohunice non rehabilitated pipelines placed in concrete monolith are indirectly monitored using geo-radar technique in a five year interval.
SK-107 |  | EC | Slovak Republic | 04. Concealed pipework | 48-57 | Bohunice NPP and Mochovce NPP: Apart from the essential service water (ESW) lines (and fire fighting water supply lines, which do not require AMP because of their material) there is no coverage of other concealed piping systems with adequate AMP and ISI programs. What is the reason for this? Some occasional inspection for the other concealed piping, i.e. Pump discharge pipes of super-emergency feeding of steam generators, circulating cooling water pipes, decarbonised water pipes, makeup water pipe to refill the ESW system and diesel fuel pipes, would be desirable. |  | Condition monitoring and assessment of all safety related pipelines is performed through the following NPP programmes: Ageing Management Programme, In-Service Inspection, In-Service Testing, Maintenance Templates and Chemical Regimes Management.
SK-108 |  | EC | Slovak Republic | 05. Reactor Pressure Vessels | 67-69 | Frequency of in-service inspections is specified indirectly. Please could you provide information on the actual frequency of the different inspections. |  | The NDT in-service inspections of RPV are performed in a regular 8 year cycle. Inspections are carried out: -from the inner surface during the outage with complete export of fuel (8 year cycle) -from the outer surface during the common outage (8 year cycle) Time displacement in performing of both inspections is 4 years.
SK-109 |  | EC | Slovak Republic | 05. Reactor Pressure Vessels | Chapter 5.2, page 70 | In page 70 is mentioned: "For the power uprate of nuclear units in NPP EBO V2 and NPP EMO, calculations were made for the fluency of fast neutrons falling on the RPV wall at an increase reactor power of 107% for a long-term operation." Question: As a result of the power uprating, is the brittle reference temperature TKF of the critical vessel materials also updated? and checked the validity of the pressure-temperature limit curves? |  | New transition temperature trend curves of RPV materials were developed following the calculations for fast neutron fluence due to power uprate throughout the plant long term operation. Consequently, pressure-temperature limit curves for normal/abnormal operation conditions, accident conditions and also limits for pressure tests were recalculated after that.
SK-110 |  | EC | Slovak Republic | 07. Concrete containment structures | 77 | What is the frequency of the basic construction and technical survey? Can you describe more the triggers for performing a special construction and technical survey. |  | See the answer to question #1285. | ref to line in source file corresponding to SK-46
SK-111 |  | EC | Slovak Republic | 07. Concrete containment structures | 77 | Monitoring of the environment: Have any inconsistencies between the real and design values of temperature and radiation in the exposed areas been revealed? What actions are triggered in case such inconsistencies are seen? Is there any monitoring of groundwater chemical content or other environmental factors that could affect ageing of concrete/steel structures? |  | Inconsistencies between the real and design parameters have been observed only in temperature (radiation dose is below the design value). Civil structures components are not affected by this temperature difference. Issue of temperature difference is managed through the appropriate corrective actions within the PSR (safety factor "Equipment qualification"). Monitoring of groundwater chemical content is carried out.
SK-112 |  | EC | Slovak Republic | 07. Concrete containment structures | 78 | Periodic integral leak test. Please can you provide the acceptance criteria for the leak test. Did past leak tests reveal any deterioration in leak rate that could be attributed to ageing of the containment structures? |  | For NPP Bohunice is allowed leakage 13% per 24 hour. Actually it is about 5%/24h. For NPP Mochovce is allowed leakage 5% per 24 hour and actually it is about 1,5%. If the change is more than 30% compared to the previous measurement of leakage, we need to take corrective action. The limits were set up by nuclear regulatory authority.
SK-113 |  | EC | Slovak Republic | 07. Concrete containment structures | 76-78 | Section 7.1.3: The description provided is very much lacking in detail and does not allow to develop a good picture of exactly which kind of inspections are performed, what are the acceptance criteria and how they allow to assess the presence or absence of the different ageing mechanisms listed on pages 75-76. |  | See the answer to question #1285. | ref to line in source file corresponding to SK-46
SK-114 |  | EC | Slovak Republic | 07. Concrete containment structures | Chapter 7 | Status monitoring and inspection frequency is not specified |  | See the answer to question #1285. | ref to line in source file corresponding to SK-46
SK-115 |  | EC | Slovak Republic | 07. Concrete containment structures | general | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | There are parts ot the containment structures which are not accessible for inspection, e.g. part of the hermetic lining, reinforcement. In case of reinforcement, the corrosion damage can impact. That degradation is associated with signs of concrete damage and it can be observed by set up inspections. The integrity of the all hermetic steel liner is indirectly controlled by the integral leakage test.
SI-1 |  | Poland | Slovenia | 03. Electrical cables | 55 | Referring to the R&D program testing method Indenter modulus (IM) acceptance criteria for thermally and radiation aged cables what are the objectives of this R&D programme or please provide its general description how this programme is used? | Website | There are few EPRI Reports associated with indenter modulus and confirming corelation between IM and EaB. Since they are elaborating commonly used cable types and generic types of insulation, NEK decided to prepare samples of its own cable types, and perform additional temperature aging to test insulation and jacket to the end of life conditions. Main reason was to get acceptance criteria that could be used for on line, field testing of installed cables in specific environment without removing materials.
SI-2 |  | Bulgaria | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | p. 37 | On page 37 in point XI.M2 /Water chemistry/, the last paragraph is written, that water chemistry program is consistent with the guidelines of EPRI “ PWR Primary Water Chemistry Guidelines”, EPRI “PWR Secondary Water Chemistry Guidelines” and Siemens KWU Secondary Water Chemistry Guidelines. Would you explain why do you use the guideline of Siemens KWU and is there difference between the requirements of EPRI и Siemens? | Website | Siemens KWU guidelines or chemistry specifications are the basis for the Secondary Water Chemistry Program, since Siemens was the vendor of steam generators. In most cases EPRI Guidelines are more strict and conservative and for that reason EPRI Guideline values are adopted and included in NEK Chemistry Specifications.
SI-3 |  | Bulgaria | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | p. 45 | On page 45 in point 2.3.4 is mentioned that in the year 2000 after 17 years of NPP operation two SG were replaced due to SG tubes degradation. Would you provide some information about degradation of the tubes of the new SG and is there opportunity new SG to be in operation until the year 2034. | Website | Results of Eddy Current Testing (ECT) showed that there is no active degradation mechanism on SG tubes in the Krško NPP. This also can be applied to support structures of the secondary side due to visual inspection performed in previous outage. NEK performs SL (Sludge Lancing) every outage and IBL (Inner Bundle Lancing) every second outage to keep secondary side as clean as possible. There is opportunity for new SG to be in operation during extended lifetime of the Krško NPP regarding projected design lifetime of the component. It also depends on the condition of U tubes (ECT results) and other parts of SG in the future.
SI-4 |  | Bulgaria | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | p. 45 | On page 45 in point 2.4 a) is written that as result of independent review of the NEK AMP and review by the regulatory autority SNSA are found 15 inconsistencies и 15 deficiencies. Would you give examples of inconsistencies и deficiencies discovered? | Website | These inconsistencies/deficiencies were found as a result of the independent review during AMP licensing procedure conducted by independent reviewer and all of them were resolved until the SNSA decision for AMP approval. Most of them are connected to programs and procedures revisions based on the GALL requirements. In time of SNSA review NEK had just introduced the modified operating procedures (MOP). The benefit of introducing the MOP is that no more important insurge/outsurge transients could appear during the heat-up/cooldown operations after on. SNSA decided that the TLAA's (which were finished before) shall reference MOP, and for example this decision generated 6 deficiencies. Based on them NEK revised 6 TLAA's reports.
SI-5 |  | United Kingdom | Slovenia | 05. Reactor Pressure Vessels | 78 | Section 5.1.3 - The information provided on detected flaws is very useful. What type of defect has been detected with the new RPV-ISI 2010 results and what is their approximate location? | Website | As mentioned in Section 5.1.3 the driving code for fourth ISI interval is ASME Section XI, 2007 Edition, with 2008 Addenda. Certain reactor vessel welds requiring UT should be examined per mandatory ASME Section XI, Appendix VIII. NE Krško should use Appendix VIII as implemented by the industry Performed Demonstration Initiative; EPRI PDI Program (Appendix VIII as implemented by the industry Performance Demonstration Initiative - EPRI proprietary) for ultrasonic examination systems. Three new reportable indications are directly related to the application of the new more sensitive tip-diffraction technique (non-amplitude technique) instead of using amplitude techniques (Distance Amplitude Curve-DAC). One indication is located in intermediate to lower shell weld (BW-3) and two indications are located in lower head ring to lower shell weld (BW-4). Signals of newly found indications were evaluated and reported according to new PDI producers. Signals can be interpreted as metallurgical inclusions within the weld or heat affected zone (i.e. slag inclusions) and are acceptable in accordance with ASME Section XI, Table IWB-3510-1.
SI-6 |  | United Kingdom | Slovenia | 05. Reactor Pressure Vessels | 81 | Section 5.2 and 5.3 – page 81 - Section 5.2 states “Until now NEK has no experience with indications related to PWSCC” but section 5.3 states that “In the past, the Krško NPP addressed different experiences, such as primary water stress corrosion cracking and based on that some important modifications i.e. the reactor pressure vessel head replacement and structural weld overlays on pressurizer were implemented”. These two statements contradict each other. Please clarify. | Website | These two statements do not contradict each other. NEK statement in section 5.3 "In the past, the Krško NPP addressed different experiences,..." is related to general industry experience with PWSCC (e.g. Davis Besse NPP in the USA, PWSCC on Reactor Vessel head penetration welds). NEK itself did not have any indications related to PWSCC which is correctly said in the statement in section 5.2 "Until now NEK has no experience with indications related to PWSCC". However, in response to the above mentioned industry experience related to PWSCC involving 600/82/182 weld material in the reactor vessel head penetrations, NEK has preventively replaced the reactor vessel head.
SI-7 |  | United Kingdom | Slovenia | 04. Concealed pipework | 66 | Section 4.1.2 refers to NEKs participation in a number of EPRI led programmes for R&D and buried pipework committee. Has this included involvement in the development or use of BPWORKS? It hasn't been mentioned in the report, so if it hasn't been used, is there a reason why? | Website | NEK has not been involved in development of BPWORKS. NEK has BPWORKS but it hasn't been used. NEK took conservative approach and try to achive 100% of inspected pipework lenght. As it was mentioned in Section 4.1.1 c), "NEK does not have too many concealed pipework … All concealed pipework is considered of high importance".
SI-8 |  | United Kingdom | Slovenia | 04. Concealed pipework | 67 | Sections 4.1.2 and 4.1.3.1 refer to NEK's early adoption of guided wave ultrasonics for demonstrating pipe integrity. Please provide some further detail on the guided wave inspections of the ESW and Diesel Generator Fuel Oil, including for example; the equipment used, the range achieved, any difficulties encountered etc. Has the learning and operational experience of using this technology been shared publicly through EPRI and if so, where might this be found? | Website | Service companies that provide GW UT inspections used Teletest and Wavemaker instruments. Both equipment had reached ranges from 6 to 20 m from the single position depends on bitumen coating thickness. It was needed 6 holes in the ground to acquire data to cover total length of SW pipework (cca. 100 m). OE can be reached through EPRI NDE Center membership.
SI-9 |  | United Kingdom | Slovenia | 04. Concealed pipework | 67 | Final paragraph of Section 4.1.2 on this page refers to NEK's goal to increase inspection coverage to 100% of pipe surfaces and lengths. Given that a judgement has been made that the pipe is in a satisfactory condition for the next 25 years, (paragraph 2 on page 67), what is the reason for trying to achieve this metric? Also, when do NEK anticipate delivering this goal? | Website | Present GW UT technology is not able to provide reliable inspection results for the outside surface of the pipework embedded in the concrete structure due to high sound attenuation. In the total lengths of the concealed pipework there are very small portions of uninspectable lengths. Development of the NDE technology capable to collect data in these portions will enable NEK to reach 100% coverage.
SI-10 |  | United Kingdom | Slovenia | 04. Concealed pipework | 68 | The first paragraph of section 'Inspection activities for Diesel Generator Fuel Oil' explains that two locations were inspected. Were these locations speculative/randomly selected or targeted as bounding locations based on the approach discussed in the last paragraph of page 64 (for example because these locations are more highly susceptibility to degradation or have a higher consequences of failure)? | Website | These two mentioned locations were selected because they are easy accessible with minimal digging in the ground. For the inspection of the rest of the pipework lengths, a massive excavation and destruction of very important structures was needed that would not be reasonable and safe. That destruction would be done in the case of found degradation on inspected locations, but this was not the case (extension of inspection scope). Inspected locations were free of any degradation.
SI-11 |  | United Kingdom | Slovenia | 04. Concealed pipework | 69 | The second paragraph on this page explains that only internal inspection of the pipework has been performed due to restrictions to the application of the GWT probes. This visual inspection will only give an indication of the pipe internals and as such, will only confirm that the corrosivity of the fluid being conveyed is being managed. There is no account for the pipework externals. Has NEK considered any other techniques through optioneering studies to feasible solutions to supplement the information gathered of the pipe internals | Website | Correct, inside VT inspection cannot be credited for the outside surface inspection. The total length of the DO pipework is about 2 m and on this length there are three elbows that are not inspectable reliably by GW UT. The decision was made to perform inside VT and in case of any degradation found, the whole pipework would be excavated by digging and inspected by GW UT. Because this pipework is in function only during DO tank filling from the truck tanks, it could be inspected. Because the condition of bitumen coating above ground was excellent and the VT did not detect any degradation on the inner side, it was concluded that excavation for GW UT in concrete would be unreasonable and dangerous.
SI-12 |  | Finland | Slovenia | 03. Electrical cables | 57 | It is said “Cables in the adverse environment are sampled in accordance with EPRI TR-107514”. The EPRI report text about cable sampling is very short. Could this and testing of the samples be explained more? | Website | The list of cables included in program are sampled from adversed environment or operating conditions. A statistical model for additional sampling from the reference EPRI TR-107514 is used for passive equipment such as pipes or electrical cables. The deviation is treated within the framework of the NEK corrective action program, and NEK accordingly expands the sample. NEK expands sample in case of finding degradation in accordance with its PM program. For instance, if adverse environment location with few cables, that cannot be removed, would be found, all affected cables could be included in scope of PM activities.
SI-13 |  | United Kingdom | Slovenia | 05. Reactor Pressure Vessels | 81 | The report states that the vessel head has been replaced (as did a number of others world-wide including Sizewell B in the UK) but has Krško also performed a weld overlay on the pressuriser? Please provide some details, for example, when it was detected and how and what method of overlay was used? | Website | The topic of the national report Chapter 5 was exclusively Reactor Vessel pressure boundary so no details on pressurizer weld overlay were included in the report but are provided hereafter. Various pressurizer nozzle assemblies of Krško NPP have bi-metallic nozzle-to-safe-end and safe-end-to-pipe welds using material with known susceptibility to Primary Water Stress Corrosion Cracking (PWSCC). In 2004, a comprehensive PWSCC susceptibility assessment of these nozzle assemblies has been performed and it was determined that this matter is of high importance to safety (as was the case industry-wide for comparable pressurizer nozzle arrangements). The Full Structural Weld Overlay (Full SWOL) was found as the most appropriate solution and this was applied in 2010 over the pressurizer Alloy 82/182 welds. The full structural weld overlay consists of a deposit of weld reinforcement on the outside diameter of piping, component and associated weld. The Full SWOL was applied over one 14-inch Pressurizer Surge Nozzle Assembly, two 6-inch Pressurizer Safety Valve Nozzle Assembly, one 6-inch Pressurizer Power Operated Relief Valve (PORV) Nozzle Assembly, and one 4-inch Pressurizer Spray Line Nozzle Assembly to prevent possible cracks on nozzles and to allow 100 % nozzle inspection with qualified ultrasonic techniques as required by ASME code Section XI.
SI-14 |  | Switzerland | Slovenia | 03. Electrical cables | 60 | Textline43: Is the software platform COSMY from NEK or a product from a supplier? | Website | The software was developed and provided by supplier.
SI-15 |  | Switzerland | Slovenia | 03. Electrical cables | 61 | Textline13: Is the health report out of the ageing management software platform COSMY? Is it also used for other electrical equipement? | Website | No, health report is prepared by cable aging responsible engineer in accordance with internal PM procedure for cables. Health reports are prepared for all programs and systems not just for cables. Cable aging software platform is not used for other electrical equipment.
SI-16 |  | Bulgaria | Slovenia | 03. Electrical cables | p. 62 | Within the regulator Assessment of the ageing management processes Cable Aging Management Program TD-2D (CAMP) issued in 2010, the regulator considered that “The general SNSA opinion is that CAMP is quite well developed, but also some weaknesses are identified.”Would you please give some details about those deficiencies? | Website | On page 63 are wrriten all details about main technical weakness under point 3.3 c). In the meantime NEK already corrected some deficiencies at the beginning of 2018 by issuing Rev. 1 of ADP-1.4.459, and Rev. 0 of PME-4.353 procedure.
SI-17 |  | Bulgaria | Slovenia | 05. Reactor Pressure Vessels | p.74 | Would you please clarify whether the thermal ageing was considered as well as possible ageing mechanism? | Website | The materials used in the pressure boundary of the NPP Krško Reactor Pressure Vessel are ferritic steels SA-533 and SA-508, which are either rolled or forged depending on the element of the RPV. According to NUREG-1801, Rev.2, Section XI.M31 thermal ageing embrittlement is applicable to Cast Austenitic Stainless Steel and therefore this program is not applicable to NEK Reactor Pressure Vessel pressure boundary materials.
SI-18 |  | Finland | Slovenia | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Website | When designing individual Ageing Programs according to NUREG-1801, all operating conditions relevant for a particular ageing mechanism (this may include safe shutdown conditions) shall be considered. However, a general statement which operating conditions present the biggest challenge to material ageing programs cannot be given. One such example is the ageing mechanism of material embrittlement due to reactor vessel irradiation. On one hand, the biggest effect on material properties due to fast neutron flux is incurred at power operation conditions since these conditions give the highest neutron flux. On the other hand, the final operating limits to preclude fracture due to irradiation have to be determined also for low temperatures and pressures (such as experienced during cold shutdown conditions) because the material is less ductile at these low parameters. To conclude, depending on the ageing mechanism all relevant operating conditions must be taken into account but a general statement as to which operating condition represents the biggest challenge for ageing management in general cannot be given.
SI-19 |  | Czech Republic | Slovenia | 03. Electrical cables | 54 | "The cable jacket is not considered a significant part of the cable from the perspective of the ageing management program……." Does it means the jacket can crack? | Website | No, this is not related to the possibility of cracking of the jacket. The reason that cable jacket is not considered a significant part for the AMP is explained in EPRI TR 1003057. In EPRI report, it is explained that the cable jacket are designed for mechanical and fire protection of the cable insulation. The material of the jacket can be leading indicator of accelerated aging of electrical insulation in harsh environment. According to EPRI references, jacket cracking does not affect functionality of electrical insulation due its mechanical and fire protection function. But, NEK does not use it as acceptable but we immediately repair or replace damaged cable and additionally move cable away from heat source (rerouting).
SI-20 |  | Czech Republic | Slovenia | 03. Electrical cables | 54 | "…visual inspection and indenter modulus testing of cable jackets is considered as the leading indicator of primary insulation conditions" The correlation between jacket and insulation ageing to assess insulation condition from the jackets modulus should be known. | Website | Correct-Internal owen aging was implemented and acceptance crirteria developed and correlation between jacket and insulation modulus as well.
SI-21 |  | Czech Republic | Slovenia | 03. Electrical cables | chapter 3.2 | "EPRI 10003057…following 60 year service limiting environments temperatures are stated for these materials EPR 75 °C, XLPE 86.6 °C……." I didn´t check this reference. But it cannot be generally stated, that e.g XLPE cable can be used for 60 years at 86.6 °C. It always depend on many factors like crossling, amount and type of stabilizers, fabrication etc. To trust literature data without experiments is not good. EPRI 1013475 gives lower temperature values | Website | Those referenced values are general, and first estimation and information but internal harsh environment is set at much lower values such as 50°C that are evaluated, tested and measured in local harsh environment. Actually EPRI TR 1013475 on page 10-3 have the same temperature for different type of insulation like is stated in our report. Anyway, the plant actual data from cable manufacturers are checked with specific harsh environment, and not a general values.
SI-22 |  | United Kingdom | Slovenia | 04. Concealed pipework | 64 | The last paragraph on this page states "inspection locations are selected based on susceptibility to degradation and consequences of failure". It is not clear whether this approach is in accordance with a specific published standard or programme for risk based inspection, or have NEK produced their own? Please explain the basis of the risk based approach and summarise how this has informed the forward inspection strategy. Has this been used to inform inspections for both TD-2Z and TD-1Z1 for the open-cycle service water programme? | Website | NEK has not used the risk based approach. NEK has limited length of buried pipings, less then 250m and 2 tanks and nearly 100% inspection is possible. NEK has taken the most conservative approach, which is in accordance with NUREG-1801. Both tanks and more then 80% of piping have already been inspected and results are very satisfying. Only those parts of the piping that are harder to access have not been inspected. Main idea is to collect a data about current pipework conditions as much as possible. Such an approach is used for both AMP programs TD-2Z and TD-1Z1.
SI-23 |  | United Kingdom | Slovenia | 04. Concealed pipework | 64 | Paragraph 3 on this page says "only one inspection should be conducted during each 10 year period beginning 10 years prior the entry into the period of extended operation”. Please clarify when the first of these inspections and subsequent inspections will be performed. | Website | First inspection was performed in 2016. Second will be performed in 2026.
SI-24 |  | United Kingdom | Slovenia | 04. Concealed pipework | 71 | In the last paragraph of this page, a weakness has been identified with the TD-2Z programme. It is not clear whether the same weakness affects the TD-1Z1 programme. Please explain the impact of this weakness on the TD-1Z1 programme. | Website | The mentioned weakness - omission of technical implementing procedures - was referred to the TD-2Z program only, which is the main program for concealed pipework (in the meantime, this weakness has already been eliminated in the new revision of the program). No such weaknesses were detected in the TD-1Z1 program.
SI-25 |  | Netherlands | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 2.2/p14 | The decision to not take further action on finding 3 of the OSART mission seems to have been taken on purely formal grounds. For the sake of continuous improvement a genuine judgement of the finding would be more appropriate. Please elabortate on that. | email | Probabilistic risk-based approach is often used for optimization and relaxation of the requirements. NEK will follow such practice in industry and possibly change the stategy, but this is not the case at the moment. In addition, since NEK is following also NRC regulation and US industry approaches, we did not find such cases from the NRC for such approach.
SI-26 |  | Netherlands | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2/p27 | GALL-report: It is unclear how the GALL report is used in the overall AMP. Please elaborate on that. | email | It is described in Overall AMP subchapters how requirements of GALL were being fulfilled by the Krško NPP within processes of scoping and screening, AMRs, AMPs, TLAAs. The Table 2-4 is provided in the report with the Krško NPP implemented programs and procedures in compliance with GALL ,and afterwords also descriptions of AMPs.
SI-27 |  | Netherlands | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2p36 | Section 'e' on page 36 suggests that AMP changes are only done when the GALL report is updated, where section 'f' suggests that changes are also coming from external operating experience. Can this be explained better? | email | As it is described in the report, the AMP changes within the updated GALL report, and also based on possible applicable plant operating experiences, which are included into the NEK Corrective Action Program database. All these inputs are used as input to change AMPs.
SI-28 |  | Netherlands | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2p36 | Does Slovenia also make use of International Reporting System (IRS) for Operating Experience and Incident Reporting System for Research Reactors (IRSRR) to find AM issues or to provide AM events to other countries? | email | Slovenia uses IRS and IRSRR databases to find possible AM issues applicable for the Krško NPP or RR TRIGA, or to provide events to that databases. National coordinators for both databases are from the SNSA.
SI-29 |  | Netherlands | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 2.4/p48 | INSEG: which R&D programmes are followed? SNSA: What are the R&D results that SNSA provides? | email | The Krško NPP is currently involved in few R&D programs for cables aging management, as it is described in section 3.1.2.1 of national TPR report. The relevant R&D issues are also provided to the Krško NPP from SNSA, for example last year Institute Josef Stefan provided project exercise regarding parameter influence irradiation embrittlement of RPV, and consequently expected lifetime of the Krško NPP as required by the SNSA. The SNSA provided these results also to the Krško NPP. Independent Safety Evaluation Group (ISEG) has the responsibility to find all relevant worldwide R&D issues, and put them into CAP program as it is written in the report.
SI-30 |  | Netherlands | Slovenia | 03. Electrical cables | 3.1.3.5 / p.58 | Does the TD-2D CAMP contain any provisions for identifying unexpected degradation? | email | Different degradation effects are expected to be identified in accordance with GALL. TD-2D CAMP does not contain additional provisions for identifying unexpected degradation. If such unexpected degradation would be found, it would be analyzed within plant Corrective action program, and Cable Aging Program would be updated.
SI-31 |  | Netherlands | Slovenia | 03. Electrical cables | 3.1.3.5 / p.58 | Are there any activities undertaken within the TD-2D CAMP to interpret the findings of previous (historic) inspections in order to detect possible trends in deterioration? | email | It was accomplished in LR AMP project, and is already included in TD-2D to check OPEX and historic values or deteriorations or trends of tested values if accomplished (i.e. insulation resistance, surveillance and calibration difficulties with connections,...). Some cables included in scope of CAMP are originated from historic operating experience.
SI-32 |  | Netherlands | Slovenia | 03. Electrical cables | 3.2 / p.60 | Does the outcome of the NEK research on the effects of high doses on cable insulation match with the observed ageing of the cables exposed to higher radiation? | email | Yes, the first research results are showing correlation between temperature and radiation effects tested with IM. In plant no such high doses were found. Maximum 60 year cumulative doses measured are not more than 40-60MRad. Cables are qualified for 200MRad. Some cables exposed to high doses, were tested and showing no significant signs of aging.
SI-33 |  | Netherlands | Slovenia | 03. Electrical cables | 3.3 / p.62 | (especially if the answers to the previous two questions of NL is 'no') Is the COMSY predictive tool verified with historic measurements? | email | First predictive tool is simplified, and was based on linear dose law that was confirmed with recent internal research.
SI-34 |  | Netherlands | Slovenia | 04. Concealed pipework | 4.1.1, p.65 | What type of degradation mechanisms are expected/identified ? (e.g. according to the IGALL tables) | email | The identified ageing/degradation mechanisms that are managed by TD-2Z program are general corrosion, pitting corosion, crevice corrosion, corrosion due to microorganisms (MIC), lining/coating degradation and fouling.
SI-35 |  | Netherlands | Slovenia | 07. Concrete containment structures | 7.3 | Evaluation of cracks is used for trending. Does the outcome of the trending influence the programme for the upcoming period? E.g. extra inspections, other techniques or preventive maintenance et cetera. | email | NEK concrete shield building does not contain any critical cracks. NEK Structures Monitoring Program (Technical observation of buildings and structures, TD-2N) provides measurement with freqvency 2 times per year for existing cracks. Cracks depth are measured once per 6 year according to the same program, i.e. TD-2N program. NEK would not allow any progressive (active) crack to grow. In case a progressive crack will be found, NEK will open a corrective action in its Corective Action Program and the problem will be thorougly analysed. Based on analysis results, a corrective action plan with required actions and time schedule will be established.
SI-36 |  | RPV expert group | Slovenia | 05. Reactor Pressure Vessels | 73-84 | I understand from the documentation presented that the boundaries of the aging management are fundamentally informed by the ASME rules. What is the strategy for dealing with threats to the Safety Case that are outside of the scope of ASME? | expert group 2 | In addition to the provisions of ASME B&PV Section XI, Section III there are also other important contributing entities providing the input to ageing mechanisms and material inspections. NUREG-1801, which is the basis for all NEK Ageing Programs, includes non-ASME based requirements, originating from industry-wide experience or other independent experts. Also, NRC provides non-ASME based rulemaking through 10CFR50.55a and this is taken into account in Ageing Management Programs.
SI-37 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 86 | Aging management requires the condition assessment for different types of structures and structural elements, such as secondary structures, anchorage elements, water-proofing sealings, drainage, coatings, fire-retarding sealings, etc. Are all these types included in the inspection programs? | expert group 4 | All these types are included in Technical Observation Program of Buildings and Structures (TD-2N) and in complementary Fire Protection Program (TD-6). NEK has in place the Area Temperatures Monitoring, which is part of the NEK Technical Specifications (NEK TS). NEK TS contains in the Table 3.7-8 list of the all important buildings and rooms that are listed together with these areas temperature limits. The temperatures in each of the areas shown in Table 3.7-8 shall be observed to be within its limit at least once per 12 hours.
SI-38 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 86 | How are the fire protecting structural elements monitored? | expert group 4 | In the Krško NPP the following fire protection structural elements are monitored based on plant specific programs: fire penetrations, fire doors, fire dumpers etc. Mentioned fire structural elements are mostly visualy checked and also its operability is being verified.
SI-39 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 86 | Are there specific testing and inspection requirements for safety related anchorage elements? (e.g. pull-out tests with acceptance criteria) | expert group 4 | All safety related anchorage elements, including also that of the concrete shield building are visually inspected according to the requirtements of ASME OM Code for operation and maintenance of nuclear power plants. So far no pull-out test was performed or planned and so no acceptance criteria have been established for such tests yet.
SI-40 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 87 | The foundation below grade is covered with a waterproofing membrane. Can this membrane be inspected, how is its tightness and the protection of the concrte structure verified in the long term? | expert group 4 | The NEK waterproofing membrane is in general not accessible and can't be inspected. The shield building waterproofing membrane could be inspected opportunistically only. NEK inspects concrete moisture content before any work on it and so far there is no evidence of moisture intrusion.
SI-41 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 88 | In addition to the visual inspections of the concrete surfaces, do you consider using onsite instrumental inspections and laboratory material testing as part of the aging management? (e.g. carbonation progress, corrosion potential of reinforcement, material strength, concrete cover depth, ...) | expert group 4 | According to the Structures Monitoring Program TD-2N, NEK performs concrete sample test with frequency once per 6 years. Sample of concrete is taken opportunistic when the plant is performing modification, where the wall penetration is necessary. So far the samples are taken from Auxiliary Building (AB), Control Building (CB), Intermedate Building (IB), and other concrete structures. No such modification has been performed until now on Reactor Shield Building, and so no sample of Reactor Shield Building concrete is available for material testing you have asked for. The Reactor Shield Building concrete is the same as concrete that had been poured for constraction in AB, CB or IB structures. Laboratory material test reports of taken samples show satisfactory results. There is no corrosion of the reinforced steel. The concrete strenght and concrete cover depth are satisfactory, and concrete carbonation is under the limit.
SI-42 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 88 | The steel containment is embedded in the reinforced concrete foundation block (Fig. 7-1 in the report). Is it possible to monitor the condition of the concrete, in order to assess the adequate protection of the steel shell from corrosion? | expert group 4 | NEK can not monitor the condition of the Reactor Shield Building foundation mat, because it is inaccessible. Between concrete and steel shell, there is a moisture barrier. NEK maintenance procedures assured that the moisture barrier stay intact. The Reactor Shield Building annulus has controlled atmosphere, and only there where the moisture barrier is accessible and so visible, can be monitored. So far there is no indications of the steel shell corrosion.
SI-43 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 90 | How are acceptance criteria for the monitored settlements? What is the long term experience on settlements? | expert group 4 | NEK is performing settlement measurements twice a year (April, October). NEK concrete structures and soil characteristics enable low level settlements. Perhaps this is a reason why acceptance criteria are not found among NEK documentation. From year 1981 to october 2015 settlement for rapper R1 is 6.2mm. The majority of this number is attributed to primary consolidation. The long term experience indicates that the settlements are well stabilized. For more than last 20 years the measured values are inside of the measurement uncertainty.
SI-44 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 91 | In which time intervals are the containment structures inspected and how are the results documented (different values are mentioned in the report)? How many periodic AM reports are available so far for Krsko NPP? | expert group 4 | NEK concrete shield building is being inspected twice per year. Results of the inspections (april, october) are documented in a yearly report. From the year 2010 to 2017, the 8 periodic AMP reports of technical observations of buildings and structures have been issued.
SI-45 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 91 | How are acceptance criteria for the inspected concrete structures defined? (crack width and depth, crack patterns, carbonation depth, prestress loss, ...) | expert group 4 | Acceptance criteria is defined in the program TD-2N. Carbonation depth shall be less then the concrete cover thickness. The NEK concrete shield building contains no prestressed concrete part.
SI-46 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 91, 92 | How are the structures and the structural elements assessed which are inaccessible for visual inspections? (indirect/indicative methods?) | expert group 4 | Concrete shield building is mostly accessible structure. Inaccessible part for visual inspections is below ground level part of concrete structure. Ground water analysis has been performed 3 times per year.
SI-47 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 92 | What is "Element 4 for sample size .." referring to? | expert group 4 | Element 4 is meant the 4th element from GALL 10-elements/attributes of AMP. The information is found at the page 29 (Element 4: Detection of aging effects).
SI-48 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 93 | Have there been "Exceptional inspections .." carried out so far? If yes, what were the findings? | expert group 4 | No.
SI-49 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 94 | Visual inspections according to ACI 201.1 R-08 are performed since 2016. How were the criteria for the earlier visual inspections? | expert group 4 | Since 2016 the visual inspections according to ACI 201.1 R-08 have been formalized and ACI 201.1 R-08 visual forms used. Technically the criteria have not been changed.
SI-50 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 96 | Krsko NPP started the systematic material sampling of concrete structures in 2016. Are there earlier samples and test results available? How is the collection and investigation of concrete and reinforcing steel from structural interventions (reconstruction, partial demolition, ...) organized? | expert group 4 | Samples are taken on occasion when maintenance work or modifications are being implemented. There are no earlier samples and test results. Collection and investigation of concrete samples is organized within the AM program TD-2N (Technical observation of buildings and structures).
SI-51 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 86 | The report describes the shield building as "relatively leak tight" and separately as "high degree of leaktightness during normal operation and under accident conditions". Please clarify as these two descriptions are different. | expert group 4 | There is no absolute leak tightness and both expressions mean a small leakage. First description pretains to shield building and the second description is refered to the steel containment of the Krško NPP. The most important and regulated by law is leak tightness of steel containment. For environmental protection the negative pressure of the reactor building annulus (space between steel containment and shield building) is under surveillance test according to the requirement from the NEK Technical Specifications and that is why the shield building must be relatively leak tight. In case of an accident the ventilation starts automatic and potential leakage from the steel containment will be pushed trough the filters in order to limit radiological consequences to environment.
SI-52 |  | Concrete containment PCPV expert group | Slovenia | 07. Concrete containment structures | 92 | Please explain what is meant by "The results of predictive maintenance are used to monitor the condition of buildings and structures" | expert group 4 | Predictive maintenance is referred to technical observations of buildings and structures. Experience gained by the past predictive maintenance influence the future predictive maintenance (e.g. scope, frequency, methodology).
SI-53 |  | Concealed pipework expert group | Slovenia | 04. Concealed pipework | 71 | Do the programs TD-1Z1 and TD-2Z cover ageing management of the pipe connections (welds, flanges, bolts, etc) and pipeline sections embedded in the concrete structures? | expert group 5 | Yes they do, although such sections are very rare in the NEK and consist only of a few concrete wall penetrations. Program TD-2Z requests VT of the flexible pipe joints (SW system) that include bolting. Flanges (DO system) are only above ground and accessible for VT. Inspection method on the portions of the pipe sections embedded in the concrete provides only limited results.
SI-54 |  | Concealed pipework expert group | Slovenia | 04. Concealed pipework | 67 | "NEK follows industry and science research and development in the area of new methods, to increase its inspection capabilities. The goal is to achieve 100% inspections of total surface and lengths": please give more information about the timetable and the methods that NEK has developed to reach this goal. | expert group 5 | NEK does not develop NDE methods, but follows the new development available in the industry. That is confirmed by the fact that GW UT has been applied in NEK since 2003 at the time it was at early stage of the field application. Any new NDE technique or method that can increase inspection coverage to 100% will be, if feasible, used in NEK.
SI-55 |  | Concealed pipework expert group | Slovenia | 04. Concealed pipework | 70 | When will the second cycle of concealed pipework ageing management inspections be conducted by the licensee? | expert group 5 | With closing first cycle NEK has confirmed very good condition of concealed pipework. As NEK is very proactive in this case, second cycle will start not later than in year 2020. Priorities are minor corrosion indications on SW discharge lines in order to establish monitoring and trending.
SI-56 |  | Concealed pipework expert group | Slovenia | 04. Concealed pipework | 72 | In the conclusions on page 72 it has been written that the weaknesses described at page 71 "can be relatively easily eliminated and this will be done by the Krsko NPP by the end of the year" and so by the end of 2017. Has the TD - 2Z program been reviewed to include the implementing procedures for dectection of ageing effects? | expert group 5 | A new revision (rev. 4) of the TD-2Z program was issued in October 2017. It includes the needed technical implementing procedures developed by NEK, including some procedures developed by contractors that provide guided wave ultrasonic inspections and magnetic flux leakage inspections.
SI-57 |  | Cables expert group | Slovenia | 03. Electrical cables |  | Aging Management Software Support Platform (COMSY) is used to evaluate cable measurements and to calculate the residual lifetime of cable with regards to cable environment. On which criteria it is based? | expert group 3 | First calculation of residual lifetime of cable insulation is simplified, based on Arrhenious Law for temperature and linear law for radiation that was used at qualification. Actual harsh environment is taken into account for calculations.
SI-58 |  | Cables expert group | Slovenia | 03. Electrical cables | 59 | HTK-insulated cables seems to be more temperature resistant than EPR-insulated cables. Could you please detail the material use in HTK cable between conductor and EPR insulation ? | expert group 3 | HTK (High Temperature Kerite) is EPR based material, but it is proprietary name and formulation of Kerite Cable company, and we do not have much of additional information about formulation, only general data that are available from qualification reports.
SI-59 |  | Cables expert group | Slovenia | 03. Electrical cables | 60 | Dose rate and oxygen concentration could have a strong influence on results of irradiation tests. Could you please provide the dose rate under which the irradiation test of 100 MRad have been performed by NEK? | expert group 3 | All our (1E) cables are Nuclear qualified for 200Mrad total integrated dose. Qualification dose rates were lower than 1Mrad/h
SI-60 |  | Cables expert group | Slovenia | 03. Electrical cables | 60 | Could you detail “tangent delta” criteria associated with “Good” and “Study” range for insulation material on MV-cables as used in Krško NPP ? | expert group 3 | In accordance with EPRI reference for pink EPR insulation used in NEK MV-cables three acceptance criteria are in use: For Std Dev TD at U0: between 0.1E-3 and 1.E-3 for study and > 1.E-3 for action For Diff TD 2U0-U0 : between 3 and 8 for study and > 8 for action For mean TD at 2U0: between 15.E-3 and 30.E-3 for study and > 30.E-3 for action
SI-61 |  | Cables expert group | Slovenia | 03. Electrical cables |  | Has IM (Indenter Measurement) been performed during initial qualification process after accelerated ageing sequence (thermal + irradiation) ? If not , how are the IM measurement on site correlated with the state of degradation simulated by accelerated ageing test during the qualification process of cables ? | expert group 3 | IM testing acceptance criteria was developed in year 2011, and detailed description is given in #1 answer to Poland Question. During development of IM criteria, it was accomplished separate for temperature and separate for radiation. Samples of old cables, manufactured in plant construction time (~1979,) and were taken from warehouse and from field. No IM test were conducted during initial qualification of cables in 1979. | ref to SI-1
SI-62 |  | Cables expert group | Slovenia | 03. Electrical cables | 23 | Are there any AM/maintenance program for buried/concealed cables. | expert group 3 | TD-2D-CAMP program in general cover all cables. So also buried/concealed cables are covered with CAMP program. Watertight design of underground manholes (MHE), and sloped underground conduits assuring dry cables. Preventive maintenance activities are: 1. Visual inspection with pumping of collected water in lowest MHE; 2. Visual control of accessible cables in MHE and boroscope for buried/embedded conduits; and 3. Diagnostic testing of all underground MV and sample of LV power cables (insulation resistance, IP, TD-tan d, PD, Z,...).
SI-63 |  | General AMP expert group | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 14 | From the chapter 2.2 of the report resulted that the AMP implemented by NEK follows mainly the US approach taking into account the recomandation provided by GALL AMP rather than IAEA IGALL AMP. Is there any regulatory agreement with regard to the selection of the technical standards used in AMP? Will NEK consider the IAEA IGALL AMP in the future for improvind its AMP process? | expert group 3 on other topics / expert group 1 | With decision issued in June 2012, the SNSA approved AMP itself, and NEK Safety Analyses Report (SAR) changes. After the detailed review of the AMP documentation, SNSA also confirmed that AMP for the Krško NPP is also in compliance with national legislation, namely the national code Ionizing radiation protection and nuclear safety act (ZVISJV), and Rules on operational safety of radiation or nuclear facilities (JV9). The selection of US NRC AMP standard (NUREG-1801; i.e. GALL Report) methodology for the Krško AMP Project have been also regulatory agreed by the SNSA. Even so, and beside that the current NEK AMP programe fully meets the requirements of NUREG-1801 – GALL, in addition the Krško NPP monitors and addresses foreign operational experience, and other guidances and standards in this area, to make changes to the AMP programe when it is necessary to improve the overall plant AMP processes. The SNSA, and the Krško NPP also follow IAEA IGALL project, and connected AMRs, AMPs and TLAAs, and plant representatives have also started with participations in IAEA IGALL working groups, and SALTO missions. We had, as stated in the report, also AMP module during conducted OSART mission, which confirmed, that AMP is in general compliance with IAEA guidance.
SI-64 |  | General AMP expert group | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | N/A | Comment: The description of the AMP for nuclear installations in Slovenia covers all elements required by Topical Peer Review 2017 - "Ageing Management Technical Specification for the Na-tional Assessment Reports" | expert group 3 on other topics / expert group 1 | It means that the technical specification has been followed.
SI-65 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 13 | 2.2: International standards. No walk downs have been performed to evaluate the impact of non safety components to safety related SSCs. The corrective actions (page 14, ad1) seem to go in the direction of seismic evaluation. However, will evaluation of environmental conditions (e.g.: chemical, vibrations, hot spots (thermal and radiological),...) be investigated as well? |  | During the aging management review project, no specific walkdowns have been performed because the walkdowns for IPE (Individual Plant Examination) were performed, and reported few years before. Seismic design was a main concern. With walkdown report from year 2003, issues related to impact of non-safety related over the safety related were resolved. Chemical conditions are not an issue, because use of chemicals in NEK is under stringent procedure. All important vibrations are monitored, and alarms come into control room. Vibrations that could limit the fatigue life of the components are not allowed. NEK has in place the Area Temperatures Monitoring, which is part of the NEK Technical Specifications (NEK TS). The NEK TS contains the Table 3.7-8 where all important buildings and rooms are listed together with their area temperature limits. The temperatures in each of the areas shown in Table 3.7-8 shall be observed to be within its limits at least once per 12 hours. The AMP (ED-4, Reactor vessel Surveillance program) have in scope components which are exposed to the strong neutron fluens.
SI-66 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 16 | 2.2.2.a: it is not clear who is responsible for the AMP: in the text it states that "the technical director has the overall responsibility for development and maintenance of programs related to AMP (incl record keeping). However, the next paragraph it states that "the maintenance manager is the dedicated AMP manager". It is also not clear how the operations department is included in this organisation. |  | As it is stated in the report, the Maintenance Manager is the dedicated AMP manager during the living phase of the AMP program, so he is responsible for AMP. The Operations department is included through their written procedures in the framework of NEK AMP program.
SI-67 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 28 | 2.3.2.a: no Operations documents are listed; what is the link with daily power plant operations? See also row 5 |  | The link with daily power plant operations is through MECL(Master Equipment Component List) database, when components or structures from the daily reports are listed as AMP flag "Yes". The other direct link with daily operations are working orders, which are main implementing forms for differnt activities also used for AMP activities. All data is remained in Preventive Maintenance database (PMA).
SI-68 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 29 | 2.3.2.b: Gall 10 elements are used as key elements to asses ageing. Regulator declares that NPP is conform this standard, but unfortunately no concrete examples are given. |  | All programs under AMP consider 10 elements or attributes according to GALL methodology. For the purpose of TPR report, all attributes are described and summary descriptions of programs are provided (see sect. 2.3.2.b, pages 28 to 34, and sect. 2.3.3, pages 37 to 44).
SI-69 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 31 | 2.3.2.c: processes for the identification of ageing. In the table some GALL programs are listed as "not credited". Please explain what is meant by that. Moreover, some programs can be quite important to asses ageing (e.g.: loose part monitoring, buried piping and tanks inspection) |  | This programs, listed as "not credited", have been deleted in NUREG-1801, Rev. 2 (GALL). Ageing assessment of buried piping and tanks are made through XI.M41. There is also very detailed plant procedure for loose part monitoring.
SI-70 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 36 | 2.3.2.f: use of internal and external OE: how are transients recorded and put in relation with AMP (e.g.: SCRAM, opening of PORV/MORV, cold water pressurizer injection, cold safety injection, etc.…) |  | After each outage, the transients report is provided by the Krško NPP with added transients that had happened during the finished cycle. After established AMP, the content is extended according to Aging Management Review recommendations, and report fulfills also requirements from Aging Management Program based on NUREG-1801 (Metal fatigue). OE are in general followed by plant based OE database and corrective program, where AMP flag is available as a potential or root cause. This is the key parameter also for AMP periodic review (every 5 years).
SI-71 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 36 | 2.3.3. The monitoring and inspection program is quite extensive. However, leak management (or follow-up) does not seem to be included |  | Leak management is part of the immediate corrective measures under Corrective Action Program. All such activities are not part of the AMP, but are part of regular corrective and preventive maintennace programs.
SI-72 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 36 | 2.3.3. Monitoring and inspection program. Technical specifications require to periodically test valve opening/closing times and checks of the safety related pumps (flow vs pressure, vibrations,...). These tests can be clear indicators for degradation (for example due to ageing). How are these incorporated in the AMP? Are these tests considered to be tests on "active" systems and thus excluded from the AMP? |  | Yes, these tests are considered to be tests on active components, which are managed under the Preventive Maintenance Program in accordance with the requirements of 10 CFR 50.65, “Requirements for monitoring the effectiveness of maintenance at nuclear power plants”. This is also part of the plant surveillance program where all activities and potential deviations are resolved within Corrective Program.
SI-73 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 45 | Section 2.4.a): are the 15 deficiencies found by the independent review the same as the 15 deficiencies found by the regulatory authority? |  | No they are different. These inconsistencies/deficiencies were found as a result of the independent review during AMP licensing procedure conducted by the SNSA and all of them were resolved until the SNSA decision for AMP approval. Based on these defficiencies, an Action Plan was developed and later also completed and verified by SNSA.
SI-74 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 46 | 2.4.c: Modification management: "the responsible engineer for each modification should perform initial screening of affected AMP equipment). Does this mean that the project leader of the modification is responsible to check if there are ageing issues? Can such a project leader belong to the another department than maintenance or engineering (e.g.: Operations/radioprotection/...) and thus not necessarily have detailed knowledge on the AMP process? How is the organisation sure that update of the AMP plans does not get forgotten (5 year review excluded). |  | AMP engineer is a reviewer (member) of the modification team. Project leader for individual modification is trained to perform initial screening of components and structures, which belong to AMP (MECL AMP flag "Yes"). During the development and review of each particular modification, ageing assessment is done by AMP specialists. This is done for each modification.
SI-75 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | 52 | 2.7. Regulator's assessment: it is clarified that although all plans have been created, technical implementation is lacking for a number of plans. This information was not found in the operator's assessment and it would be nice to see it added (or to get an idea of the work that needs to be performed). |  | As described in the chapter dedicated to concealed piping (few weaknesses), this SNSA observation is connected with "Buried and underground piping and tanks program", and relevant implementing procedure based on this program. In general major part of implementing procedures under AMP are already implemented in the Krško NPP.
SI-76 |  | EC | Slovenia | 02. Overall Ageing Management Programme requirements and implementation | Chapter 2.4, page 48 | In page 48 it is mentioned "NEK is a single reactor site plant, with Westinghouse NSSS, and alone it is not able to conduct its own extensive R&D as required for the purpose of aging management program development.". Question 1): Has NEK access to the R&D results of the EPRI program 2) Is NEK involved in some way in the research activities of the NUGENIA European network?. In positive case it should be mentioned. |  | 1. Yes, the Krško NPP has access to the R&D results of the EPRI program. 2. The Krško NPP is currently not involved in NUGENIA project directly, but indirectly yes, because Institute Jozef Stefan as authorized institution in Slovenia does. The connection at different projects assures this connection.
SI-77 |  | EC | Slovenia | 03. Electrical cables | Generic 53-63 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found. |  | Groups are mentioned in the NAR. All cables are included in CAMP. They are divided in few groups due to required activities: - Low voltage cables (power, control, instrument), - High Voltage Low Level Current instrumentation cables, - High voltage cables, - Low voltage underground power cables.
SI-78 |  | EC | Slovenia | 03. Electrical cables | Generic 53-63 | Environmentally qualified cables have no follow-up of ageing? |  | EQ program performs environmental/conditions monitoring, what is a case also for EQ cables. The purpose of monitoring is to confirm or revise equipment specific initial environmental qualification evaluation design inputs, and qualification conclusion due to new or more severe degradation mechanisms. EQ cables may be located in environment, which can be more severe than considered in original qualifications. It is continuous EQ task to monitor environment and equipment by walk-downs (identification of degradations), collect and evaluate conditions data based on permanently or temporary installed measurement equipment/detectors. This follow-up task is required to be performed by EQ group and maintenance personnel. NEK EQ group has performed also systematic evaluation of EQ equipment locations to identify, measure and evaluate radiation and temperature hot-spots. Hot-spots has been evaluated and consequently following (as applicable) actions were performed: - Equipment (Cable) Qualified Life reduction (shorter than determined in initial qualification evaluation) - Equipment (Cable) replacement - Equipment (Cable) relocation to avoid hot-spot (cable rerouted to avoid hot-spot)
SI-79 |  | EC | Slovenia | 03. Electrical cables | Generic 53-63 | Are there any practices to follow up ageing with laboratory tests on naturally aged cables (cable deposits, or replaced cables)? |  | Yes, naturally aged cables are sampled from field with different operation environment, and they were tested or are ready for additional laboratory tests with predefined acceptance criteria.
SI-80 |  | EC | Slovenia | 07. Concrete containment structures | 92 | In the numbered list at the bottom of page 92, in item 1: - the text mentions visual inspection of concrete areas that includes inaccessible and underground areas. Please can you clarify and give further details of how these areas are considered in the ageing management programme. - reference is made to 'Element 4' for sample size and justification of areas to be inspected. Please can you clarify where to find this information in the report. |  | Inaccessible part for visual inspections is below ground level part of concrete structure. Ground water analysis has been performed 3 times per year. Results of the ground water analyses justifies that the environment to which the concrete structure is potentially exposed doesn't support degradation processes triggered by potential water chemistry effects. Element 4 is meant the 4th element from GALL 10-elements/attributes of AMP. The information is found at the page 29 (Detection of aging effects).
SI-81 |  | EC | Slovenia | 07. Concrete containment structures | 92 | In the numbered list at the bottom of page 92, in item 2, could you describe the actions that would be triggered in case the groundwater is found to contain chlorides or sulphates at levels exceeding the acceptance criteria given on page 94. What is the frequency of the groundwater chemistry investigations? |  | The frequency of the groundwater chemistry analysis is 3 times per year. So far, NEK has no problem indicated coming out from these ground water chemistry analysis. In case that any of the chemical elements, relevant for these effects exceeds the allowable limit, NEK will open corrective action in its Corective Action Program and the problem will be thoroughly analyzed and actions and recommendations defined. A corrective action plan with a time schedule will be established.
SI-82 |  | EC | Slovenia | 07. Concrete containment structures | 93 | The main activities for regular periodic observation…, 3rd bullet 'cracks depth measurement'. Please can you provide more information on the circumstances under which these measurements are performed (criteria for deciding which cracks require depth measurement). |  | According to the aging management program TD-2N, all concrete structures inspections are performed based on ACI 349.3R-02. For the previously identified cracks, the depth should not increase and if it does, the causes should be explored and analyzed in possible details.
SI-83 |  | EC | Slovenia | 07. Concrete containment structures | 93 | The main activities for regular periodic observation…, 4th bullet 'periodic testing of materials and laboratory tests on samples'. Please can you provide more information on the circumstances under which these tests are performed (frequency, criteria for deciding when to perform tests, which kind of tests). |  | Periodic testing of materials and laboratory tests on samples are carried out once per 6 years for shield building in the Krško NPP, as it is foreseen/required by plant AM program TD-2N. Tests are performed based on an environment/material combination. Probable aging mechanisms and aging management program are provided in Aging Management Review process and documented in the AMP documentation.
SI-84 |  | EC | Slovenia | 07. Concrete containment structures | general | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | Reactor Shield Building foundation mat is inaccessible part of the containment concrete shield building structure, which is included in the NEK AMPs. It is underground and therefore inaccessible. Ground water analysis is performed 3 times per year. Results of the ground water analyses justifies that the environment to which the Reactor Shield Building foundation mat is potentially exposed doesn't support a potential additional chemically induced concrete degradation processes.
NO-1 | 1 | Cables expert group | Norway | 03. Electrical cables | 29 | Please clarify whether each specific category of cables that is considered of particular importance for safety is addressed in a specific ageing management programme. (HBWR and JEEP II). |  | The AMP do not differ between safety related cables and other cables. The cables are grouped according to where they are installed and inspection is performed with respect to radiation exposure. Therefore, there is a room for improvement in the AMP for electrical cables at HBWR. For JEEP II, some safety-related cables are changed as part of a preventive management system as they are rarely accessible.
NO-2 | 2 | Cables expert group | Norway | 03. Electrical cables | 30 | What is frequency of tests in LIRA-technology in the research reactor HBWR? |  | This is not specified in the AMP, but will be performed when faults are detected.
NO-3 | 3 | Cables expert group | Norway | 03. Electrical cables | 31 | Please provide more details for acceptance criteria related to ageing management for cables on HBWR and JEEP II. |  | There are currently no formal acceptance criteria but expert judgement based on experience (HBWR and JEEP II).
NO-4 | 4 | Cables expert group | Norway | 03. Electrical cables | 34 | The statement in the report “HBWR plans to extend the program to include power cables in the future”, does it mean that the current AMP for cables covers only measurement cables? |  | The sentence referred to is inaccurate and should not have been included in the report. The power cables HBWR do have are supplying power to heaters and motors, and these cables are included in the AMP.
NO-5 | 5 | Concealed pipework expert group | Norway | 04. Concealed pipework | 39 | Were corrective measures or plan established taking into account to INSAAR-team (2017, JEEP II) recommendations/suggestions? If yes, may you provide these measures related to concealed pipework? |  | JEEP II is now re-assessing its approach in the current AMP, by re-categorization and re-classification of the SSC, which will be submitted to the regulatory authority as part of the licensing process in 2018. This will form the basis for a renewed AMP established before 2019. Concealed pipework will be part of this program.
NO-6 | 6 | Concealed pipework expert group | Norway | 04. Concealed pipework | 40-41 | It is stated that there are a very few critical pipes for both research reactors. What ageing mechanisms/phenomena were identified? Why these pipes are called “critical”? |  | HBWR: Only one concealed pipe in the primary circuit contains radioactive material. The pipe is situated in air and only internal ageing mechanisms are considered. The condition of other accessible pipes are considered by IFE to be representative for this piping. For HBWR, IFE make a technical assessment which includes feedback from an independent technical assessment by a third party organization. The technical assessment is used to demonstrate that the condition of other accessible pipes are considered to be representative for the concealed pipework. JEEP II: There is concealed pipework related to the water outlet of the reactor, and the emergency cooling system, e.g. critical systems. The pipes are situated both in dry air and water, hence the ageing mechanism is considered only from internal degradation mechanism such as corrosion and pipe wall reduction. The pipes are called critical because of their relevance for safety.
NO-7 | 7 | Concrete containment PCPV expert group | Norway | 07. Concrete containment structures | 58 | With reference to Section 7.1.3. Monitoring, testing, sampling and inspection activities for concrete structures, what is the timeframe envisaged for establishing a comprehensive AMP, including a formalized inspection or monitoring program for the concrete in the JEEP II reactor? |  | See question 5. A renewed AMP will be established in 2018. A first look at AMP for concrete will be part of this program. | ref. to NO-5
NO-8 | 8 | EC | Norway | 01. General information | 5 | Are there any plans to extend the lifetime of HBWR beyond 2021? If so, has a licence prolongation been initiated? |  | Yes, IFE is currently preparing the application for new license. The IFE board will make a decision this summer regarding continued operation of the reactor. IFE is required to apply for a new license within the deadline of 31. December 2018.
NO-9 | 9 | EC | Norway | 02. Overall Ageing Management Programme requirements and implementation | 7 | IAEA INSARR missions are mentioned. Are there any plans for any further IAEA missions for HBWR, in particular related to ageing management? |  | IAEA have performed an ISCA in march 2018. There are currently no further plans for a new IAEA missions at HBWR.
NO-10 | 10 | EC | Norway | 02. Overall Ageing Management Programme requirements and implementation | 29 | It is noted that an AMP is under development at JEEP II and will be implemented in the coming years. Is there a deadline for its development and implementation? |  | IFE have implemented a plan which involves a) re-categorization and re-classification of the SSC, b) implementation of already planned AMP activities during summer maintenance period in 2018, and then subsequently revision of the AMP before the end of 2018.
NO-11 | 11 | EC | Norway | 03. Electrical cables | Generic 29-35 | The NAR should list the groups of electrical cables included within the AM. Such list cannot be found, although HBWR has implemented an AMP. |  | See question 1. | ref. to NO-1
NO-12 | 12 | EC | Norway | 03. Electrical cables | Generic 29-35 | According to the report, both HBWR and JEEP II have formally established AMPs, but in both cases the cable ageing management does not seem to be very comprehensive. |  | The current AMP for electrical cables is not adequate and needs to be developed at both HBWR and JEEP II. This includes developing grouping according to safety level of cables and definition of inspection frequency and method. Regarding JEEP II, INSARR suggested a revision of the overall approach regarding AMP, for example electrical systems and concrete are being specifically included in the revised program.
NO-13 | 13 | EC | Norway | 05. Reactor Pressure Vessels | Chapter 5.1.1, page 45 | In the page 45 is indicated: "The irradiation- induced shifts in transition temperature are also smaller for the weld material. The weld material is therefore not included in the ongoing material surveillance program.” Question: Is this in accordance with the theoretical prediction? For instance base on the Cu, Ni and P content in the weld material and the neutron fluence. |  | This is based on Charpy testing of the material. Base material, welds and Heat Affected Zone (HAZ) have been tested and the base material has a clearly higher transition temperature and is thus the limiting material in the RPV.
NO-14 | 14 | EC | Norway | 07. Concrete containment structures | 55 | most information provided does not seem relevant for the "scope of ageing management for concrete structures" |  | OK.
NO-15 | 15 | EC | Norway | 07. Concrete containment structures | 59 | For JEEP II there is no formalised inspection for concrete but there is a process in place to develop a comprehensive AMP. Do you have a deadline for the development and implementation of this AMP? |  | See question 10. | ref. to NO-10
NO-16 | 16 | Finland | Norway | 02. Overall Ageing Management Programme requirements and implementation | 6 | At the moment the national regulatory requirements for AMP are those included in the operating licenses of the two reactors and they are different. Is there a plan to harmonize the national requirements for AMP for both reactors? |  | The TPR process has further highlighted the need for consistent requirements from the regulatory body. The license conditions include requirements for AMP. In addition to the license conditions, JEEP II was requested to update their AMP. The licenses for the two reactors now end and start at different times which has resulted in inconsistent national requirements in general, not just specific to ageing management. Currently, general license criteria are being developed by NRPA which will further improve the harmonisation of requirements for the two reactors.
NO-17 | 17 | Finland | Norway | 03. Electrical cables | 29-30 | Report does not clearly indicate if there are cables which have performance requirements in case of accident conditions. If there are such cables how this is considered in the AMP? |  | HBWR: All cables for emergency control room are routed in separate cable trays. Both these and other cables for emergency equipment are treated together with other cables in the AMP. JEEP II: See question 1. | ref. to NO-1
NO-18 | 18 | Finland | Norway | 05. Reactor Pressure Vessels | 43 | What is meant by GAP analyses. Some definition, reference or explanation could be given. |  | Should be written in small letters “gap analysis” and involves the comparison of actual performance with potential or desired performance (according to rules and regulations).
NO-19 | 19 | Finland | Norway | 05. Reactor Pressure Vessels | § 5 | There is no clear reference to ASME XI (Periodic in-service inspections of safety related SSCs). How are piping welds and components selected for the NDT inspections? How is the inspection interval determined? |  | The in-service inspection for the Class 1 pipes are made in accordance to ASME XI and for these pipes at least 50% of the welds are inspected every 9th year. Lower class piping is regulated by national regulations for non-nuclear pressurized equipment and intervals and selection are accordingly.
NO-20 | 20 | Finland | Norway | 05. Reactor Pressure Vessels | § 5 | Schematic drawings with the main parts could be provided for both reactor types. The drawings could be very simple describing only the basic structure. This could help to better understand the constructions of the reactors and the surrounding structures. |  | Schematic drawings would improve the understanding of the reactor, and could have been included in the report.
NO-21 | 21 | Finland | Norway | 05. Reactor Pressure Vessels | 53 | In the regulator’s assessment it is stated that there is no AMP for the RPV of the JEEP II facility. What plans there are to create an AMP for the RPV of the JEEP II facility? What will be the basis of the establishment of a new AMP? |  | In the report it is stated that the regulator’s assessment is that the “JEEP II has an AMP for the reactor tank, with a scope that covers all relevant parts.” The AMP is agreed with a third party organization, involving material samples and an assessment regarding possible future changes.
NO-22 | 22 | Germany | Norway | 02. Overall Ageing Management Programme requirements and implementation | 07 bis 12 | In chapter 2.3.1 it is said that JEEP II has a formally established AMP (p. 11). However, it still needs some improvements. Regarding to HBWR reactor (p. 7 and 8) it is not clear, if a comprehensive formalized AMP is implemented here. Could Norway provide more information on it? JEEP II: Will the AMP be extended to comply with the IAEA SSG - 10 "Ageing Management for Research Reactors"? When the Program supposed to be developed and implemented? HBWR: what is the current status of the AMP? Is it a comprehensive formalized program according to the corresponding national or international guidance? Is further development planned? If yes, please give more information on necessary improvements and planed time schedule for it. |  | AMP at HBWR is formalized and is divided into individual areas. However, it has been identified a need for improvement as significant gaps has been identified, e.g. electrical cables, but there is currently no formalized time schedule for when this should be done. Regarding JEEP II, see question 5 and 12. INSARR was completed on the basis of SSG-10, and the existing AMP for JEEP II will be revised on the basis of the INSARR recommendations, and regulatory requirements. | ref to NO-5 & NO-12
NO-23 | 23 | Germany | Norway | 02. Overall Ageing Management Programme requirements and implementation | 23 | In chapter 2.4 it is said that "IFE has no regular cooperation or exchange of experience on ageing management with other reactor operators, but cooperation is done on a case-by-case basis". Could Norway give more information on these processes? How is it ensured that the licensee receive all relevant information from other nuclear facilities to be able to select these relevant for own reactor? |  | IFEs operating organisations take part in relevant operator forums (RROG, EEAS) and relevant IAEA groups (for example EURSAC), in addition to inviting various missions to review safety in different areas. The Halden Reactor Project is itself a relevant cooperation for safety internationally. Both HBWR and JEEP II use an international third party organization for reviewing and revising the existing AMP, which also provides IFE with international experience.
NO-24 | 24 | Germany | Norway | 03. Electrical cables | 30 | It says that "At HBWR, there are about 7000 cables, and the number varies in line with the number of experiments that are carried out." To which categories belong these cables? Were all cables subjected for testing the aging mechanisms? |  | See question 1-4. | ref. to NO-1-NO-4
NO-25 | 25 | Germany | Norway | 05. Reactor Pressure Vessels | 47 | In chapter 5.1.2 it is said that "At present, the estimated time goes beyond the year 2200 for safe operation of the RPV." It is very long term estimation. Could Norway provide more details on the methodology used for this estimation? How reliable is this prediction? |  | IFEs calculations are based on the minimum pressure and temperature limits given in USNRC Reg 10 App G and H as well as ASME XI app G. Such that the argument is based on the fault the RPV should withstand and the material properties for different fluence values. IFEs prediction is made regarding when the fluence and limiting material property will coincide.
NO-26 | 26 | Germany | Norway | 05. Reactor Pressure Vessels | 47 | In chapter 5.1.2 it is said that "At present, the estimated time goes beyond the year 2200 for safe operation of the RPV." It is a very long term estimation. Could Norway provide more details on the methodology used for this estimation? How reliable is this prediction? |  | This is a repetition of question 25 | ref. to NO-25
NO-27 | 27 | Netherlands | Norway | 03. Electrical cables | 3.1.2 / p.31 | Both HBWR & JEEP-II: Are the acceptance criteria documented, or do they only exist in the minds of experienced personnel? Can examples of these acceptance criteria be provided? |  | See question 3. | ref. to NO-3
NO-28 | 28 | Netherlands | Norway | 03. Electrical cables | 3.1.3 / p.32 | Wouldn't it be an easier approach to formalise the cable checking frequency? That way there would be no need for regular replacement of cables (regardless of functionality); it would also allow for detection of premature cable ageing, which in turn prevents cable replacement after malfunction. |  | Thanks for this proposal. In general, it has been identified a need to improve the AMP for electrical cables. See also question 1. | ref. to NO-1
NO-29 | 29 | Netherlands | Norway | 03. Electrical cables | 3.1.4 / p.33 | (HBWR) To what extend has it been formalised that personnel keep an eye out for impending cable faults? |  | This is not formalized.
NO-30 | 30 | Netherlands | Norway | 03. Electrical cables | 3.3 / p.35 | Both HBWR & JEEP-II seem to be at a similar stage in their development of incorporating (cable) AMPs. The RRs belong to the same organisation (IFE) and the descriptions in the NAR are quite similar. Is a common overall AMP a feasible solution? |  | HBWR and JEEP II are different types of reactors and a common AMP is not feasible. But close cooperation in further development of the AMPs are important. See question 16, regarding harmonization of requirements for the two reactors. | ref. to NO-16
NO-31 | 31 | Poland | Norway | 03. Electrical cables | 30, 34 | 1. What is frequency of tests in LIRA-technology in the research reactor HBWR? 2. There is information: “HBWR plans to extend the program to include power cables in the future”. Does it mean that actual AMP for cables covers only measurement cables? |  | See question 2 and 4. | ref. to NO-2 & NO-4
NO-32 | 32 | RPV expert group | Norway | 05. Reactor Pressure Vessels | §5.1.1 p43 | What is meant by GAP analyses? Some definition, reference or explanation could be provided. |  | See question 18 | ref. to NO-18
NO-33 | 33 | RPV expert group | Norway | 05. Reactor Pressure Vessels |  | How are piping welds and components selected for NDT inspections? How is the inspection interval determined? |  | See question 19 | ref. to NO-19
NO-34 | 34 | RPV expert group | Norway | 05. Reactor Pressure Vessels | §5.3 p53 | What plans there are to create an AMP for the RPV of the JEEP II facility? What will be the basis of the establishment of a new AMP? |  | See question 21 | ref. to NO-21
NO-35 | 35 | Switzerland | Norway | 03. Electrical cables | 29 | Textline26: Some of the cables from 1959 are still in use. “These cables are monitored continuously”. How are they monitored continuously? What kind of insulation materials for cables was used? |  | The insulation resistance is monitored continuously for both signal and power cables. Insulation is paper/oil and PVC.
NO-36 | 36 | Switzerland | Norway | 03. Electrical cables | 29 | Are any international experiences/sources/standards in this field monitored/used? I.e. IAEA TecDocs 1188/1402? |  | HBWR are using the IEC standards
UK-1 |  | Norway | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 20 | In relation to MDI covering all SSCs in Table 2: Does that mean it is covering Passive and Active SSCs? (Because active SSCs are more readily detected and corrected by surveillance and maintenance activities throughout the plant's operation) |  | Maintain Design Integrity, the process that manages the safety case, covers all passive and active SSCs. Both passive and active components are subject to appropriate testing, maintenance and inspection activities as specified by the safety case.
UK-2 |  | Norway | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 25 | - What are the requirements for renewing operating licenses? -Does Plant Life Extension (absence or with works) require transboundary (public) consultation? |  | The operating licence is subject to the licensee demonstrating continued safety performance and compliance against all licence conditions. There is no specific licence condition for a plant life extension, but continued operation does require regulatory permission to start-up the plant following a statutory shutdown (every 3 years for an Advanced Gas Reactor and every refuelling outage for Sizewell B). Additionally, regulatory permission is required for continued operation in accordance with a periodic safety review carried out every ten years. The regulatory process for continued operation does not involve transboundary consultation.
UK-3 |  | Norway | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 14-59 | Can you please briefly describe: -The methodologies used to determine the structures and components subject to an aging management review. |  | All safety related SSCs, including SSCs that can interact with safety related plant, are identified by the safety case. This is recorded in a number of documents and databases including the safety case, the plant asset management system, the maintenance schedule and an equipment reliability plant management system. The safety case determines the ageing management and maintenance strategy for each system, structure and component. There are also a number of complementary measures used to screen and identify plant for ageing management review. Technical Governance provides additional support to components, e.g. electrical cables, specifying how the plant is designed and controlled, including the ageing management of these components. Component user groups and component user guides also provide additional support. Major plant systems also have Through Life Management Strategies (TLMS) and all safety related systems have system lifetime plans. TLMS are produced for key non-replaceable systems (e.g. boilers, graphite core, etc.) and other significant plant areas, providing holistic plans and detailed description of threats to future operation, ageing mechanisms, potential work and when it will be required and prospects of operating safely through an extended plant lifetime.
UK-4 |  | Norway | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 14-59 | -How is AMP managed for SSCs in case if there is no design documentation (for example for cables)? |  | The design basis for the plant is contained in the safety case. The safety case identifies the safety related systems, structures and components and their ageing management arrangements including the overall maintenance and inspection schedule. The Equipment Reliability process is used to manage the day to day plant condition where active change in plant configuration and performance can be readily measured. The Technical Governance process provides additional support to components, such as electrical cables, specifying how the plant is designed and controlled, including the ageing management of these components.
UK-5 |  | Bulgaria | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | p. 16 | 2.16. “… The licensee may have to go beyond relevant good practice if the safety case shows that it is reasonably practicable to do so.” Please explain how the licensee is supposed /or asked by ONR/ to go beyond the relevant good practice and how this is justified by ONR. Please give some examples if this is possible. |  | The key requirement on the licensee is to demonstrate that the risk is ALARP. This is written into the legislation.and the licensee demonstrates that it has met this through the safety case. It is implicit in the requirements that the licensee must consider going beyond relevant good practice if it is necessary to demonstrate that the risk is ALARP. This forms part of the normal regulatory interactions between the regulator and the licensee and does not require any special consideration or process.
UK-6 |  | Bulgaria | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | p. 16 | 2.18 - Why the fifth principal (related to obsolesce) is considered outside of the scope of the report? What are the legal requirements when safety related equipment has to replaced but the item is no longer manufactured or even the manufacturer doesn’t exist? |  | The scope of the TPR project as described in the technical specification specifically excludes consideration of obsolesence.
UK-7 |  | Slovak Republic | United Kingdom | 01. General information | Pages - general | Is there a licensee´s ageing management database in place? How is it structured? Does it include acceptance criteria and trending to decide on the required steps for corrective actions? |  | The ageing management process is not a standalone process, it is integrated throughout the management system. There is no single ageing management database. All safety related systems, structures and components are identified by the safety case. This is recorded in a number of documents and the plant asset management system. The safety case determines the ageing management and maintenance strategy for each system, structure and component. An Equipment Reliability process and database is used to manage the day to day plant condition where active change in plant configuration and performance can be readily measured. The Technical Governance process provides additional support to components, such as electrical cables, specifying how the plant is designed and controlled, including the ageing management of these components. There are also supplementary activities including Periodic Safety Reviews and Plant Life Extension projects which provide additional support to ageing management. The above arrangements include specification of acceptance criteria, plant trending and the management of corrective actions. The safety and plant performance has significantly improved over the last decade as a result of these arrangements.
UK-8 |  | Switzerland | United Kingdom | 03. Electrical cables | 64 | Textline4: Is there an AMP for electrical equipment (eg. motors, electronics, etc.)? |  | Technical guidance on ageing management exists for other systems and components including motors, switchgear, electrical protection relays and uninterruptible power supplies. These components are also subject to Equipment Reliability programmes.
UK-9 |  | Switzerland | United Kingdom | 03. Electrical cables | 66 | Textline12-point3.8: Are there specific national requirements for the Technical Guidance Note from the licensee? |  | The Technical Guidance note is wholly owned by the licensee and contains elements of national standards, international best practices and operating experience.
UK-10 |  | Switzerland | United Kingdom | 03. Electrical cables | 66 | Textline20-point3.10: Does this qualification program apply for NPP in operation or for the new builds? What are the ageing test methods? |  | The point is made with relation to the existing PWR station, Sizewell B, but an equivalent programme will be undertook at Hinkley Point C for the new build project but will be based on OPEX from French and UK installations operated by EDF and any other Relevant Good Practice (RGP).
UK-11 |  | Switzerland | United Kingdom | 03. Electrical cables | 81 | Textline39-point3.95: Are the addressed inspectors from EDF or ONR? |  | The inspectors are all employed by EDF Energy.
UK-12 |  | Czech Republic | United Kingdom | 03. Electrical cables | 67 - 68 | "EDF-NG’s guidelines recommend that visual inspection of five representative cables of each type is undertaken at six yearly intervals." (3.17, p 67 and 3.23, p 67 and 3.25, p 68) Why only five or ten cables have been selected? Who selected these cables? Are these cables installed in harsh enviroment? |  | The technical guidance is based on identifying a representative sample of cables that are operating in the worst operating environments within the station and then monitoring them over an extended period. The five or ten cables are deemed to form the representative sample. Suitably qualified and experienced inspectors make the selection from the environments of most significance.
UK-13 |  | Czech Republic | United Kingdom | 03. Electrical cables | 68 | "Functional cable tray wrapping is installed…" (3.28) Please describe what is it cable tray wrapping? |  | Please see 3.118. The wrapping is to maintain isolation, for instance, between two diverse lines of protection, from a common cause failure, e.g. fire.
UK-14 |  | Bulgaria | United Kingdom | 03. Electrical cables | p.79 | Would you please clarify whether for validation of the electrical cables results you used artificial thermal and radiation ageing? |  | In the case on New Build the thermal and radiation exposure is applied by virtue of the samples being located/stored within the Reactor Containment Building. These samples will then compared with control samples stored in an unexposed location. It is not currently intended to undertake additional artificial temperature and radiation ageing unless something comes to light that requires further consideration.
UK-15 |  | Bulgaria | United Kingdom | 03. Electrical cables | p.79 | In the cases when there were firefighting barriers, realized in different ways at electrical cables penetrations, which reflected to the cumulative ohmic resistance, did you use some corrections to evaluate finally cables lifetime? |  | When electrical cables pass through barriers greater than 150mm deep they are de-rated in line with a company technical instruction note. It is important to note that whilst the principles are the same as those expressed in BS7671 the actual values used differ.
UK-16 |  | Finland | United Kingdom | 05. Reactor Pressure Vessels | Chapter 5.3 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? |  | The operational requirement for Sizewell is based on a design life of 40 years. The fracture assessment informs the basis for fatigue assessment for the RPV which is based on the number of design transients over the life of the plant. This is continually monitored under a surveillance programme. This includes ramp rates for start-up and shut down. The forewarning of failure safety leg is met through the in-service inspection provisions and the routine inspections of the boric acid programme. The reactor pressure and temperature limits are periodically reviewed when surveillance capsules are removed from the vessel and material property data has been assessed.
UK-17 |  | Czech Republic | United Kingdom | 07. Concrete containment structures | chapter 2.4 - generally (52-57) and chapter 7 - generally (164-206) | How often - or if even - are the inspection intervals of civil structures reassessed? Are those inspection intervals changes based on operational experiences and ageing effect treds? Is the NPPs age, especially when considering the LTO phase of operation with higher risk of ageing effects appearance, taken into account for establishment of the inspection intervals? |  | At each surveillance campaign the continued integrity of the civil structures is assessed for the forward period of operation. This evaluation includes the need to identify additional monitoring or changes to the scope and frequency or inspection activities. Changes to the frequency of inspection have been enacted for civil structures e.g. sea defences, spent fuel ponds, critical roofs to ensure weather protection etc. No major changes have been made to the inspection arrangements of the PWR containment inspection arrangements other than in making improvements to the surveillance scope to recognise potential ageing and degradation issues and in recognition of international OPEX.
UK-18 |  | Czech Republic | United Kingdom | 07. Concrete containment structures | chapter 7.165-7.168 (189) | Have you ever detected the ASR (alkali-silica reaction) in reinforced concrete structures of nuclear power plants during their operation? If so, which parts of structures were affected? Please describe, if the appearance was found in monolithical parts of constructions built on site or in imported prefabricated materials. If ASR was found, how did you proceed this issue? |  | No, ASR has not been detected in concrete structures on the EDF nuclear fleet.
UK-19 |  | Czech Republic | United Kingdom | 07. Concrete containment structures | chapter 2.3.3. (42-49) | In what form you have processed the zero-condition passportization of flaws and malfunctions of NPP civil structures? Is this base passportization updated on the basis of results of regular maintenance activities and/or more detailed survey of intednded structural objects? Do you regulary evaluate appearance of new flaws or changes in previously found flaws and malfunctions with respect to the base zero-condition passport? What kind of documentation do you use for planning and conducting of this constructional-technical survey (e.g. ISO 13822)? What kind of degradation that was found within the constructional-technological surveys is most often (please provide examples, e.g. shear cracks, bend cracks, shrinkage and creeping of concrete, carbonation of concrete CO2, corrosion of reinforcement or concrete, mechanical overload, stability loss of constructions - tilting, bracing, excessive bending, etc.)? |  | Don’t fully understand the term "zero-condition passportization"? In terms of how the on-going structural integrity of the UK PWR concrete containment structure is evaluated, in addition to the ISI planning and type of defects encountered, this is set down in detail in Chapter 7.
UK-20 |  | Czech Republic | United Kingdom | 07. Concrete containment structures | chapter 2.109 (38) | Do you have geodetic measurement and assesments of settlement and tilt of civil structures important for (main production block, containment, confinement) and related to (ventilation chimney, building with dieselgenerators, blackout dieselgenerators, main pump station, end heat receiver, etc.) nuclear safety in your aging management programs? Did you find any problems with uneven foundation settlement of NPP civil structures? Did you identify any typical flaws (shear cracks) caused by civil structures settlement? If so, please specify and describe, how did you deal with this issue |  | Foundation settlement surveys are routinely undertaken. These have found no structurally significant issues to date of the type requested. At one AGR site founded on soft ground the tilt and settlement of the main PCPVs is carefully monitored to ensure that adequate margins remain to ensure the safe functionality of the primary shutdown system. There has been some evidence of uneven settlement but well within the acceptable limits and with no evidence of secondary structural distress of the type requested.
UK-21 |  | Czech Republic | United Kingdom | 07. Concrete containment structures | chapter 7.256-7.263 (200-201) and 7.288 (204) and 7.289 (204) | In what way and how often do you perform monitoring of containments steel hermetic lining condition? Is it measured punctually on test spaces chosen in advance within the construction phase, or is the measurement conducted aeraly e.g. by phased-array probes? Did you change test spaces during operation or was the number of test spaces extended/narrowed based on the inspection results? Have you ever found problems with thickness weakening in base material or weld joints of the containment hermetic steel lining during operation of any nuclear facility ? If so, please specify and describe, how did you deal with the situation. |  | The PWR containment liner is subject to technical surveillance as part of the long term in-service inspection programme at each 18 monthly Refuelling Outage (RFO). The inspection zones of the liner are identified in advance. Inspection is visual and in accordance with ASME XI Sub Section IWE. The general condition of the UK PWR liner and its paint coating has been found satisfactory. Visual inspections to date have confirmed the absence of significant degradation or penetration of the paint coating. At each RFO, a segment of the liner surface from working floor to dome apex is subject to visual examination. This scope includes both liner plate and liner plate welds. ASME XI IWE requires that the surface examination coverage exceeds 80% of the nominated containment boundary which provides some practical allowance for areas of liner accessibility. Over a 10 year period, the full liner will have been subject to 100% surveillance incrementally via each RFO inspection .
UK-22 |  | Netherlands | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 2.4.1/p52 | Apart from WANO, has the use of IAEA SALTO missions been considered in the UK? |  | EDF Energy is familiar with the SALTO peer review service and Sizewell B NPP have requested a workshop with relevant IAEA experts to present the SALTO methodology, SALTO mission results and good practices from other member states. This workshop is scheduled for September 2018 and will be focused on furthering EDF Energy’s and Sizewell B’s understanding of the IAEA’s Long Term Operation framework (it should be noted that Sizewell B NPP is at the early stage of considering LTO, no formal decision has yet been made and therefore any request for a SALTO peer review would only be made at some time in the future). In addition to this engagement, EDF Energy has provided a staff member, as an observer, to a recent SALTO peer review mission.
UK-23 |  | Netherlands | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 2.4.1/p54 | What are the main sources of external operating experience? |  | For the overall programme, operating experience is obtained through relevant nuclear and non-nuclear organisations such as IAEA, WANO, INPO, EPRI, PWR Owners Group, International Electroctechnical Commission, etc. This can include formal review of publications, reports and reportable events, participation in workshops, forums and inspections. Technical support missions, peer reviews, assist visits and benchmarking are also carried out.
UK-24 |  | Netherlands | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 2.4.1/p54 | Does the UK feed its own experience into international systems like IAEA IRS, NEA CODAP? |  | ONR feeds its experience into IRS, but is not a participant in the NEA CODAP project
UK-25 |  | Netherlands | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 2.4.1/p54 | In what international gremia related to ageing, are staff from operators or regulators participating? |  | Both ONR and the licensees participate in a range of international forums and working groups within them. Many of these are involved in various aspects of ageing management e,g, WENRA, ENSREG, IAEA and OECD-NEA groups, WANO, European Nuclear Installations Safety Standards Initiative (ENISS), PWR Owners Group and international conventions. Few groups are specifically ageing management related. For goups that are specifically ageing management related, UK particpates in OECD-NEA Working Group on Integrity and Ageing of Components and Structures (WGIAGE) and EDF now participates in the IGALL programme.
UK-26 |  | Netherlands | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 2.5.1/p57 | What are the improvements considered (apart from review of IGALL) related to the statements in 2.220? |  | Examples of improvements include: acceleration and reinforcement of programmes such as corrosion management. Addressing plant performance shortfalls through improved governance, oversight or investment. Plant replacement or modification to support station lifetime ambitions.
UK-27 |  | Netherlands | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 2.7.3/p64 | The ONR statement that EDF-NG has an adequate overall AMP seems to be in contradiction with the elements of the AFI formulated. It also seems to state that an overall AMP proces is not required, allthough WENRA and IAEA do require it. Please explain. |  | The report recgonises that EDF-NG does not have a specific process for ageing management. It does, however, show that EDF-NG's management system the elements necessary to manage ageing in accordance with the detailed requirements in NS-G-2.12. Fig 2.2 and the text descibing the processes for maangeing ageing demonstrates that the licensee has an integrated approach to identifying, analysing, monitoring and taking corrective actions and document the ageing degradation of structures, systems and components as rquired by the WENRA RLs. Section 2.7 of the report shows how ONR has assessed the adequacy of the licensee's ageing management through routine regulatory processes and assessment of the licensee's contributions to the UK report. It concudes that the licensee has adquated processes in place for manageing ageing. The UK report notes that whist ageing is managed adequately there are a number of improvements that would be beneficial to improve ageing management, although they are not necessary for it to be adequate.
UK-28 |  | Netherlands | United Kingdom | 03. Electrical cables | section 3.1.1.1 | In paragraph 3.6, the EDF-NG's view on relevant ageing mechanisms is clearly stated. However, it is unclear which processes/procedures were used to identify these mechanisms, as is requested in the TPR technical specification. Please elaborate on this subject. |  | The processes and procedures used to identify the ageing degradation mechanisims are described within the EDF-NG technical guidance note described with this chapter. The chapter describes: cables to be considered; cables likely to age prematurely and their ageing degradation mechanisims; acceptance criteria related to those ageing degradation mechanisms and the methods of cable inspection.
UK-29 |  | Netherlands | United Kingdom | 03. Electrical cables | section 3.1.2.1, p.72, Table 3.3 | Of the constituent elements, the insulation, jackets and termination arrangements are discussed in detail. However, no information was given on possible ageing mechanisms of the conductor material itself. Was this a conscious choice? |  | Time Domain Reflectrometry (TDR) checks are routinely carried out on instrumentation cables to check for high resistance joints or discontinuity. The UK has limited experience of conductor failures apart from inadequately executed cable joints.
UK-30 |  | Netherlands | United Kingdom | 03. Electrical cables | 3.1.3.1 | Section 3.1.3.1 contains no proces for using the inspection history for the purpose of identifying trends. Is this considered in EDF-NG NPPs? |  | All the results of the inspections are recorded on spreadsheets which allows trending to be carried out.
UK-31 |  | Netherlands | United Kingdom | 04. Concealed pipework | 4.1.1, p.100 | Since the operating conditions, pipe material and diameter as well as environment can influence the degradation mechanism, could you please provide such information? |  | Unfortunately, this level of detail would be subject to Export Controls so cannot be shared. In addition, it is considered that the scope of the review does not warrant this level of detail.
UK-32 |  | Netherlands | United Kingdom | 04. Concealed pipework | 4.1.1, p.107 | For operating reactors it is not very clear what grouping criteria are exactly used; based on the risk assessment (low/high) or based on the system (table 4.1). Could you please clarify? |  | The “grouping criteria” mentioned in the report is in the context of HPC, as opposed to the currently operating reactors. For the concealed pipework installed at the currently operating stations, a Risk Based Inspection (RBI) programme was developed, as discussed in Section 4.36, primarily initiated by adverse OPEX. For buried pipework, the RBI approach utilised BPWorks to assist with the risk ranking.
UK-33 |  | Netherlands | United Kingdom | 04. Concealed pipework | 4.1.1, p.107 | Would international experience be considered as a basis for identifying ageing mechanisms for the EPR reactor? |  | As a fundamental part of the UK EPR’s concealed pipework AMP, appropriate national and international operating experience (OPEX) will need to be routinely reviewed with lessons learned incorporated into the continually improving ageing management strategy. Screening of this OPEX will be required in order to assess relevancy to the UK EPR.
UK-34 |  | Netherlands | United Kingdom | 04. Concealed pipework | 4.1.3, p.113 | BPWORKS software is used to estimate the probability of corrosion of metallic pipelines. Are any provisions made to identify any unexpected degradation mechanisms (besides general corrosion) during monitoring, testing and inspection? What are the input parameters for the BPWORKS software? |  | BPWorks allows a range of inputs to be specified for the particular pipework system. These include nuclear safety classification, pipework material, design code, design pressure and temperature, pipework dimensions, joint configuration, groundwater data etc. If specific data is not available then conservative assumptions are made, which can affect the validity of the conclusions/assessment. Having as much detail as possible on the specific pipework system helps to ensure that the output from the assessment is valid. Obviously, the converse is true – if there are too many unknowns or assumptions then the output may suggest a higher risk for that particular system. In terms of unidentified issues, there will always be a risk of this to some extent. However, supplementing the output from the assessment with some form of targeted inspection should help to minimise this risk.
UK-35 |  | Netherlands | United Kingdom | 05. Reactor Pressure Vessels | Ch.5 | The information provided in this NAR in its chapter 5 on ageing management of reactor pressure vessels, is to a great extent qualitative. However in the Technical Specification for the NARs, the countries are requested to report in their NARs on the acceptance and action criteria for the various ageing phenomena. Apart from indicating those criteria, it is obvious that the NARs must discuss the compliance of the reactors with these criteria. Could you please provide this information? |  | For in-service inspection there are agreed guidesheets (agreed by an expert panel called the structural integrity panel). These specify the inspection requirements and the reporting threshold. For IOF components the safety case details the inspection defect size which corresponds to the start of life defect size used in fracture assessment. Irradiation embrittlement and thermal ageing of the RPV has defined criteria in the surveillance programme. These are assessed as the plant ages. In turn fatigue transient are accrued and to date there are large margins between the accrued fatigue transients compared with the lifetime allowable. In the event they are concerns with respect to fatigue trends then early warning allows operational adjustments to be made.
UK-36 |  | Netherlands | United Kingdom | 05. Reactor Pressure Vessels | p.148 | What limits are meant in par 5.115 with the statement "the results to date remain within limits"? |  | Limits are defined in surveillance programme 9. Results are compared with 50C shift in Charpy impact data for irradiated embrittlement and 30C shift in Charpy impact data for thermal ageing. Both are based on end of life. These are underpinned by measured fracture toughness data.
UK-37 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | Please, explain why UCC (Under Clad Cracking) is considered an active ageing mechanism? Have UCC been identified during the manufacturing process of the RPV? |  | UCC is not specifically a degradation mechanism but it has been included as it is something we specifically inspect for. Although the cladding process may have introduced short cracks at the interface detailed inspections pre-service and in-service have not found any cracks.
UK-38 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | Two of the identified ageing mechanisms for the RPV steel are thermal ageing and embrittlement due to neutron irradiation. Have the combined effect of thermal ageing and simultaneous neutron irradiation been considered? |  | In reactor specimens provide details of combined thermal ageing and irradiation embrittlement and forms part of the RPCV steel surveillance programme. A separate thermal ageing programme is also included in the programme with no irradiation element. Thermal ageing affects are included in the parameters defined in the technical specification.
UK-39 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | Sizewell B have already removed and tested all 8 capsules with irradiated specimens. What was the purpose to remove all 8 capsules so early? |  | Early capsule removal was carried out to support understanding of upper shelf toughness. The final capsule was removed with a dose equivalent of approximately 60 years.
UK-40 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | 7 new capsules with specimens have been installed in Sizewell B, does the new capsules contain dosimeters? |  | Yes. Both fissile and activation dosimetry are included.
UK-41 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | What are the lead factors for the new capsules. What is the purpose with the new capsules? |  | The new capsules have the same lead factor as the original capsules (approximately 3.5 for forgings). The new capsules will support current safety case data and possible scope for life extension – providing more datasets.
UK-42 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | What are the requirements for the qualification and validation of the used ISI methods? What type of defects are used for the validation process? |  | Qualification and validation requirements for the highest relaibility components, designated IoF, follow ENIQ guidelines. As specified within the NGL requirements document for qualification, all IoF components are subject a full validation process which is performed by an independent third party organisation, the Inspection Validation Centre (IVC). The process includes qualification of procedures, personnel and equipment. This is done through personnel performing blind trials, on a large representative test sample using the same equipment used within the site inspection in conditions represenative to those on site (immersed in water etc). The defect information remains unknown to the operators. The IVC ensures the data remains on site and secure. Data analysis is done on the collected data which is re-arranged in order to prevent operators learning the data patterns. Results are given on a pass/fail basis and feedback on performance will be only given based on whether they met the criteria correctly (or not). The defect information is only known to the IVC. The defects were created around the time of construction of Sizewell B using most the current methods at the time of defect production, creating a variety of defects representative of those that could form in-service with a variety of sizes which test the limits set within the defect specification.
UK-43 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | Which organization perform the in-service–inspections? Is it the licensee or an independent laboratory? |  | The inspections are performed by a contracting organisation of the licensee (Doosans).
UK-44 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | Regarding the inspection of the Nozzle inner radii, what is an enhanced visual inspection? |  | The nozzle inner radii is now subject to enhanced VT-1 visual examinations in accordance with the ASME Code Case N-648-1 in leiu of UT examination. Enhanced VT-1 examination must be capable of detecting (surface) flaws of the size and oreintation of concern. This is demonstrated through independent validation of the technique.
UK-45 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | On page 157, section 5.182, there is a description of test results from samples removed from SZB, which indicate that values used in the safety justification may no longer be conservative and EDF-NG developed a revised approach accepted by ONR. It would be valuable if ONR could give a description of the found deviations and the revised approach to verify the safety margins. |  | During the assessment of material properties from the monitoring process there was a concern that the material properties used in the fracture assessment were not longer bounding. This relates to the upper shelf fracture toughness values. Adjustments were made to the fracture assessment and included in the RPV safety case. This required in a limited number of RPV locations to adopt a revised inspection criteria known as the high capability of detection (hcd), which differs from that given in section 5.16. The ‘hcd’ approach enabled a lower validation factor to be used but added other requirements, such as it must be acceptable and have an acceptable validation factor if a smaller end of life defect size is used. This was agreed by the Regulator.
UK-46 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | 5.20, 5.21, 5.22, 5.26, 5.25 2.3.1 Paras. 5.20, 5.21 and 5.22 list the degradation mechanism for each part of RPV (i.e. irradiation embrittlement, thermal ageing effects, under-clad cracking, fatigue mechanisms etc.). Paras. 5.26 and 5.27 describe only programmes for fatigue and stress corrosion cracking but, at the same time, there is no description of other ageing mechanisms. Corresponding clarifications for all ageing mechanisms should be provided as an answer. |  | Section 5.24 covers irradiation embrittlement and thermal ageing. The thermal ageing is applicable for all RPV components. Although per say strictly a degradation mechanism, UCC is something inspected for under the in-service inspection programme.
UK-47 |  | RPV expert group | United Kingdom | 05. Reactor Pressure Vessels |  | 5.82, 5.84 In para. 5.82, the RPV AMPs in the IGALL [C4] are listed. Para 5.84 states that in many cases there is a direct relationship between AMPs in IGALL and at Sizewell B. Is it possible to show this relationship? |  | Although not shown graphically the relationships between the AMPs and at Sizewell are as follows: AMP101 – the intent of the AMP is implemented through Surveillance Programme 3 (Fatigue). AMP102 – the intent of the AMP is implemented through Surveillance Programme 6 (ISI). AMP118 – the intent of the AMP is implemented through Surveillance Programme 9 (RPV Steels). AMP110 – the intent of the AMP is implemented through Surveillance Programme 10 (Boric Acid). AMP 103 is implemented via tech specs using EPRI guidelines on reactor chemistry. AMP 104 is implemented under the inspection programme SP6 (studs are replaceable) AMP 111 is also implemented under the inspection programme plus specific safety cases covering inspection frequencies.
UK-48 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 179 | 7.1.2 The secondary containment is clad with protective weather tiles and has limited exposure to external conditions. Question : is it possible to bring the evidence that no significant corrosion of the rebars, or other pathology, is developing under the cladding ? |  | There is no routine inspection of the outer surface of the secondary containment (i.e. in the gap between the concrete surface and the external cassette style cladding tiles). During construction, the outer concrete dome was subject to close site supervision ensuring that the cover requirements to the embedded steel reinforcement was assured. In addition, a waterproofing membrane was applied to the outer surface concrete and then enveloped with the outer cladding arrangement. The inner face of the secondary structure has not given rise to any evidence of dampness or concerns. Similarly, there has been no significant evidence of movement, staining or distress to the cladding fixings. The risk is judged to be low.
UK-49 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 198 | 7.1.3 The instrumentation recording system has been afflicted by a number of reliability issues since the SOT and this has led to limited data availability for some periods (…). Question : Could you precise the main locations, numbers and redondancy of the strain (and temperature) gauges currently available ? |  | Base - 22 VWSGs and 78 RFSGs that monitor strain behaviour. Barrel - 81 VWSGs and 69 RFSGs that monitor strain behaviour. Dome/Azimuth - 20 VWSGs and 6 RFSGs that monitor strain behaviour. Of the VWSGa, 28% continue to measure strain reliably and 61% continue to measure temperature reliably. Of the RFSGs, 60% continue to measure strain reliably. . The data returned by functioning gauges indicates that overall, the PCCV continues to behave in a stable compressive state, with slowly increasing compressive strain due to concrete creep. There is still a sufficient number of functioning gauges distributed throughout the PCCV to allow the general strain state of the PCCV to be assessed. The temperatures of the PCCV concrete are measured through a combination of VWSGs and TCs. Of the 123 VWSG and 48 TCs, a total of 75 (61%) and 42 (88%) respectively continue to provide reliable temperature data. Therefore there remain a sufficient number of functional gauges distributed throughout the PCCV to allow the general temperature state of the PCCV to be assessed. All functioning thermocouples continue to measure temperature reliably, although further independent temperature readings are requested for the steam and feed penetrations to validate current readings of all thermocouples in this area
UK-50 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 181 | 7.1.1 The AMP recognises the potential for corrosion to develop at the leak chase channels and these are subject to detailed inspection. We understand that those channels are still free, i.e. not filled with any corrosion inhibiting material. Question : Could you provide the principle of the detail inspection carried out in the channels ? |  | There have been recent occurrences in stations of similar design where damage has been identified in leak chase channel covers, which resulted in further investigations showing corrosion of the channels below, which may present a challenge to the integrity of the containment. During the RO13 an opportunity was taken to inspect the leak chase channel plugs to determine their condition. The results of the RO13 inspection show that there is no indication of there being an issue at the UK PWR with only minor surface corrosion on some inlet pipes. An inspection was undertaken in RO14 to survey the Instrument Tunnel which was not available in RO13, and determine if there were any additional leak chase points. During the liner inspection of the Lift Shaft additional channel inspection points were noted and added to the report. The four points identified as not being where the drawings indicated were not found during RO14 therefore they were either not installed as shown in the construction drawings, or are now obscured. Given the condition of the other approx. 100 channel plugs it is considered a low risk that they may be damaged and therefore no concerns are raised regarding the condition of the plugs. This is further supported by the successful ILRT performed in RO12. Notwithstanding, the surveillance program recognises the need to maintain vigilance of these components.
UK-51 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 207 | 7.1.3 The international experience shows that the most sensitive location, concerning the risk of liner corrosion, is the junction between the liner wall and the concrete floor of the PCCV. 7.309. The interval of an extended ILRT is now 180 months (it was formely 10 years). Question : could you explain how the risk of liner corrosion is controled during the 15 years interval? |  | Comment on 7.1.3 is noted and agreed. Comment on 7.309 : the liner is subject to technical surveillance at every 18 monthly Refuelling Outage (RFO)
UK-52 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 199 | 7.1.3 7.249. The pre-stressing system performance and component integrity are routinely monitored. (...) The load in one vertical and one horizontal tendon (the 'common tendons') is measured at each surveillance; the others are randomly selected from the population not already tested. One tendon of each type is de-tensioned (…). Question 1 : how many tendons of each group (horizontal and vertical) is de-tensionned and inspected at each examination ? Question 2 : could you indicate the periodicity of the examinations ? |  | Q1: The civil ISI plan identifies a selection of tendons for load checking, excluding those which have been examined at earlier inspections. Four horizontal and three vertical tendons are selected. In addition, a common tendon of each type is included. Common tendons are examined at each surveillance and were designated at RFO1. In total, five horizontal and four vertical tendons are examined at each surveillance campaign. Q2: Every 5 years.
UK-53 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 206 | 7.1.3 and 7.2 Question : what are the results of the corrosion surveillance of the tendons ? Were corroded tendons found ? Please provide some information. Did those results lead to modifications of the AMP ? |  | No corrosion has been found from the prestressing surveillance of the UK PWR containment structure.
UK-54 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 195 | 7.1.2.2 7.224. In order to protect the liner against corrosion, the entire liner containment surface not in contact with concrete is painted. The international experience shows that the most sensitive location, concerning the risk of liner corrosion, is the junction between the liner wall and the concrete floor of the PCCV. Question : What are the provisions that will be taken during contruction, in order to maintain that junction free from water, and to prevent the paint of the liner from being damaged ? |  | During construction, the addition of protection plate above Inner Containment (IC) liner base cup junction at the IC and internal structure slab interface is proposed. The purpose of the protection plate is to reduce the risk of liner corrosion from potential stagnant water during construction.
UK-55 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 231 and 243 | 8.1.2 The Report aknowledges the value of the information provided by the monitoring devices embedded in the concrete of PCPV, although they were not intended for long term monitoring. A gradual failure of gauges is observed. Question : does the Licensee consider the possibility of placing new gauges on the concrete surface near the key embedded ones, in order to register the correspondance between embedded and surface gauges, before the embedded gauges fail ? |  | Yes, this is an area of research in which we are certainly interested and it forms part of the late life management strategy for the containment structures e.g. the fitting of new instrumentation ideally non-intrusive to the main structural concrete. To date the focus has centred around the C&I re-invigoration of previously redundant instrumentation.
UK-56 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 231 and 243 | 8.1.2 and 8.1.3 Concerning the rubber bearing pads supporting the PCPV, visual inspection is carried out on the pads that are accessible. Question 1 : could the Licensee provide the detail programme for the visual inspection, precising which parameters are inspected and measured ? Question 2 : does the Licensee consider some mechanical testing on samples or real size pads, in accordance with the state of the art in that field ? |  | Q1. The accessible areas of the bearing pads are visually inspected by the APEX on a 3 yearly basis as part of the PCPV concrete inspections. This is typically restricted to the outer edges of the rubber bearings where visual access is afforded (typically at two stations). Bearing inspections are subject to ALARP reviews due to the plant configuration and operational constraints that limit ready access. Other visual inspections have been carried out following temporary removal of materials obstructing the inspection of the bearings, but these inspections are not a routine activity. Q2. physical testing to assess hardness of the samples and chemical analysis to review the properties of the rubber material has been undertaken at one station. To date, there has been no evidence of any change in the rubber material properties from the sampled bearing locations.
UK-57 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 247 | 8.1.4 In the podded PCPV designs, the Report presents an issue concerning “wetted” tendons that are adversely exposed to PVCW leaks due to their vertical orientation : "8.209. Mechanisms identified to date that have subsequently affected the wetted tendon strands include general surface corrosion, localised pitting of the tendon strand, and evidence of stress corrosion cracking in the presence of emulsified grease." Question : does the Licensee consider the possibility of replacing the grease by a more permanent protection, similar to the greased and sheathed strands technology, or other solution ? |  | We have considered various options to enhance the resilience of the prestressing against wetting action from PVCW leaks entering the tendon ducts. This has included consideration of sheathed and greased technology. However, the prestressing layout was optimised during construction to suit the design intent and this presents a challenge for any retrospective activities on the tendons due to geometry, profile and load requirements on the prestressing arrangement. Any new technology would be technically very difficult to implement on an operational reactor and unlikely to meet the criteria for ALARP.
UK-58 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 171 | Aging management requires the condition assessment for different types of structures and structural elements, such as secondary structures, anchorage elements, water-proofing sealings, drainage, coatings, fire-retarding sealings, etc. Are all these types included in the inspection programs? |  | Yes, all are included in the scope of the technical surveillance arrangements.
UK-59 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 171 | Are there specific testing and inspection requirements for safety related anchorage elements? (e.g. pull-out tests with acceptance criteria) |  | Where appropriate to safety significance, load cells are fitted to monitor anchor loads for acceptance against safety case limits.
UK-60 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 171 | How are the fire protecting structural elements monitored? |  | Building gaps and interbuilding seals are monitored on an interval program before 3, 7 and 10 years. Doors seals are inspected annually or on a 6 month rolling programme.
UK-61 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 171 (7.39) | What types of monitoring devices are installed in Sizewell B? |  | The embedded instrumentation of primary interest comprises vibrating wire strain gauges (VWSGs) for the measurement of strain & resistance foil strain gauges (RFSGs) for the measurement of concrete temperature. In addition, there are thermocouples attached to the steel penetration tubes.
UK-62 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 174 (7.59) | Prestressed concrete structures : Nearly 280 tendons will be grouted, 4 will be unbonded and instrumented for monitoring purpose. How is the experience on representativeness from existing comparable CCS installations? Are all 4 unbonded tendons tested periodically? |  | Tendon tension is measured on the 4 purely vertical greased prestressing tendons, 3 of which are located in the vicinity of the invar wires and pendulums (radial lines at 61°, 123°, 207° and 297°). They provide a means of measuring the effect of relaxation of tension in prestressing tendons and concrete shrinkage, creep and thermal effects. Measurements are carried out using dynamometric tensile gauges installed on the passive end of each of the instrumented tendons. The values measured by the dynamometers will be continuously recorded by the acquisition device during the whole period of tests and plant operation, and will be used in conjunction with other Inner Containment monitoring devices, such as embedded strain gauges, temperature probes, extensometers and pendulums to assess structural integrity. The monitoring of tension in the ungrouted tendons is not to provide a representative profile for tension in the grouted tendons but to provide additional information that can be used in combination with measured strain, deflection and temperature variation in order to verify shrinkage, creep and tendon relaxation effects are compliant with the design basis.
UK-63 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 178 (7.77) | In addition to the visual inspections of the concrete surfaces, do you consider using onsite instrumental inspections and laboratory material testing as part of the aging management? (e.g. carbonation progress, corrosion potential of reinforcement, material strength, concrete cover depth, ...) |  | It is currently foreseen that the routine inspection programme for HPC will be limited to visual inspection of all accessible concrete surfaces only, with possible crack monitoring if needed. Periodic destructive and non-destructive testing is not planned but can be considered following the findings of the periodic structural inspections, particularly if evidence of structural defects is observed. As the in-service inspection programme for HPC will only be finalised later in the construction sequence it is not possible to state this is the final position.
UK-64 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 179 (7.87) | How are the acceptance criteria for the inspected concrete structures defined? (crack width and depth, crack patterns, carbonation depth, prestress loss, ...) |  | Surface inspections are in accordance with ASME XI Section IWL. The condition is assessed by the SQEP APEX who will refer any evidence of concrete defects, including cracking, that may be of structural significance, to the PCCV Responsible Design SQEP(s) who fulfil the technical authority role as per INSAG-19. To date fine shrinkage cracking up to 0.15mm has been fitted with DEMEC gauges to monitor and trend the structural behaviour. A drawing record of all defects, cracks etc. is maintained and updated as a live record of the containment concrete condition. Reference to international OPEX, practical experience of large concrete nuclear structures and professional technical judgement is exercised when assessing the significance of containment concrete cracking - noting that the APEX role is subject to pre-requisite training and qualifications.
UK-65 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 179 (7.93) | Are there prestressing cables which are exposed to elevated irradiation? How is the impact of irradiation on the strength and ductility of prestressing steel assessed and monitored? |  | The only structures likely to experience significant levels of irradiation are the Reactor Building Internal Structures, and in particular the Primary Shield Walls which surround the Reactor Pressure Vessel (RPV). The overall effect on the containment structure is minimal. Any relaxation of tendon load, embrittlement etc. would be identified by the load testing or mechanical testing of strand wires during the routine maintenance activities.
UK-66 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 180 (7.97) | Are the removed strands replaced by new ones? Does this replacement have an impact on the long term behavior of the tendon? |  | Yes all removed strands (for examination) are replaced. The tendon is restressed notionally to original design intent.
UK-67 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 196 | How is the collection and investigation of concrete and reinforcing steel from structural interventions (reconstruction, partial demolition, ...) organized? |  | There are no intrusive inspections that require reconstruction or partial demolition of the structures. All inspection activities are organised via a Technical Specification Programme that identifies the in-service inspection requirements for the containment.
UK-68 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 196 | How are the structures and the structural elements assessed which are inaccessible for visual inspections? (indirect/indicative methods?) |  | Inaccessible areas are identified as potential outliers whereby access may require to be specifically arranged or developed - subject to safe access, outage access, radiological conditions, operational constraints etc. Indirect methods are used to identify evidence of secondary structural effects e.g. secondary cracks, evidence of leaks, foundation movements, corrosion products etc.. All inaccessible areas encountered during inspections are recorded on the surveillance record drawings with appropriate recommendations for future access where possible.
UK-69 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 207 (7.310) | Which type of embedded concrete instrumentation has been installed according to the examiners recommendation? |  | The embedded instrumentation was installed during the construction. The APEX has made recommendations that the longer term continued performance of the instrumentation should be addressed as a focus area. These improvements are centred around the C&I efficiency of the instrumentation system and the need for research into potential retrospective fitting of additional gauges / or the reinvigoration of redundant instruments.
UK-70 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 209 (7.317) | How is the experience with the embedded strain gauges (collected information, long term behavior) |  | The long term behaviour of the serviceable gauges continues to confirm the linear elastic behaviour of the PCPV under normal operating conditions and in accordance with design / FE model predictions and comparisons against the overpressure test results.
UK-71 |  | Concrete containment PCPV expert group | United Kingdom | 07. Concrete containment structures | 211 (7.325) | "The anchors cannot be physically inspected". Is it considerable to inspect selected anchors by probing? |  | Not feasible as they are entirely cast into the containment wall with no access points. These anchorages were attached to the outer face of the steel liner which subsequently provided the inner face formwork for the containment wall concrete.
UK-72 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 224 (8.35) | How many strain gauges are embedded in the PCPV, and how is their long-term behavior? How many are still functionable? |  | The extent of installed VWSGs varies between PCPVs depending upon the original design intent, vessel geometry and construction. Typically several hundred gauges per vessel. The long term behaviour of the serviceable gauges continues to confirm the linear elastic behaviour of the PCPV under normal operating conditions and is in general accordance with design / FE model predictions and comparisons against the overpressure test results. The extent of gauges that no longer function again varies between sites and parts of the vessel, however the remaining coverage is still sufficient to provide an informed evaluation of the structural behaviour - noting that the gauges were installed for the purposes of the overpressure test during construction and their continued presence and functionality at this late stage in the vessel life can be regarded as a bonus in terms of providing supplementary late life information on the vessel health.
UK-73 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 226 (8.48) | Are the prestressing cables exposed to elevated irradiation? How is the impact of irradiation on the strength and ductility of prestressing steel assessed and monitored? |  | The prestressing system is generally not subject to high levels of irradiation due to rapid attenuation, particularly within the innermost depth of circa 200mm in the concrete structure. Any relaxation of tendon load, embrittlement etc. would be identified by the load testing or mechanical testing of strand wires during the routine maintenance activities.
UK-74 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 227 (8.55) | In which interval is the optical level survey of the top cap performed? |  | Every 3 years aligned to statutory outages.
UK-75 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 232 (8.92) | Have the samples of bearing pads been tested mechanically (strength, stiffness)? |  | Yes, at one station small samples have been extracted in-situ from the original rubber bearings and tested by chemical analysis and hardness tests.
UK-76 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 238 (8.138) | Groundwater ingress: Are the reactor buildings protected against groundwater ingress, e.g. by waterproof sealings? |  | Generally the main buildings were constructed in accordance with good practice and incorporated the standard techniques of water bars, movements joints, seals and water proofing membranes. In the presence of a high water table and tidal conditions, the main buildings are to varying degrees affected by ground water ingress and these are assessed on a case-by-case basis in terms of the safety significance. Pressure & injection grouting of concrete micro-cracking has been undertaken to mitigate the extent of ground water ingress at critical locations.
UK-77 |  | Concrete containment PCPV expert group | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | 240 (8.153) | Are the removed strands replaced by new ones? Does this replacement have an impact on the long term behavior of the tendon? |  | Yes the strands removed for examination are replaced and the full tendon is restressed to nominally full design intent. Scope exists on the older vessels approaching their end of generation to relax the requirement for strand replacement subject only to a safety justification that considers the remaining residual prestress and in the absence of any concerns for the tendon condition.
UK-78 |  | Cables expert group | United Kingdom | 03. Electrical cables | 67 | 3.17. EDF-NG’s technical guidance provided to the stations recommends that visual inspection of five representative cable routes should be undertaken at six yearly intervals. Does it mean that 5 sets of cables routes are inspected every 6 years, OR six different sets are inspected each year? |  | In relation to PE, XLPE and EPR polymeric cables (>= 3.3kV) the guidance is that five representative groups are inspected over a rolling 6 year interval. It is for the stations to decide whether to do all of the groups at the same time or to do them equally spread over the period.
UK-79 |  | Cables expert group | United Kingdom | 03. Electrical cables | 87 | Some cable samples are stored in a " similar facility" as at the NPP. Although those samples are not subject to the radiation, at NPPS some of those cables might be subject to other environmental influences. How do you control for those |  | Page 65, Para 3.6 summarises the current understanding of cable ageing factors including thermal, radiation and environment. The section goes on to state that the combination of these factors is not fully understood. The storage of samples inside and outside containment addresses one of these variables, radiation. Whilst there are no similar controls in place for instance with humidity, Para 3.114 identifies the environmental monitoring system which capture actual operating conditions and is used to validate life calculations. The samples themselves are inspected by ERA, an independent research laboratory, which has considerable experience in the forensic analysis of cables.
UK-80 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 14 | non-prescriptive goal, which requires licensees to determine how best to achieve it and to justify their chosen approach |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-81 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 16 | The SAPs include a section on ageing and obsolescence within the engineering principles. This includes five principles, although the fifth is related to obsolescence and hence is outside the scope of this report. The four remaining principles relate to ageing and are as follows:  EAD.1 - The safe working life of structures, systems and components that are important to safety should be evaluated and defined at the design stage.  EAD.2 - Adequate margins should exist throughout the life of a facility to allow for the effects of materials ageing and degradation processes on structures, systems and components.  EAD.3 - Where material properties could change with time and affect safety, provision should be made for periodic measurement of the properties.  EAD.4 - Where parameters relevant to the design of plant could change with time and affect safety, provision should be made for their periodic measurement. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-82 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 18 | 2.24. The licensees’ approaches to ageing management incorporate guidance provided by IAEA Safety Report Series No. 15 (Ref. 16) and IAEA Safety Guide No. NS-G-2.12 (Ref. 17). They adopt a systematic ageing management process which is an adaptation of Deming’s ‘Plan-Do-Check-Act’ cycle, illustrated by Figure 2.1, and linked to a central requirement to ‘Understand’ SSC ageing and degradation mechanisms. To reflect this, the process is described in this report as ‘Understand-Plan-Do-Check-Act’ 2.25. The licensees’ approaches to ageing management are also compliant with the ageing management requirements of IAEA Specific Safety Requirements SSR-2/1 (Rev.1) Safety of Nuclear Power Plants: Design (Ref. 18), SSR-2/2 (Rev.1) Safety of Nuclear Power Plants: Commissioning and Operation (Ref. 19), and WENRA SRL I1.1 (Ref. 2). |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-83 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 18 | The NSPs/NSAPs are routinely reviewed (every three years) against relevant international standards, including IAEA SSR-2/1 and 2/2 and the relevant WENRA Safety Reference Levels, including WENRA SRL I1.1. 2.29. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-84 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 18 | EDF-NG performs a periodic review of safety for each of its power stations every ten years (paragraph 2.48). This includes a review of ageing, obsolescence and lifetime management against relevant national and international standards, including IAEA Safety Report Series No. 15 and IAEA Safety Guide No. NS-G-2.12. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-85 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 19 | Common, but commendable general practice: 2.36. The EDF-NG AMP is not a standalone process; it is integrated throughout the EDF-NG Management System. This is illustrated in Figure 2.2 below. It is designed to provide an integrated approach to identifying, analysing, monitoring and taking corrective actions and documenting the ageing degradation of structures, systems and components, in accordance with WENRA SRL I1.1. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-86 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 19 | And p 20 2.39. The Management System integrates safety, health, environmental, security, quality and economic objectives to ensure that safety is not compromised. It also provides the arrangements that fulfil the relevant Licence Conditions. The Management System is divided into 35 company processes, supported by numerous sub-processes. The key processes that have direct impact on ageing management are summarised below. 2.40. The three EDF-NG processes that have the most significant contribution to ageing management are:  Maintain Design Integrity (MDI) which manages the production, maintenance and implementation of the safety case. All SSCs are underpinned by a safety case. For significant or life-limiting ageing mechanisms, the safety case may also be supported by additional programme or surveillance arrangements (see paragraph 2.55). These additional arrangements are typically applied to significant irreplaceable passive systems, e.g. the reactor pressure vessel or graphite core.  Fleet Engineering, Equipment Reliability (ER) which manages the day to day plant condition and performance in accordance with the safety case. The focus of ER is predominantly upon plant and system components where active change in plant configuration and performance can be readily measured and managed.  Technical Governance (TG) which specifies the engineering standards and guidance to which the plant is designed (influencing the safety case) and controlled (influencing ER). TG supports both the safety case and ER processes. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-87 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 20 | 2.4.2 ….. For significant projects or vulnerable plant areas, the safety case may also include research and development (R&D) in order to underwrite the case. When compiling a safety case it is standard practice to include all reasonably practicable plant inspections where failure of the plant would result in significant consequences. For significant or life-limiting ageing mechanisms, additional programme or surveillance arrangements are put in place (paragraph 2.55). |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-88 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 20 | 2.4.2…… Any challenge to the safety case, either through a revealed plant condition or through a change in understanding (e.g. operating experience, changes to codes and standards, R&D, etc.) would be subject to an immediate assessment using the EDF-NG Safety Case Anomalies Process (SCAP), and appropriate action taken. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-89 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 20 | 2.44. Fleet Engineering, Equipment Reliability (ER) integrates and coordinates a broad range of activities to evaluate station equipment, develop and implement a long-term maintenance plan, monitor equipment performance, and make continuing adjustments to Preventative Maintenance (PM) tasks and frequencies based on equipment operating experience. ER controls the requirements for examination, inspection, maintenance and testing of the plant in accordance with the safety case. The stations’ Engineering Managers are responsible for the delivery of ER at their stations. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-90 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 20 | 2.45. Technical Governance (TG) provides the means by which the company specifies and monitors engineering standards and guidance to which the plant is designed and controlled. TG documents specify design standards, in-service controls, condition monitoring, the testing, maintenance and surveillances that support ER and the safety case. The Chief Engineer in the Design Authority is responsible for the TG documentation that specifies the standards and guidance. The stations’ Engineering Managers are responsible for implementation of TG standards on their power stations. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-91 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 22 | 2.4.7 ….. Organisational Learning Process (OLP) provides the means to identify, evaluate and address non-conformances, evaluate and make effective use of internal and external operating experience and to evaluate and assess the performance of areas under self-assessment and benchmarking programmes. This includes ageing-related plant events. OLP primarily supports the ‘Understand’ stage of the ageing management cycle (Figure 2.2), albeit noting that organisational learning is applied to all processes across the whole ageing management cycle. The station Performance Improvement/Continuous Improvement Managers are responsible for the performance of the OLP on their sites, supported by a corporate Fleet Performance Improvement Manager who manages and coordinates the overall programme. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-92 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 21 | And p. 22 Observation: Having only one operator, owning many, mostly very similar, operating units at 7 locations has made a comprehensive organization to keep track of, systematize and make new information operational a natural solution – and it seems to be very efficient |  | Observation noted.
UK-93 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 39 | Reasonable and commendable: Hinkley Point B being identical to Flamanville-3 and similar to the other French NPPs (as well as common ownership) makes cooperation with EdF France a natural – and prudent – practice, not only during the design phase 2.113. The Level 1 designer role provides the specifications for the System Requirements and controls a multitude of generic equipment specifications, engineering rules, tools, codes and standards etc. These documents have all evolved throughout the years of operating experience attained by EDF from within the French Fleet and internationally, the documents that hold this information are collectively called the EDF Referentials or Doctrines. These are owned and maintained by EDF’s Direction d’Ingénierie et Projets Nouveaux Nucléaires and are used as design references for new plant designs and modifications/refurbishment of the existing fleet. |  | It is noted that this is commending liaison with EDF France on Hinkley Point C.
UK-94 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 41 | 2.125, point 3: good practice it is important that full functionality must also be assured during a Postulated initiating event – and during the event 2.125. The development of both the design of the HPC EPRTM and the accompanying safety case is an iterative process, and the safety case has progressed over time as the design has developed. The latest version of the safety case, Pre-Construction Safety Report 3 (PCSR3), has been assessed by NNB against the NSDAPs. This assessment included consideration of the following section of the NSDAPs relevant to ageing management: 6.5.9.2 Ageing Management 1. Ageing management (AM) should be the measure to control the ageing effects. 2. Appropriate margins shall be provided in the design for all SSCs with safety function so as to take into account relevant ageing and wear-out mechanisms and potential age related degradation, in order to ensure the capability of the structure, system or component to perform the necessary safety function throughout its design lifetime. 3. Ageing and wear-out effects in all normal operating conditions, testing, maintenance, maintenance outages, and plant states in a Postulated Initiating Event (PIE) and post-PIE shall also be taken into account. 4. Provision shall also be made for monitoring, testing, sampling and inspection, to assess ageing mechanisms predicted at the design stage and to identify unanticipated behaviour or degradation that may occur in service. |  | It is noted that this is recognising the need to assure full functionality during a postulated initiating event.
UK-95 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation |  | General observation throughout chapter 2 Using the main characteristic, the graphite core and associated systems, of the AGRs as an example throughout chapter 2 is a good practice and gives a good understanding of one of the most important ageing issues for this type of reactors (in some respects similar to aspects addressed in the TPR-specifications for the CANDU-reactors) |  | Observation noted.
UK-96 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 54 | 2.4.1, para 2.203. TLSC are related to plant which is predominantly (but not limited to) passive plant components in the nuclear island, which will undergo quantitative assessment of damaging effects such as creep, fatigue, oxidation and irradiation on an appropriate timescale. This is typically presented as either a degradation limit (e.g. core irradiation), an operating limit (e.g. valid for a number of cycles or specified operations hours) or as a defined time period. The ongoing integrity of these cases and their associated plant is assured by the MDI process. The Component Life Assessment (CLA) is a key component of this for AGR reactor and boiler components. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-97 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 57 | Observations from the regulator: 2.5.1, 2.218. The EDF-NG Management System, and the supporting arrangements and organisation, undergo continuous review and improvement (paragraphs 2.47 and 2.59). As the EDF-NG AMP is integrated throughout the Management System, it also undergoes continuous review and improvement. ... A core part of this was the establishment of the ‘Fleet Approach’ (paragraph 2.47). This is based on a Fleet Management organisation with responsibility for establishing best practice standards across the fleet for core processes and programmes such as Operations, Engineering, Maintenance, Supply Chain, Fuel Route etc. This is led, for each core process, by a central Fleet Manager supported by their functional counterpart from each power station to form a ‘peer group’. The peer group develops long term and shorter term improvement plans to close any gaps to world best practice and performance in their area of responsibility. ... The development of a clear lifetime strategy has been a major improvement in the EDF-NG arrangements. The PLEX approach (see paragraph 2.48) and a clear station lifetime strategy via TLMS have provided clarity and visibility of the key components required to achieve the proposed lifetime. |  | This is largely a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-98 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 57 | Observations from the regulator: 2.218 cont.: The ageing management arrangements across the EDF-NG fleet have undergone significant improvements over this period. Primarily as a result of the changes discussed in the previous bullet points, but also as a result of specific focus areas including ER and TG. |  | This is largely a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-99 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 58 | 2.221 experiences: AGR boilers: AGR boiler ageing and degradation is subject to a comprehensive dedicated AMP (paragraph 2.55). The onset of creep/fatigue cracking in Hinkley Point B and Hunterston B boilers (the mechanism is discussed in Section 2.3.2.1) has led to extended outages to carry out additional repairs and inspections, and a reduction in plant load in order to reduce component temperatures. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-100 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 58 | 2.221 experiences: AGR graphite cores: The AGR graphite cores are also subject to a comprehensive dedicated AMP (paragraph 2.55 and examples discussed in Section 2.3). Keyway root cracks have been identified in the lead station slightly earlier than expected, but within the anticipated range for the onset of cracking. Nonetheless, as a result of these observations, the operational period of the affected reactor has been limited, with EDF-NG committing to further core inspections to better underpin predictions of crack progression and rate of crack opening in the core. This understanding will be used to underwrite the longer term safety case |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-101 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 58 | 2.221 experiences: There have been several events over the last decade involving leaks from, and failures of, concealed pipework (see Section 4). A fleet-wide project has been established covering all concealed systems, including cables, civil structures and pipework for systematically identifying and inspecting all concealed nuclear safety related plant in order to establish its condition and to take any remedial actions necessary. A risk-based inspection and repair strategy, based on the potential safety significance of each concealed system, is now in place. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-102 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 58 | 2.221 experiences: Internal and external oversight, plant inspection and a number of pipe failure events have identified a shortfall in the management of corrosion. External systems exposed to the corrosive effects of salt in the atmosphere, and in particular where corrosion has occurred under insulation or lagging, have been particularly vulnerable. A fleet-wide corrosion management programme has been established. As with the concealed system programme, a risk-based inspection and repair strategy, based on the potential safety significance of each system, is now in place. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-103 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 58 | Could you elaborate on the results of this review? 2.222, … The specific SSCs identified for review in Sections 3 to 8 have considered relevant IGALL documentation, and have not identified any gaps or shortfalls. Nevertheless, EDF-NG recommends that the periodic review and update of EDF-NG’s TG documents include review of relevant IGALL documents. EDF-NG plans to update its TG document review management process by 28 February 2018 to include the requirement to review IGALL during the three-yearly cycle of TG document updates. |  | EDF-NG Technical Governance documents set down the engineering standards for safety related plant. They are compiled by EDF-NG subject matter experts, which includes review of relevant standards and operating experience, albeit IGALL documents were not historically referenced. As part of this topical peer review, all relevant IGALL documents were reviewed by the subject matter experts for the plant covered by the review, and it was concluded that the EDF-NG documents are aligned with the IGALL documents. Sections 3 to 8 of the report contain the outcome of these reviews. All EDF-NG Technical Governance documents are subject to a periodic review and update, which will now include reference to IGALL documents.
UK-104 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 58 | Could you elaborate on the results of this review? 2.223. Although ageing management is established throughout the EDF-NG Management System, there is no single company document describing this approach. EDF-NG therefore recommends that the description of the EDF-NG ageing management arrangements, described in Section 2 of this report, be issued in a formal company guidance document. EDF-NG advises that this will be captured within its MDI process and will be issued by 31 March 2018. |  | Section 2 of the topical peer review has been issued as a company report, in order to help EDF-NG staff understand our ageing management arrangements. This brings together information from many other company documents across the management system into one document.
UK-105 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 60 | Regulator policy: 2.231. In line with established international practice, ONR uses the Licence Conditions to require the licensee to undertake a Periodic Reviews of Safety (PSR) for each site every ten years. Here the licensee has to review the impact of ageing on nuclear safety and demonstrate that the plant is safe to operate up to the next PSR. ONR undertakes comprehensive assessments of the licensee’s PSRs. It will only confirm that continued operation is acceptable if the licensee has demonstrated that it has an adequate strategy for dealing with ageing and obsolescence up until the next PSR. |  | Noted - there does not appear to be a question to respond to.
UK-106 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 61 | 2.7.3 ONR’s assessment of EDF-NG’s overall ageing management programme 2.236. EDF-NG has noted that ageing management is integrated into its management system, but it does not have a specific ageing management process. ONR recognises this and its SAPs note that whilst a specific AMP may be used, it is not a requirement. ONR therefore agrees that the approach adopted by the licensee is acceptable, provided it results in suitable ageing management processes for all SSCs. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-107 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 62 | 2.240. Periodic Safety Review (PSR) provides a ten-yearly review of safety at the plants. ONR can confirm that ageing is explicitly included in the licensee’s PSR process as set out in the IAEA’s Safety Guide SSG-25 (Ref 20). In recent years, ONR has assessed the latest PSRs for Sizewell B (Ref 29) and Hinkley Point B and Hunterston B (Ref 30). In each case ONR concluded that the licensee had carried out an adequate PSR to justify operation for the following ten years. The latest PSRs for the other AGR stations have all been started and are due to be submitted to ONR by January 2019, with regulatory decisions by January 2020. ONR supports the licensee’s claims for PSR. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-108 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 62 | 2.241. EDF-NG’s strategic approach to ageing is included in its Plant Life Extension (PLEX) projects, which cover the whole plant. ONR has reviewed submissions for irreplaceable components (Ref 31 to 33) and concluded that these did not reveal any significant flaws or omissions. ONR has further engaged with the licensee on its medium term plans for investment in the plants and was satisfied that the major investments it would expect to see for each station were present, including increased investment in corrosion, boiler modifications and nitrogen plant etc. ONR considers that the licensee is planning suitable investments in irreplaceable components to ensure that the effects of ageing are adequately mitigated. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-109 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 62 | 2.243. Within its review of ageing management reported in this chapter, the licensee has identified two areas for improvement:  The description of the EDF-NG ageing management arrangements, described in Chapter 2 of this report, should be issued in a formal company guidance document by 31 March 2018 (paragraph 2.223).  The periodic review and update of TG documents should include review of relevant IGALL documents. EDF-NG has advised that the TG document review management process will be updated by 28 February 2018 to include the requirement to review IGALL during the three-yearly cycle of TG document updates and hence this will be completed by mid-2021 (paragraph 2.222). ONR accepts that these improvements are appropriate and that the dates for their completion are acceptable. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-110 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 63 | 2.244. EDF-NG has a number of review processes embedded within its arrangements which contribute to understanding the impact of ageing on its plants. It has already been noted that ageing is not treated as a standalone process. Similarly, ONR notes that the licensee does not have a review process that looks at the impact of ageing as a whole. Given that the AGRs are reaching the ends of their operating lives, ONR considers that the licensee should ensure that it builds on its current processes for plant reviews and ensures that ageing management is explicitly considered. ONR has therefore asked the licensee to review its arrangements for the annual reporting of ageing management, and to include ageing management within an appropriate oversight process for each station for its reviews of performance for the calendar year 2018. These reviews for 2018 will start in early 2019, and hence the process will need to be in place by 31 December 2018. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-111 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 63 | Commendable that the licensee, on its own initiative, includes the most important ageing issue in its report for the TPR 2.245. In addition to its evaluations against the requirements of WENRA’s technical specification for national reports, EDF-NG has illustrated its processes for ageing management by describing how it enacts its AMP for graphite cores and reactor internal components. These are the two key AGR plant areas which are subject to important ageing mechanisms and significant regulatory interest. ONR agrees that these sections are an accurate description of the ageing management processes for these plant areas. |  | It is agreed that it was important to describe these two key plant areas to demonstrate effective ageing management.
UK-112 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 63 | 2.249. NNB has assessed the latest pre-construction safety case against its NSDAPs and found no gaps in its safety case. It has, however recognised that it needs to formalise its ageing management arrangements by producing a Corrosion and Ageing Management Strategy report in early 2018. ONR supports the production of this report. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-113 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 64 | 2.252. For EDF-NG, the stations require a full AMP. The licensee has noted that whilst it does not have a specific ageing management process, it nevertheless has all the elements necessary within its management system. ONR notes that this is consistent with its regulatory expectations. ONR’s assessment of the licensee’s contribution to this chapter of the national assessment report demonstrates that the licensee has an adequate overall AMP. |  | This is a quote from the text of the UK National Assessment Report and there does not appear to be a comment to respond to.
UK-114 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 64 | Repeats of “areas for improvement” (included above): 2.254. In spite of having adequate AMPs, ONR’s assessment has identified a number of areas for both licensees where improvements to ageing management would be beneficial. For the overall AMP, these are as follows:  EDF-NG should issue a formal company guidance document to describe ageing management arrangements, described in Chapter 2 of this report, by 31 March 2018 (paragraph 2.243).  EDF-NG should include review against relevant IGALL documents in the periodic review and update of TG. EDF-NG has advised that the TG document review management process will be updated by 28 February 2018 to include the requirement to review against IGALL during the three-yearly cycle of TG document updates and hence this will be completed by mid-2021 (paragraph 2.243).  EDF-NG should review its arrangements for the annual reporting of ageing management, and to include ageing management within an appropriate oversight process for each station for its reviews of performance for the year 2018, which will start in early 2019. (paragraph 2.244).  NNB should formalise its ageing management arrangements by producing a Corrosion and Ageing Management Strategy report by 30 June 2018 (paragraph 2.249). |  | The purpose of this paragraph was to bring all of the areas for improvements for both licensees together in the overall conclusions of Chapter 2.
UK-115 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 19 | At page 19 NAR mention that he EDF-NG AMP is not a standalone process; it is integrated throughout the EDF-NG Management System and it is designed to provide an integrated approach to identifying, analysing, monitoring and taking corrective actions and documenting the ageing degradation of structures, systems and components, in accordance with WENRA SRL I1.1. However some aditional information with regard to the quality assurance of the overall AMP, in particular, collection and storage of data and trending of information on maintenance his-tory and operational data and indicators used to assess the effectiveness of the process we would like to be provided for a complete understanding of the AMP. |  | Maintenance history is recorded on the station asset management system. Regular trending of equipment performance parameters either logged automatically by computer systems (e.g. PI historian) or available through installed instrumentation to Operations staff or Condition Monitoring measurement staff. Examples include pump pressure/flow, motor winding temperature, motor operated valve current, heat exchanger differential pressure/temperature etc. Condition monitoring is also carried out using many different technologies such as vibration analysis, chemical analysis, thermography, motor current analysis, etc. Regular trending of system performance information available via metrics published at monthly intervals. Example uses include trending of system related test failures, plant unavailability, Condition Reports, defects, standing alarms, output losses, modification backlogs etc. Periodic reviews of maintenance history and operational trends and data are also carried out as described in Section 2.4 of the UK report. Degradation due to ageing that impacts the plant condition or plant performance may be identified by these reviews, and appropriate actions put in place. There are multiple layers (defence in depth) of oversight which help inform the effectiveness of the company processes. These layers are informed by many different types of activities, including key performance indicators (KPIs) for system health, operational and maintenance activities.
UK-116 |  | General AMP expert group | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | N/A | Comment: The description of the AMP for nuclear installations in UK covers all elements required by Topical Peer Review 2017 - "Ageing Management Technical Specification for the National Assessment Reports" |  | Comment noted.
UK-117 |  | EC | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 29 | As indicated in point 2.66 there are a number of ageing and degradation mechanisms that are unique to AGR. Did any of these mechanisms have evolved in a faster way than originally expected? Where some of these mechanisms discovered during the NPP operation even recently (see example of Torness on page 45)? |  | As with all ageing and degradation mechanisms, there is a range of uncertainty which is accounted for in the safety case, with appropriate limits and conditions of operation and inspection programmes to account for these uncertainties. The safety cases also have defence in depth to cover for unexpected degradation. Research and development is also carried out in order to improve understanding and reduce uncertainty. Over the operating history of the EDF-NG AGR fleet, inspection results have been found across the range of expected uncertainties, high and low, with appropriate actions taken. This has included downrating reactors in order to reduce damaging mechanisms (for boilers) and increasing inspection frequencies. The mechanism referred to on page 45 did not challenge the understanding of brick cracking and graphite ageing and degradation in the graphite core.
UK-118 |  | EC | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 51 | point 2.181, how many reactors (and which ones) have seen their operational period being limited due to faster than anticipated ageing processes? Which were the SSCs mainly affected? Is the list on page 57-58 exhaustive? |  | As with all ageing and degradation mechanisms, there is a range of uncertainty which is accounted for in the safety case, with appropriate limits and conditions of operation and inspection programmes to account for these uncertainties. The safety cases also have defence in depth to cover for unexpected degradation. Over the operating history of the EDF-NG AGR fleet, inspection results have been found across the range of expected uncertainties, high and low, with appropriate actions taken. This has resulted in the operating period between graphite core inspections being limited for Hinkley Point B and Hunterston B. The list on page 57 and 58 covers all significant events.
UK-119 |  | EC | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 63 | Operation license for Hinkley Point C will be granted for 60 years (as mentioned in table 1, page 12). The construction already started in March 2017. ONR states that NNB has an adequate AMP while the ageing management arrangements are not included in it. Is this statement pending on the production of the report in 2018? |  | NNB has a site licence for Hinkley Point C. This licence will remain in place for the full duration of the plant's life through construction, commissioning, operation, defueling and decommissioning. Entering the operational phase of the stations life is one of the steps that will require permission from ONR. When the licensee is ready it will submit a request for permission to ONR accompanied by a safety case to demonstrate that it is safe to operate. Prior to granting the permission, ONR will assess the licensee's safety case and part of this will be to ensure that the licensee's arrangements for ageing management are adequate.
UK-120 |  | EC | United Kingdom | 02. Overall Ageing Management Programme requirements and implementation | 61-63 | In 2.236 is noted: EDF-NG does not have a specific ageing process. And in 2.244: EDF-NG does not have a review process that looks at the impact of ageing as a whole". Can you explain why then in the executive summary is stated that both operating/licensing companies have an AMP and assessed by ONR? |  | The report recgonises that EDF-NG does not have a specific process for ageing management. It does, however, show that EDF-NG's management system the elements necessary to manage ageing in accordance with the detailed requirements in NS-G-2.12. Fig 2.2 and the text descibing the processes for managing ageing demonstrate that the licensee has an integrated approach to identifying, analysing, monitoring and taking corrective actions and document the ageing degradation of structures, systems and components as rquired by the WENRA RLs. Section 2.7 of the report shows how ONR has assessed the adequacy of the licensee's ageing management through routine regulatory processes and assessment of the licensee's contributions to the UK report. It concudes that the licensee has adquated processes in place for manageing ageing.
UK-121 |  | EC | United Kingdom | 03. Electrical cables | 66 | It is written that for the Water Cooled Reactors, an extensive qualification programme has been followed. How is it with AGRs, were the cables not qualified? |  | The qualification of the PWR cables was focussed on those in containment and their ability to withstand credible faults such as a loss of coolant accident. The cables used in an advanced gas cooled reactor are all accessible and operate in significantly less harsh operating environments so the same qualification process was not deemed necessary.
UK-122 |  | EC | United Kingdom | 03. Electrical cables | 83 | Is there a comprehensive programme to replace old paper insulated lead sheathed cables that risk to fail if disturbed? |  | No. PILC cables are disturbed on occasion when exchanging HV motors and / or transformers. The key factor in minimising damage to the plumb connection at the cable box or in the cable is to ensure that it is properly supported using a scaffold structure. It is recognised that this is no guarantee and when recently replacing transformers the practice has been to cut the cables back to a horizontal section and then inserting a new XLPE cable using a jointing kit.
UK-123 |  | EC | United Kingdom | 03. Electrical cables | Generic 65-99 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found. |  | Noted.
UK-124 |  | EC | United Kingdom | 03. Electrical cables | Generic 65-99 | Are there any regular practices to follow up AGR cable ageing with laboratory tests on naturally aged cables (cable deposits, or replaced cables)? Or is it done only for samples of suspected cables? |  | There is no systematic programme in place to test AGR cables in laboratories. Autoclaves have been used for specific ageing programmes e.g. gas circulator motor windings, but these are the exception rather than the norm.
UK-125 |  | EC | United Kingdom | 04. Concealed pipework | 100-129 | Licensee has taken quite some efforts to improve AMP for concealed piping and to repair and replace concealed piping. But the way the report is written (focussing on few running reactors as examples for the whole fleet) makes it difficult to assess the current status of improvements in AMP and the status of repair and replacement of concealed piping. What is the design of concealed piping used in all running AGRs and PWR in terms of material, coatings and possible use of cathodic protection? How often is concealed piping inspected in all running AGRs and PWRs and which techniques are used? |  | Unfortunately, this level of detail would be subject to Export Controls so cannot be shared. In addition, it is considered that the scope of the review does not warrant this level of detail.
UK-126 |  | EC | United Kingdom | 05. Reactor Pressure Vessels | Paragraph 5.122, page 149 | What exactly means "No significant defect indications were found". It seems that some indications were found. What kind of indications? Why they are no significant?. |  | This refers specifically to the Bottom Mounted Instrument penetrations. These were not subjected to the same level of inspections pre-service. A decision was made, based on opex, to conduct more detailed examinations. These were in the form of ultrasonic and eddy current examinations. Five penetrations were found to contain recordable indications due to fabrication. The indications were found to be away from the wetted surfaced and confirmed by experts to not be significant.
UK-127 |  | EC | United Kingdom | 05. Reactor Pressure Vessels | Paragraph 5.209, page 161 | I support the licensee approach to use fluence-based approach to estimate irradiation damage as the first choice and a displacement per atom (dpa) based approach as secondary. There are very reliable embrittlement trend curves for the fluence approach. What it is needed is to demonstrate in some way that the effect of the change in the neutron spectrum is negligible or can be quantified. How do you approach this? |  | This will be followed up by new build. The change in neutron spectrum, due to the presence of the heavy reflector, has been analysed by EDF R&D. This analysis considers a tentative modification to RSE-M (from which the current, fluence-based embrittlement correlation is taken) to index it on dpa. This re-indexing has been applied to pertinent data sets obtained from the French operating fleet. The differences between the two indexations have been assessed, and in particular the difference in transition temperature at end-of-life predicted by the fluence-based approach and the dpa-based correlations is shown to be small. The potential impacts on the withdrawal schedule for surveillance capsules has also been addressed.
UK-128 |  | EC | United Kingdom | 05. Reactor Pressure Vessels | Paragraph 5.45, page 138 | In this paragraph it is mentioned: "Irradiation embrittlement is also relevant, mainly for the two core shells, but also for the transition ring and the Nozzle shell. Irradiation embrittlement is arguably the dominant ageing mechanism for the RPV." Question: Are the chemical contents of Cu, Ni and P of the transition ring and nozzle shell materials also limited (as it is the case for the traditional beltline region) ? |  | Yes, for Sizewell strict limits were placed on the material composition for all RPV components. For Cu 0.08& max, Ni 0.37 to 0.85% and P 0.008% max.
UK-129 |  | EC | United Kingdom | 05. Reactor Pressure Vessels | Paragraph 5.82, page 144 | It is advisable to include in the list the IGALL AMP160 on Neutron Fluence Monitoring and to have a similar AMP implemented in the UK plants. Was there a reason not to include it and do you intend to implement a similar AMP? |  | It is not clear why this was omitted, it was not identified on the IAEA website at the time of the review during Q3 2017. Nevertheless, neutron fluence monitoring forms part of the SP9 RPV surveillance programme. Each cycle specific safety case uses historical data and the predicted fluence for the coming cycle based on the proposed core design.
UK-130 |  | EC | United Kingdom | 07. Concrete containment structures | p59 | The report describes the regulatory oversight process, which seems to include inspections of many aspects covering indirectly or partly some aspects of the AMP. However, ONR does not seem to conduct a dedicated inspection focused on the whole AMP as part of its periodic inspection programme (i.e. outside the TPR). Please confirm. |  | ONR performs its regulatory functions by sampling the licensees' activities. As noted in the comment it includes many aspects of the licensee's AMP. ONR's regulatory approach does note require it to inspect the whole AMP.
UK-131 |  | EC | United Kingdom | 07. Concrete containment structures | p61 & p63 | Please clarify the statement “EDF-NG has noted that ageing management is integrated into its management system, but it does not have a specific ageing management process.” The licensee should have a specific / dedicated ageing management programme, effectively implemented, integrated into its integrated management system (cf IAEA SSR-2/2). Please clarify whether this is the case. |  | EDF-NG has an ageing management programme, as described in Section 2 of the report. It is integrated throughout the management system, with ageing management forming a key part of the companies activities. The description of how all of the ageing management activities work together has now been set down in an EDF-NG document.
UK-132 |  | EC | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | p217 | The report does not contain any information about the AMP concerning the containment steel liner of the PCPV in AGRs. This liner is an important element associated to the PCPV, with an important safety role. It should be covered in the report. Please provide detailed information about the AMP of this liner, its associated surveillance programme and operating experience. |  | The steel liner was not included as part of the TPR scope for Chapter 8 and hence was not specifically covered in the final AMP report. Its importance to the overall integrity of the PCPV pressure boundary is agreed. The liner Is not visible as it is covered with insulation panels on the reactor internals side and cast against concrete on the other face The performance of the liner is monitored shiftily by thermocouples to ensure that steel temperatures remain within technical specification limits during normal operation. OPEX to date has not presented any evidence across the fleet of liner defects or poor structural performance.
UK-133 |  | EC | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | p217 | The report does not contain any pressure test of the PCPVs in AGRs. Do you perform periodic overall pressure tests of PCPVs (i.e. above the operating pressure)? Do you perform periodic pressure tests to measure the leak tightness of PCPV penetrations? Please provide details of the tests and their periodicity. |  | All the AGR PCPVs were subjected to a vessel proof test during construction as per UK practice at the time and later embedded within BS 4975. The test level was equivalent to 15% above the design pressure (which is 1.1 times the operating pressure). The overpressure test is not repeated during the vessel operational cycle. Global losses of primary coolant are recorded and assessed during normal operation to evaluate any potential leakage from the vessel liner, penetrations & concrete boundaries. Safety Relief Valves are routinely assessed for functionality.
UK-134 |  | EC | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | p225 and p250 | As this might be a potential good practice, please provide details about the role of the APEX, the design authority, and the operating group, and in particular about who is deciding what and how they are independent. |  | Refer to Clauses 8.8 - 8.10. The PCPV Design SQEP(s) provide the responsible designer (RD) role as per INSAG-19 for the vessels with the APEX providing the independent oversight and surveillance. Design Authority manage the safety case aspects with appropriate technical input from the SQEP(s).The APEX cannot propose design changes or modifications to the vessel integrity but rather will review and agree to any proposals from the DA/RD SQEPs. The APEX role is functionally separate from the DA & RD and provides an independent technical conscience role that does not consider the commercial aspects of technical decisions that require to be made. The APEX prepares a mandatory stand alone inspection report for presentation to the ONR to underwrite the continued integrity of the vessel for the forward period of operation including any engineering recommendations to support this position. The APEX also fulfils the independent competent person role as per PSSR 2000.
UK-135 |  | EC | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | p225-231 | Please indicate the periodicity of all the items of the surveillance mentioned in §8.1.2. When only a sampling is performed (for example for tendon load checks or visual inspection of surfaces), please indicated the percentage that is checked at each periodicity. |  | Surface inspections - 3 yearly by the APEX at on load and shutdown condition, and supplemented by interim system owner walkdowns during periods of operation between statutory outages. Prestressing surveillance - 3 yearly. Tendon load checks are carried out on a sample of tendons - typically at least 1% in line with BS 4975 recommendations. Insulation & Liner - thermocouple data monitored shiftily. VWSGs - reviewed 6 monthly and also a 5 yearly review for comparison against FE model predictions of vessel strain behavior. PVCW leaks - assess during surface examination for evidence of leaks or routine checks of tell-tale drains. Bearing pads - 3 yearly where visual inspection is possible without removing surrounding materials.
UK-136 |  | EC | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | p243 | What is the acceptance criterion for PVCW leaks to be mandatorily repaired during outage before authorizing the reactor to restart? |  | The principle is for all known PVCW leaks to be sealed prior to return to service following a statutory outage on a best endeavours basis. Leak search and sealing activities are most successfully undertaken during periods of shutdown, although techniques are being developed for on-load leak repairs. The majority of small PVCW pipework defects (and hence the hardest to seal) tend to close when the reactor is shutdown. This can lead to problems when attempting to leak search & seal whilst off load. Sometimes, the repaired leak can manifest again upon the unit return to service. Hence a safety case must exist to justify safe operation with active PVCW leaks. Further development work continues to be undertaken to improve leak search and sealing capabilities for the fleet PCPVs.
UK-137 |  | EC | United Kingdom | 08. Pre-stressed concrete pressure vessels (AGR) | p244 and p227 | Please indicate clearly the acceptance criterion for cracks in PCPV and how they are repaired when needed. According to the report, it seems that cracks smaller than 1,0mm in width are only monitored but not repaired. This is not in line with international consensus (see namely TECDOC-1054 p75 and NP-T-3.5 p203) that recommends to repair much smaller cracks (around 0,3mm width for indoor cracks). |  | Cracks less than 0.5mm in width not associated with changes in section or areas of high stress combination are generally considered as not significant. Cracks between 0.5mm and 1.0mm in width are typically monitored for abnormal crack development. Cracks greater than 1.0mm in width are generally assessed utilising demec gauges, photography etc. with reference made to the vessel analysis for possible areas of high stress. The cracks to date are attributable to shrinkage action and localised cracking at construction joints or localised surface stress concentrations near to penetrations. The cracks do not extend beyond the outermost layer of prestressing due to the global compression in the vessel and are limited to surface cracking only. Since they are not structurally significant, repairs have been limited to date as generally recourse to remediation is not required as there is no change or risk to the expected structural behaviour of the PCPV design intent.
RO-1 |  | Poland | Romania | 03. Electrical cables | 45, 52, 56, 68 | 1. What are methods and criteria used for selecting electrical cables within the scope of ageing management? In paragraph 3.3.1 a) there are no information about that. 2. What are established acceptance criteria related to ageing mechanisms? In paragraph 3.1.2 A b) there are no information about any acceptance criteria. 3. What are frequencies of mentioned in this paragraph actions related to ageing control of electrical cables in the Cernavoda NPP? 4. What are frequencies of testing actions related to ageing control of electrical cables in the TRIGA RR? | Website | Cernavoda NPP 1. Selecting electrical cables within the scope of aging management is done depending on the type of cabling insulation, the equipment it serves, the area where the cable is located, the degradation mechanisms and the internal and external operating experience. 2. Acceptance criteria are established in connection with aging mechanisms and are provided by the manufacturer, the applicable national regulations and national and international standards, as a result of measurements performed and the EPRI recommendations. 3. The frequency with which all the actions are carried out is at each scheduled plant outage (every 2 years for each Cernavoda NPP unit). TRIGA Reactor - ICN Pitesti 4. The testing actions related to the ageing control of electrical cables for the TRIGA research reactor are performed annually. Verifications are performed in accordance with the provisions of a national standard issued by the Ministry of Energy applicable to Maintenance and Repairs activities and Testing of Electrical Installations.
RO-2 |  | Bulgaria | Romania | 02. Overall Ageing Management Programme requirements and implementation | p. 27 | From the text it is not clear if only non- mandatory inspections include activities performed by “third party certification organizations” or those organizations are used also for mandatory inspections. Please clarify this. | Website | The most important mandatory inspections – such as those for Steam Generators, Fuel Channels, Feeders, Containment structure- are performed by third party organizations – especially the manufacturer or the designer of these assets. Other mandatory inspections-such as for nuclear piping, pumps, vessels, valves, – are performed by Cernavoda NPP personnel. The same approach was used also for the non-mandatory inspections: the majority are performed by external organizations, mainly local contractors (e.g. heat exchangers inspections, snubbers testing, buried pipe inspections, vibrations measurement), but some are performed by Cernavoda NPP personnel (Flow Accelerated Corrosion, Main Steam Line, Supports & hangers, Expansion Joints, cables). There is no general rule to perform the mandatory & the non-mandatory inspections by certain organizations, it was decided on a case by case situation, depending on many factors such as: - the impact of equipment failure on plant reliable operation, or extension of normal outage duration, - the complexity of plant life management inspection services which require specialized tools and certified personnel to perform it; - and the need for continuity in the assessment of the results.
RO-3 |  | United Kingdom | Romania | 03. Electrical cables | 68 | "TRIGA Research Reactor Please explain the international practice(s) that have been used to develop and establish the overall AMP for electrical cables and confirm compliance. " | Website | Only Romanian standards (issued by the Ministry of Energy, applicable to Maintenance and Repairs activities and Testing of Electrical Installations) have been used by the development and implementation of the AMP for electrical cables. IAEA guidance documents and reports related to ageing of research reactors were consulted when available.
RO-4 |  | United Kingdom | Romania | 03. Electrical cables | 68 | "TRIGA Research Reactor Please explain: (i) the electrical testing undertaken; (ii) the periodicity of the tests to be undertaken; (iii) the electrical parameters recorded; (iv) how the electrical parameters are assessed; (v) electrical parameter acceptance criteria" | Website | (i) the electrical testing undertaken - high voltage testing; insulation resistivity; (ii) periodicity: once/year in correlation with the maintenance program (iii) the electrical parameters recorded: loss in dielectric insulation; electrical resistivity of conductors; thermography of cables junctions and terminals (iv) the electrical parameters measured are compared with the initial values and accepted limits for utilization. (v) the measured values should be comparable with the normal parameters for utilization.
RO-5 |  | Finland | Romania | 03. Electrical cables | 42-58 | Report does not clearly indicate if there are cables which have performance requirements in case of accident conditions. If there are such cables how this is considered in the AMP? Are there cable sample depositories? | Website | There are cables that have performance requirements for accident conditions but they have been qualified for the conditions in which they have to fulfil their functions and from ageing management point of view they are treated like other cables without any other difference. At Cernavoda NPP there are no cable sample depositories.
RO-6 |  | United Kingdom | Romania | 07. Concrete containment structures | 122 | Section 7.2.A states "the main ageing issues related to buildings and structures at Cernavoda U1 up to date have been with the elastomeric components". There is no other mention of elastomeric components in the Chapter. Please provide more information on the elastomeric defects encountered to date. | Website | The NR-5S 400 (Normac) has been successfully used in dry scenarios for lining the containment boundaries and it is qualified material for use as a non-metallic liner under the standard CSA N287.2-08 (Material requirements for concrete containment structures for CANDU nuclear power plants). At Cernavoda NPP this material (Normac) was removed in the Dousing Tank, under water level.
RO-7 |  | Switzerland | Romania | 03. Electrical cables | 43 | Textline34: Why is the operating temperature = 150°C? Are these mineral isolated cables? | Website | This temperature is the specified temperature by the manufacturer, the temperature at which the cables are designed and tested. It is not the actual operating temperature. Yes, these cables are mineral isolated cables.
RO-8 |  | Switzerland | Romania | 03. Electrical cables | 45 | Textline13: Where are PVC-cables applied? Are there no problems with HCl in case of fire? | Website | The PVC cables are installed in areas without radiation (they are not installed in radiological areas). The PVC cables are protected with fire retardant coatings and some of them are located inside metallic pipes.
RO-9 |  | Switzerland | Romania | 03. Electrical cables | 45 | Textline16: What experiences are made with Hypalon (ClSO2-PE)? Where is it applicated? What are the (dis-)advantages? | Website | The CSPE cables (Hypalon) do not benefit from additional tests compared to other types of cables in the Cernavoda nuclear power plant. They are applicable everywhere in the Cernavoda nuclear power plant.Advantages are as follows: - very low cost; - excellent chemical resistance; - good resistance to low temperatures; - excellent electrical insulation properties; - very low water absorption. And the disadvantages are : - prone to crack in stress conditions; - lower rigidity than polypropylene; - low UV resistance.
RO-10 |  | Switzerland | Romania | 03. Electrical cables | 47 | Columne7: Why are cables passing through / connecting to reactor building penetrations not replaceable? | Website | The cables that pass through the reactor building penetrations can be replaced, but this requires a preliminary assessment and it can be done only with the reactor shut down
RO-11 |  | Czech Republic | Romania | 03. Electrical cables | 43 | "The Canada Wire fabrication cables, used for SDS 2 (Shutdown System #2) and HFD (Horizontal Flux Detectors), according to test report, were tested at a total integrated dose (normal dose + accident dose) of 300 Mrads. The operating temperature for these cables is 150°C." (3.1.1.1) How long is operating time of this cables? Is it mineral cable? | Website | This temperature is the specified temperature by the manufacturer, the temperature at which the cables are designed and tested and not the actual operating temperature. Yes, these cables are mineral isolated cables.The operating period of these cables was estimated for at least 30 years in conditions that are enveloping of the actual operating conditions (i.e. conservative assumptions have been used).
RO-12 |  | Czech Republic | Romania | 03. Electrical cables | 49-51 | "Whole document is written very generally. It seems to me like a set of action that should be done. I am not sure if it is really done (measurements of cables at NPP, environmental monitoring etc.). E.g on page 49-51 is list of measuring methods. Does it contain methods you really use for measuring, or it is only a list of possible methods? " | Website | The most effective methods for determining the state of degradation are listed. Only some of them are currently used by Cernavoda NPP (like: Polymer ageing Monitor by INDENTER and measurement of ohmic resistance), but we intend to use as many of them as possible.
RO-13 |  | Bulgaria | Romania | 02. Overall Ageing Management Programme requirements and implementation | p.6 | Would you please clarify whether the following IAEA safety standards, reports and guides and WENRA report had been used too: 1.IAEA, Data Collection and Record Keeping for the Management of Nuclear Power Plants Ageing, Safety Reports Series No. 50-P-3, IAEA, Vienna (1991) 2.IAEA, Implementation and Review of a Nuclear Power Plant Ageing Management Programme, Safety Reports Series No. 15, IAEA, IAEA, Vienna (1999) 3.IAEA, Equipment Qualification in Operational Nuclear Power Plants: Upgrading, Preserving and Reviewing, Safety Report Series No. 3, IAEA, Vienna (1998) 4.IAEA, Periodic Safety Review of Nuclear Power Plants, Safety Standards Series No. SSG-25, IAEA, Vienna (2013) 5.IAEA, A system for the Feedback of Experience from Events in Nuclear Installations, Safety Guide No. NS-G-2.11, IAEA, Vienna (2006) 6.IAEA, Maintenance, Surveillance and In-service Inspection of Nuclear Power Plants, Safety Standards Series Safety Guide No. NS-G-2.6, IAEA, Vienna (2002) 7.WENRA Report, Safety Reference Levels for Existing Reactors, 2014 | Website | 1. SRS 50-P-3, Not directly used, but the specific sections in NSG 2.12 AM and NSG 2.6 have been analysed in 2016. No gaps were identified as compared with IAEA guidance on data collection and records keeping. 2. SRS 15: Yes, used in the elaboration of PLiM Manuals for PIPING Surveillance (FAC) , HXs, Expansion Joints. 3. SRS 3: Yes, used in the station instruction developed to implement the Environmental Qualification Program at Cernavoda NPP (SI-01365-T051). 4. SSG-25, Yes, used indirectly in the Reference Document RD-01364-L008 “Administration of Cernavoda NPP Nuclear Safety Licences”, based on specific regulation NSN-10 for Periodic Safety Review, which is aligned with SSG -25. 5. NS-G-2.11, Yes, Cernavoda NPP OPEX program was initially tailored based on IAEA 1989: “Feedback Operational Safety Experience from operating NPP”, and subsequently, applicable IAEA documents were used to make improvements during application. In 2016 a self-assessment was performed regarding compliance of Operational Feedback System at Cernavoda NPP with the requirements of NS-G-2.11 and no gaps were identified. NS-G-2.11 was also used by CNCAN for the elaboration of the regulation NSN-18 on the use of operational experience. 6. NS-G-2.6, Yes, used in the specific procedures: SI -01365-P009 Preventive Maintenance and : SI -01365-T057 “Periodic Inspection Program”. Also used by CNCAN for the elaboration of the regulation NSN-16 on surveillance, testing, maintenance and in-service inspection. 7. WENRA Reactor Safety Reference Levels Report,Yes, it was used in the Reference Document RD-01364-L008 “Administration of Cernavoda NPP Nuclear Safety Licences” and also used in CNCAN regulations
RO-14 |  | Finland | Romania | 05. Reactor Pressure Vessels | Chapter 5 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Website | Up to present, as resulted from System and Component Health Monitoring programs, Cernavoda NPP has not identified any issues associated with AMPs, susceptible to affect one of the nuclear safety functions.
RO-15 |  | Czech Republic | Romania | 07. Concrete containment structures | chapter 2 - generally (34-37) and chapter 7 - generally (111-123) | How often - or if even - are the inspection intervals of civil structures reassessed? Are those inspection intervals changes based on operational experiences and ageing effect treds? Is the NPPs age, especially when considering the LTO phase of operation with higher risk of ageing effects appearance), taken into account for establishment of the inspection intervals? | Website | The inspection intervals are established in accordance with technical standards (Canadian standards and national Civil Constructions prescriptions). These can be changed if the standards or local norms are revised, if any problems occurred, or if it appears as necessary, following any assessment /testing report results
RO-16 |  | Czech Republic | Romania | 07. Concrete containment structures | chapter 07.1.2A (115-119) | Have you ever detected the ASR (alkali-silica reaction) in reinforced concrete structures structures of nuclear power plants during their operation? If so, which parts of structures were affected? Please describe, if the appearance was found in monolithical parts of constructions built on site or in imported prefabricated materials. If ASR was found, how did you proceed this issue? | Website | This kind of degradation was identified on monolithic parts. It was identified on the protection concrete around the ring beam. The injection was performed in the cracks and the sealing material was applied on the upper side.
RO-17 |  | Czech Republic | Romania | 07. Concrete containment structures | chapter 02.3A and 02.3B. (7-34) | In what form you have processed the zero-condition passportization of flaws and malfunctions of NPP civil structures? Is this base passportization updated on the basis of results of regular maintenance activities and/or more detailed survey of intednded structural objects? Do you regulary evaluate appearance of new flaws or changes in previously found flaws and malfunctions with respect to the base zero-condition passport? What kind of documentation do you use for planning and conducting of this constructional-technical survey (e.g. ISO 13822)? What kind of degradation that was found within the constructional-technological surveys is most often (please provide examples, e.g. shear cracks, bend cracks, shrinkage and creeping of concrete, carbonation of concrete CO2, corrosion of reinforcement or concrete, mechanical overload, stability loss of constructions - tilting, bracing, excessive bending, etc.)? | Website | Civil structures are monitored since the start of the operation, all the degradation indications have been assessed and the solutions for repair have been implemented. All the information gathered was used for the Life Assessment Study.
RO-18 |  | Czech Republic | Romania | 07. Concrete containment structures | chapter 07.1.3A(120) | Do you have geodetic measurement and assesments of settlement and tilt of civil structures important for (main production block, containment, confinement) and related to (ventilation chimney, building with dieselgenerators, blackout dieselgenerators, main pump station, end heat receiver, etc.) nuclear safety in your aging management programs? Did you find any problems with uneven foundation settlement of NPP civil structures? Did you identify any typical flaws (shear cracks) caused by civil structures settlement? If so, please specify and describe, how did you deal with this issue | Website | The settlement measurements are performed for the major civil structures, such as: Intake Basin structures, Discharge Channels, Turbine Building, Service Building, Emergency Core Cooling System Building, Diesel Generators, etc. Basically all the technological buildings on Cernavoda site are monitored for settlement. We have faced no problems so far. The foundations of all these major civil structures were made in massive rock.
RO-19 |  | Czech Republic | Romania | 07. Concrete containment structures | chapter 07 (111-126) | In what way and how often do you perform monitoring of containments steel hermetic lining condition? Is it measured punctually on test spaces chosen in advance within the construction phase, or is the measurement conducted aeraly e.g. by phased-array probes? Did you change test spaces during operation or was the number of test spaces extended/narrowed based on the inspection results? Have you ever found problems with thickness weakening in base material or weld joints of the containment hermetic steel lining during operation of any nuclear facility ? If so, please specify and describe, how did you deal with the situation. | Website | On the perimeter wall there is a non-metallic liner.
RO-20 |  | Netherlands | Romania | 02. Overall Ageing Management Programme requirements and implementation | 02.4A | The evaluation against IAEA standards et cetera started in 2016 and finished end of 2017. It is unclear if the findings were implemented at the same time or have to be implemented beyond 2017. Please explain. | email | Since 2009, IAEA Guides have been used as reference for some PLiM Program Manuals, for the selection of PLiM components, or for the elaboration of Life Assessment studies. Afterwards, the first gap analysis of IAEA Guides NSG 2.12 and SRS57 and the self-assessment of IGALL AMPs was performed in 2014, but a systematic evaluation started in 2016, when the Regulation on Ageing Management (NSN-17) was issued, which required specifically such an analysis. In the meantime, the above mentioned guides have been combined in the new DS485 and the AMPs have been continuously enhanced and approved by the end of 2017, when IGALL Phase III ended. As such, the intention of the action plan, for complete alignment to NSN-17 requirements, was to perform a systematic analysis of the latest IAEA Guides & IGALL AMPs and to address any gaps identified in a future revision of the specific program Manuals. It was considered a good opportunity to find any weaknesses and take actions to enhance our programmes before the next scheduled PSR evaluation.
RO-21 |  | Netherlands | Romania | 02. Overall Ageing Management Programme requirements and implementation | 02.4A | Has it been considered to invite an IAEA SALTO mission? | email | Yes, it has been considered and a Preliminary Workshop is organized with IAEA support, between 28-30.08.2018, on Cernavoda site. This will continue the initiative taken in 2016 by the Romanian Regulatory Authority, CNCAN, to familiarise all the technical personnel involved in Romanian nuclear industry ( Regulator, utility plant and headquarters and local research institutes) with IAEA assessment missions (SALTO, OSART) and programmes (IGALL) in support of Member States
RO-22 |  | Netherlands | Romania | 02. Overall Ageing Management Programme requirements and implementation | 02.4B | What were the main improvements needed after the reassessment of the 2013 AMP in 2017? Have they already been implemented? | email | TRIGA Reactor - ICN Pitesti: More systematic documentation of the integrated ageing management program was performed. The list of SSCs in the scope of the AMP and the list of ageing-related mechanisms and methods for detecting ageing degradations have been updated and supplemented.
RO-23 |  | Netherlands | Romania | 02. Overall Ageing Management Programme requirements and implementation | 02.4B | Are IAEA INSARR missions considered (they contain an AM-module). Since 2017 also a LTO mission for RR is available. | email | TRIGA Reactor - ICN Pitesti: The IAEA INSARR missions considered the application of IAEA guides concerning AM SSG-10.
RO-24 |  | Netherlands | Romania | 02. Overall Ageing Management Programme requirements and implementation | 02.6 | The inspections on AM have become more systematic. Please provide more detailed information which new systematic elements of the AM inspection have been introduced,that were not performed before. | email | Before the issuance of the NSN-17 regulation, CNCAN was focusing on system inspections and was assessing ageing management only for specific systems, structures and components (SSCs) important to safety. The new approach covers also the programmatic elements of an ageing management program and supplements the inspections focused on the conformance with the design and reliability requirements of the SSCs important to safety.
RO-25 |  | Netherlands | Romania | 03. Electrical cables | 3.1.2A(b) / p.55 | How is the outcome of these testing methods transformed into acceptance criteria, and is that process incorporated in the AMP (or PLiM/PM)? | email | Depending on the results of the tests performed and the comparison of the obtained results from the measurements with the actual regulations, results values are compared if they are in the acceptance criteria or not. Some of these acceptance criteria are included in PLiM / PM and it will be reviewed to incorporate all of them.
RO-26 |  | Netherlands | Romania | 03. Electrical cables | 3.1.2B / p.66 | The content of 3.1.2B seems to be what is actually requested under the Tech.Spec. of the TPR in its section 3.1.1 (a,b,c). Could the RB or licensee provide some information for the TRIGA-RR on: - what it has found to be the most significant degradation mechanisms and how their ageing is managed; - how the criteria for replacement or acceptance are implemented in the RR's AMP. (i.e. please answer questions (a,b) from TPR Tech.Spec. 3.1.2) | email | TRIGA Reactor - ICN Pitesti: -The most significant degradation mechanism is electrical stress for high voltage cables. Affected cables are replaced when the insulation resistance trend to minimum accepted value. -Cables are replaced when defected without compromising nuclear safety due to redundancies
RO-27 |  | Netherlands | Romania | 03. Electrical cables | 3.2B / p.68 | The defect in the cable was discovered during an unplanned maintenance. Could it be concluded that the AMP for the TRIGA-RR was not adequate in this case? | email | TRIGA Reactor - ICN Pitesti: The mentioned unscheduled maintenance was performed on a non-safety system. The failure analysis did not reveal any weakness of the AMP.
RO-28 |  | RPV expert group | Romania | 05. Reactor Pressure Vessels |  | Which organization perform the periodic inspections? Is it the licensee or an independent laboratory? | expert group 2 | Cernavoda NPP: The periodic inspections for the pressure tubes are performed by AECL (now called Candu Energy Inc.), the original designer and engineering company for Cernavoda NPP’s fuel channels. TRIGA Reactor - ICN Pitesti: TRIGA RR does not have a pressure vessel; the reinforced concrete reactor pool has an aluminium liner. The operating organization performs periodic inspection of the liner.
RO-29 |  | RPV expert group | Romania | 05. Reactor Pressure Vessels |  | If a laboratory perform the NDT- inspections, is the laboratory accredited for the type of inspections that are carried out under the periodic inspection program? | expert group 2 | Cernavoda NPP: Yes. The laboratory or company that performs NDT inspections is qualified and accredited for this type of inspections, according to the CAN/CSA N285.4 Standard as well as by the Romanian regulatory bodies (ISCIR and CNCAN). TRIGA Reactor - ICN Pitesti: The NDTs are performed by the research reactor operations team, who have the required qualifications and authorization in accordance with national standards and regulations.
RO-30 |  | RPV expert group | Romania | 05. Reactor Pressure Vessels |  | Are the methods, systems and personal used for the periodic inspections qualified? | expert group 2 | Yes. The methods, systems and personnel are qualified and authorized internally by the licensees and also by the regulatory authorities - ISCIR (Romanian regulatory authority for pressure vessel and systems) and CNCAN, before any inspection is performed. The inspection work plans, technical documents, systems and methods must be accepted by CNCAN before the inspection.
RO-31 |  | RPV expert group | Romania | 05. Reactor Pressure Vessels |  | If so, what requirements are applied for the qualification? Who is supervising the qualification? | expert group 2 | Cernavoda NPP: The requirements for the qualification follow all the clauses of CAN/CSA N285.4 Standard. In addition, the Romanian requirements (as issued by CNCAN and ISCIR) must be followed as well. The level of Qualification is requested in the Framework Agreement and is demonstrated with updated qualification documents on each inspection. These requirements are in line with the industries best practices, as well as all guideline documents. TRIGA Reactor - ICN Pitesti: The periodic inspections are performed by the operations team, qualified internally by the licensee’s organization. Also the Institute ICN holds an authorization issued by the regulatory body CNCAN on quality management system for operation activities.
RO-32 |  | RPV expert group | Romania | 05. Reactor Pressure Vessels |  | The estimation of time to contact between the CTs and the LINs for Cernavoda Unit 1 is 264 kEFPH. Does the estimated time include a margin? How large is the margin? | expert group 2 | Yes, a margin is included. The estimated time to CT-LISS contact is conservatively given as the lowest-bound value (taken as 97.5% LPL- Lower Prediction Limit) that resulted from qualifying the prediction model with inspection results and measurements. According to the CT-LISS gap assessment performed in 2016 by Candu Energy Inc. the estimated time-to-contact is expected to increase, as a result of more accurate prediction (from future inspection results).
RO-33 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 111 | Please visualize the layout and anchorage of the prestressing tendons with a representative drawing, particularly for the sub-base gallery (accessible for inspections). | expert group 4 | The pre-stressing cables are inside of concrete structure. It is not possible to see any anchorage, the concrete covered pre-stressed tendons.
RO-34 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 111 | Is it possible to assess the condition of the sliding membrane below the sub-base slab? | expert group 4 | No, it is not possible because this area is not accessible.
RO-35 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 112 | Are the elastomer liner coatings (epoxy, polyurethane) fully accessible for visual inspections and repair measures? | expert group 4 | The elastomer liner coatings (epoxy, polyurethane - Normac) are mostly in accessible areas for inspections and repair, except for some areas, where the access is subject to restrictions depending on the operating status (e.g. areas with high level radiation fields during full power operation).
RO-36 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 115 | Are there prestressing cables which are exposed to elevated irradiation? How can the potential degradation effect be monitored? | expert group 4 | The pre-stressing cables are inside of concrete structure. The potential degradation effect can be reviewed and monitored, if it will be necessary. It has been assessed in Life Assessment study for U1 (elaborated after 20 years of operation and 30 years since it was erected), with no concern, so far, for this degradation mechanism.
RO-37 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | In which time intervals are the containment structures inspected and how are the results documented? What is the interval for the leak rate tests? How many periodic AM reports are available so far, for units 1 and 2? | expert group 4 | During every planned outage (every 2 years, for each NPP Unit) an inspection is performed by a civil system engineer and another one for monitoring the behaviour of the Containment structure is performed by Reactor Building PLiM program responsible. Leak rate tests have been performed for Unit 1 in 1998, 2003, 2008, 2014 and another one is scheduled for 2018; for Unit 2, leak rate tests have been performed in 2006, 2011 and 2017. Ageing management information is part of the quarterly periodic system health monitoring reports for the containment system. Detailed reports on the containment system status and performance are issued after the leak rate tests.
RO-38 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | Why are not all the structures included in the scope of in-service inspections? | expert group 4 | It was a misunderstanding. There are inspections performed as part of Reactor Building PLiM structures program, such as: - pre-stressing gallery (accessible at full power operation and monitored once per year); - Calandria Vault Structure (accessible only in outage and monitored once every two years).
RO-39 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | In addition to the visual inspections of the concrete surfaces, do you consider using onsite instrumental inspections and laboratory material testing as part of the aging management? (e.g. carbonation progress, corrosion potential of reinforcement, material strength, concrete cover depth, ...) | expert group 4 | Yes, the use of instrumental inspections is an improvement area to be introduced in the next stage of the programme enhancement. A general revision of the actual PLiM Program Manual is scheduled to be elaborated by the beginning of 2019, using the insights and the technical support of CANDU Energy Inc, who performed also the Life Assessment studies for U1 &U2.
RO-40 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | How are acceptance criteria for the inspected concrete structures defined? (crack width and depth, crack patterns, carbonation depth, prestress loss, ...) | expert group 4 | The acceptance criteria are established in the CSA standards for concrete containment structures. These standards are part of the licensing basis for the plant. After visual inspection, a report is issued, which includes conclusions and recommendations for each of the indications that were identified and for which corrective actions were implemented. For loss of pre-stress tension there are in place specific tools and monitoring reports (deformation strain gauges and beam test). For the moment, all the indications discovered during the inspection program, were dispositioned with support from CANDU Concrete Containment designer, who was awarded a long term agreement for technical support and technical solutions for repair.
RO-41 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | How are acceptance criteria for the monitored settlements? What is the long term experience on settlements? | expert group 4 | Usually the settlement value is less than 1 mm, and the acceptable value is 200 mm. At Cernavoda NPP location, this settlement is acceptable for technological buildings.
RO-42 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | How is the collection and investigation of concrete and reinforcing steel from structural interventions (reconstruction, partial demolition, ...) organized? | expert group 4 | The collection and investigation of concrete and reinforcing steel from structural interventions will be organized as necessary when such situations will occur.
RO-43 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | How are the data from the Vibrating Strain Gauges evaluated and how is this information implemented in the aging management process? | expert group 4 | In Cernavoda NPP deformation monitoring is done in cold and hot weather conditions, as well as in every planned outage. The Design Institute (the Service Provider of such assessments) issues an interpretation and a presentation report. Regarding the ageing management process a special report will be issued by the Canadian Service Provider in the beginning of 2019.
RO-44 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | Is there a concept available for monitoring the grouted tendons? | expert group 4 | Yes, it is based on deformation and test beam reports.
RO-45 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | How are the structures and the structural elements assessed which are inaccessible for visual inspections? (indirect/indicative methods?) | expert group 4 | The thermography tests and leak detection using soap solution (during the time of the reactor building leak rate test) are available and used at NPP Cernavoda. Our intention is to review other non-destructive methods and adopt other methods in the new revision of the program manual.
RO-46 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | Aging management requires the condition assessment for different types of structures and structural elements, such as secondary structures, anchorage elements, water-proofing sealings, drainage, coatings, fire-retarding sealings, etc. Are all these types included in the inspection programs? | expert group 4 | All these types of condition assessment are included in the inspection programs and are tracked using the current and special tracking program of building behavior in operation (Civil Structures Monitoring Program). In the future, these issues can be improved within the IGALL specific Working Group for Civil Structures and will be part of the enhanced Reactor Building PLiM Program and Civil Structures Monitoring Program.
RO-47 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | How are the fire protecting structural elements monitored? | expert group 4 | All penetrations in fire protection barriers are coded and they are inspected periodically in accordance with specific procedures.
RO-48 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 120 | Are there specific testing and inspection requirements for safety related anchorage elements? (e.g. pull-out tests with acceptance criteria) | expert group 4 | Anchorage elements are inspected only visually.
RO-49 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 121 | What insights result from the test program on the 3 beams with unbonded tendons? Can the findings be applied to the behaviour of the other beams with grouted tendons? | expert group 4 | The reports for the test beams are based on both the beams with grouted tendons and on the beams with un-bonded tendons. The analysis takes into account both types of testing. The results did not show significant difference between the 2 methods, but further evaluation is needed, as recommended by Life Assessment study (the results should be combined with deformation system information/data).
RO-50 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 111 - 114 | The content of para “07.1.1A Scope of ageing management for concrete structures” of the Romania NAR does not correspond to the requirements listed in section 07.1.1 of RHWG REPORT TO WENRA. In para 07.1.1A of the Romania NAR, there is no information related to: - methods and criteria used for selecting components within the scope of ageing management (see item “a” of para 07.1.1 of RHWG REPORT TO WENRA); - processes/procedures for the identification of ageing mechanisms for the different materials and components of the 07. Concrete containment structures and associated methods and criteria (see item “b” of para 07.1.1 of RHWG REPORT TO WENRA). This information should be added to the Romania NAR or corresponding clarifications might be provided as an answer. | expert group 4 | Section 07.1.2A Ageing assessment of concrete structures explains how the ageing mechanisms have been identified: based on specific technical literature from EPRI, IAEA, COG and CSA reference documents that reflect the operating experience in this area. The components selected in the scope of the AMP have also been identified based on the standards for periodic inspection of the concrete containment structures and on industry guidelines and good practices that make use of the available operating experience.
RO-51 |  | Concrete containment PCPV expert group | Romania | 07. Concrete containment structures | 115 - 120 | The content of para “07.1.2A Ageing assessment of concrete structures. Life Assessment Study”, in general, corresponds to the requirements listed in section 07.1.2 of RHWG REPORT TO WENRA and comprises sufficient information on ageing assessment. However, according to section 07.1.2 of RHWG REPORT TO WENRA, there is no information on the establishment of acceptance criteria related to ageing mechanisms (see item “b” of para 07.1.2 of RHWG REPORT TO WENRA). Corresponding clarifications might be provided as an answer. | expert group 4 | The establishment of acceptance criteria related to ageing mechanisms and ageing related degradation is done based on the standards and guidance documents listed on pages 118-119.
RO-52 |  | Concealed pipework expert group | Romania | 04. Concealed pipework | 80 | Do the BP Program Manual and BP Program cover ageing management of the pipes connections (welds, flanges, bolts, etc)? | expert group 5 | Yes, the BP Program covers also the ageing management of the pipe connections (welds, flanges, bolts, etc). To be noted that for concealed piping, these pipe connections are located inside underground valve pits or inspection pits, which are also included in the BP program scope.
RO-53 |  | Concealed pipework expert group | Romania | 04. Concealed pipework | P 75 | The list of activities involved in the detailed risk ranking process using BPWORKS includes the definition of programme exceptions. Could Romania explain what are those programme exceptions? | expert group 5 | Program exceptions refer to the variables considered for risk-ranking (as part of the BPWORKS software) and which are not applicable or does not exist in the Cernavoda NPP plant. These program exceptions are: - all variables related to concrete / PCCP (Pre-stressed Concrete Pipe); - all variables related to sea water piping; - specific variables related to impressed cathodic protection.
RO-54 |  | Concealed pipework expert group | Romania | 04. Concealed pipework | P 76 | In the description of the weigting factors applied by the BPWORKS software to the consequence of failure, it might be surprising that a failure affecting workers' safety in ranked below a failure causing the temporary loss of power generation. Could Romania justify this ranking? | expert group 5 | This ranking is part of the BPWORKS version 2.2 software, that was used for the prioritisation and it cannot be modified by the user. The justification is that, for the specific case of concealed piping, the risk of failure is greater for lost generation than the risk for workers (except for the case in which the concealed piping is exposed during inspections).
RO-55 |  | Concealed pipework expert group | Romania | 04. Concealed pipework | P 77-78 | The risk ranking summary charts presented in figures 4.3 and 4.4 exhibit very different total numbers of segments depending on NPP unit. There are about 200 segments for unit 1 and two times less for unit 2. Could Romania explain this difference in segmentation? | expert group 5 | The reason that segmentation of Unit 1 BP is almost double than segmentation in Unit 2 is that Unit 1 of Cernavoda NPP, which is 10-years older, includes some systems and related concealed piping that have common functions for both units, but they don’t physically exist in Unit 2.
RO-56 |  | Concealed pipework expert group | Romania | 04. Concealed pipework | P 87 | It is stated that the run-or-repair decision is based on a 'uniform loss' assessment. However, this approach is based on UT measurements which are most likely performed in some small sections of the pipelines. Could Romania specify if a margin is taken into account to include possible occurence of higher degradation in non inspected pipeline sections? | expert group 5 | Possible occurrence of degradation was considered for all concealed piping included in the program scope, by using the risk-ranking process (with BPWORKS software). Then, inspections have been planned and executed with priority on the pipeline sections identified with the higher risk of degradation. Therefore, also the non-inspected pipeline sections have been evaluated and the margin was taken into account from the risk-ranking process itself.
RO-57 |  | Concealed pipework expert group | Romania | 04. Concealed pipework | P 87 | For Group 2, could Romania indicate the ratio of the pipe surface annually monitored by UT to the total pipeline surface? | expert group 5 | 100% to the total accessible (mostly exposed to degradation) pipeline from Group 2 is periodically monitored by UT. For the rest of concealed piping in Group 2, which is concrete-embedded, the associated degradation risk does not justify annual inspections.
RO-58 |  | Concealed pipework expert group | Romania | 04. Concealed pipework | General | As for “concealed pipework” the Romanian report is clear and concise. The ageing management programme for buried pipes which is described seems comprehensive and proportionate to the risks. It includes a serious direct inspection programme for the initial condition assessment as well as for monitoring. It makes large reference to external experience and makes use of external experts for some evaluations. | expert group 5 | Thank you for these comments.
RO-59 |  | Concealed pipework expert group | Romania | 04. Concealed pipework | P 82, 84 | It is stated that account is taken of possible seasonal variation in the soil analyses as well as for cathodic protection system monitoring. This seems to be a good practice. | expert group 5 | Thank you for this comment.
RO-60 |  | Cables expert group | Romania | 03. Electrical cables | 43 | The Philips power and instrumentation cables are said to have the lifetime of 30 years. As the Unit 1 is in operation for 21 years, and was in construction for expended period of time, it is very likely that those cables are already beyond their design life? | expert group 3 | The mentioned period of 30 years of operation is valid from the commissioning of the nuclear unit. Also, the actual operating conditions for these cables are less harsh than the conditions considered in the design when their lifetime was estimated.
RO-61 |  | Cables expert group | Romania | 03. Electrical cables | 45 | What are methods and criteria used for selecting electrical cables within the scope of ageing management? In paragraph 3.3.1 a) there are no information about that. | expert group 3 | Electrical cable selection for aging management is based on the type of cable insulation, the equipment it serves, the area where the cable is located, the degradation mechanisms and the internal and external operating experience. Acceptance criteria established in connection with aging mechanisms are given by the manufacturer, the actual regulations and standards, as a result of the measurements performed and according to EPRI recommendations.
RO-62 |  | Cables expert group | Romania | 03. Electrical cables | 52 | What are established acceptance criteria related to ageing mechanisms? In paragraph 3.1.2 A b) there are no information about any acceptance criteria. | expert group 3 | The acceptance criteria are established in connection with the aging mechanisms (given by the manufacturer), the actual regulations and standards, as a result of the actual measurements performed and according to EPRI recommendations.
RO-63 |  | Cables expert group | Romania | 03. Electrical cables | 53 | Table 3.3 indicates that there is no possibility for replacement of cables that are passing the reactor building penetrations. What would be the solution for those cables when those are not any more serviceable? | expert group 3 | The cables that pass through the reactor building penetrations can be replaced, but it requires a preliminary assessment and it can be done only with the reactor shut down.
RO-64 |  | Cables expert group | Romania | 03. Electrical cables | 56 | Have you been undertaken a systematic thermography of cables to identify " hot spots" , either those caused by ambient conditions or those eventually caused by high current carried by the specific cables? | expert group 3 | Thermographies are routinely performed in accordance with the preventive maintenance program.
RO-65 |  | Cables expert group | Romania | 03. Electrical cables | 56/68 | What are frequencies of actions related to ageing control on electrical cables in the Cernavoda NPP and TRIGA RR? | expert group 3 | At Cernavoda NPP the frequency with which all actions are performed is at each scheduled Plant Outage (that means every 2 years for each unit). At TRIGA Research Reactor, annual inspections of the safety-related cables are performed. During the periodic functional tests of major equipment, (pumps, valves, and switch gears, electric cabinets) the current paths of the cables are also verified.
RO-66 |  | Cables expert group | Romania | 03. Electrical cables | 65 | The programme manual for AMP on electrical cables was issued in 2009, but from the NAR it is not clear whether the inspections and other activities to control the cable commodities are being implemented or as indicated on the page 57 " will be subjected to tests", implying that no test have bene done so far. Could you please clarify what is the status of the implementation of the AMP for cables. | expert group 3 | Tests for cables have been performed on each scheduled Plant Outage. The AMP for cable program is currently under review, which means updating the information and improving the list of tests that will be performed in the future.
RO-67 |  | Cables expert group | Romania | 03. Electrical cables | 65 | Does Cernavoda NPP have any cable deposits for accelerated ageing due to temperature and/or radiation? If not are there arrangements with other CANDU owners to exchange the information on the cable degradation in particular using the deposited cables? | expert group 3 | Cernavoda NPP does not have such testing facilities, but we are considering collaboration with another CANDU nuclear power plant in this regard. Cernavoda NPP is informed on the operating experience of the other CANDU programs through EPRI, COG (CANDU Owners Group), etc.
RO-68 |  | Cables expert group | Romania | 03. Electrical cables | 65 | Have there been any operational events on Cernavoda 1 or 2 due to possible degradation of cables | expert group 3 | Yes, Cernavoda NPP had events due to the degradation of the electrical power cables, but not for safety-related systems; these occurred in the area of the underpasses of the access roads, due to the overheating.
RO-69 |  | General AMP expert group | Romania | 02. Overall Ageing Management Programme requirements and implementation | 24 | Has a dedicated plant programme to manage technological obsolescence been developed and implemented? | expert group 3 on other topics / expert group 1 | Yes, Cernavoda NPP has documented and approved a program for Proactive Obsolescence since 2012 to identify and solve the obsolescence issues using the tools created at plant level for this purpose. Besides of that, since 2012 SNN (the company that owns the plant) has joined at two international databases: Proactive Obsolescence Management System (POMS) and RapidPartSmart, with the benefit of the identification of replacement items for obsolete products. This information is then used by technical responsible engineers in the evaluation of the necessity to replace these parts.
RO-70 |  | General AMP expert group | Romania | 02. Overall Ageing Management Programme requirements and implementation | 28 | Does the plants used risk-informed approach for determine time interval and extent of testing for in-service inspection of mechanical components? | expert group 3 on other topics / expert group 1 | No, as the Canadian Standards which are part of the licensing basis and which are used for mandatory inspections do not accept such an approach. However, for some non-mandatory inspections, there are some software applications which identify the priority for inspection based on the risk: like CHECKWorks for piping Flow Accelerated Corrosion, SNUBWorks for snubbers and BPWorks for Buried Piping.
RO-71 |  | General AMP expert group | Romania | 02. Overall Ageing Management Programme requirements and implementation |  | An important attribute in ageing management is the establishment of acceptance criteria. Are there established criterion that the SSCs shall maintain their intended function during design basis events (incl. severe accident) and at all stages of the lifetime cycle of a nuclear installation (incl. decommissioning))? | expert group 3 on other topics / expert group 1 | These general requirements are included in the national regulations for nuclear installations, on design and on ageing management, respectively. The actual technical criteria to fulfil the mentioned general requirements are specified in industrial standards and in safety analyses and qualification reports that are part of the licensing basis for the nuclear installations. The parameters that are directly linked to the function of SSCs (systems, structures and components) in accident conditions (including severe accidents) are used in safety analyses and generally represent minimum allowable performance standards for those SSCs (the assumptions are generally conservative). The criteria for evaluating ageing-related degradation are chosen as to ensure sufficient margins in relation to the assumptions in the accident analysis.
RO-72 |  | General AMP expert group | Romania | 02. Overall Ageing Management Programme requirements and implementation | 10 | Has a dedicated specific ageing management programmes for elements and ageing mechanisms? | expert group 3 on other topics / expert group 1 | Cernavoda NPP has not developed specific ageing management programs for elements and ageing mechanisms, but the programs developed so far: PM, PLiM, support programs (PdM, EQ, SL, FAC, Periodic Inspection Program, Testing Program, Proactive Obsolescence Program), address all the applicable age related degradation mechanisms. The AMP for the TRIGA Reactor - ICN Pitesti covers all the relevant ageing mechanisms. The program is structured by systems and structures under the scope of the AMP. The program was revised to be in accordance with international practices and experience from other TRIGA Mark II reactors.
RO-73 |  | EC | Romania | 03. Electrical cables | 56 | The section on monitoring, testing, sampling and inspection activities does not respond to the questions in the TRP Technical Specifications. No information is provided on specific activities, frequencies and their acceptance criteria. |  | The methods of tracking the status of the cable system are divided as follows: A) Preventive Maintenance Methods (Electrical Tests, Visual and Tactile Inspection) that are performed with internal resources and addresses the following components: - cables; - connection elements; - protective systems and cable supports. B) Methods for determination of defects and remaining lifetime (Chemical tests, Spectroscopy, Elongation at break, Complex electrical tests) that will be performed with external resources and addresses: - cable insulation; - cable jacket. Following these tracking methods can result in the following actions: a) Component replacement (when degradation is accentuated and proven by tests); b) Component repair (when defects are identified / predictable by common tests); c) Keeping the component in service (when there are no defects and it is demonstrated that the lifetime of the component is large enough to be maintained). The frequency with which all the actions are carried out is at every scheduled Outage (every 2 years for each of the NPP Units). The acceptance criteria are established in national and international standards applicable to the respective electrical cables.
RO-74 |  | EC | Romania | 03. Electrical cables | Generic 42-68 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found. |  | Following the evaluation of the critical and essential components lists at U1 and U2, approximately 4900 cables and related components (connecting elements, support and protection systems) were identified to ensure the operation of these equipment. Of these, 3600 belong to critical nuclear safety equipment, and the rest are critical for production. The electrical cable system was grouped by families according to the following criteria: - the electrical cables have the same voltage level (LV, MV) - the electrical cables have the same type of insulating material - the electrical cables serve equipment installed on the nuclear side (also affected by radiation), or the classical part (non-radiation areas).
RO-75 |  | EC | Romania | 03. Electrical cables | Generic 42-68 | The report doesn't refer to the cable categories defined in the TRP Technical Specifications. |  | The electrical cable (include electrical cable with environmental qualification and instrumentation cables) system was grouped by families according to the following criteria: - the cables have the same voltage level (LV, MV) - the cables have the same type of insulating material - the cables serve equipment installed on the nuclear side (also affected by radiation) or the classical part (non-radiation areas).
RO-76 |  | EC | Romania | 04. Concealed pipework | 69-88 | Cernavoda NPP: The AMP for concealed piping is still in the implementation phase, so no final conclusions can be drawn yet. However, the steps undertaken by the licensee in preparation of the AMP are similar to the ones undertaken by licensees in other European countries, so a promising result can be expected. What is the status of implementation of the AMP on concealed piping and is there already some feedback? |  | Implementation of this AMP is still in progress, but the feedback obtained up to present, after completion of planned inspections, showed no significant age-related issues on the concealed piping.
RO-77 |  | EC | Romania | 07. Concrete containment structures | p119 | The report does not explicitly mention the operating experience from other CANDUs. Please mention whether ageing mechanisms identified in particular in Pickering A (epoxy liner damaged by radiation exposure, shrinkage cracks in reactor building domes, …) and Gentilly 2 (reactor building cracks in reactor building epoxy and concrete) have been checked in Cernavoda and whether they are applicable (see TECDOC-1025 p100). |  | The operating experience from other CANDUs is monitored within COG (CANDU Owners Group) collaboration and specific Working Group where SNN (the company that owns the plant) is participating since 2010.
RO-78 |  | EC | Romania | 07. Concrete containment structures | p120 | The report states that “some of the RB structures (e.g. pre-stressing gallery, Calandria Vault Structure) are not included in the scope of in-service inspections.” Please explain and justify why. |  | It was a mistake in the report. Pre-stressing gallery was inspected every year with a routine. Calandria Vault (civil structure) is included in Reactor Building PLiM Program scope and is inspected every outage (when the reactor is shut down).
RO-79 |  | EC | Romania | 07. Concrete containment structures | p120 | Please provide details about the containment leak rate tests performed periodically. Does it include integral containment leak test and penetration tests? What is the precise content (pressure applied vs pressure expected during accidents, periodicity, …)? |  | CANDU building pressure test is an Integrated Leak Rate Test (ILRT) only. CANDU design does not have provision for any penetration individual testing. However, individual leak testing is feasible and is periodically performed (as mandatory or post-maintenance) for: all pipe lines on which containment isolation valve pairs are installed, airlocks, spent fuel transfer door seals interspace, spent fuel transfer ball valves. CANDU reactor building leak rate test (RBLRT) consists of an ILRT performed at 124 kPa(g), which is the maximum peak pressure considered in conservative safety analyses for the design basis postulated accident scenarios. The standard CSA 287.7 is part of the licensing basis for the plant and contains in-service examination and testing requirements for concrete containment structures for CANDU nuclear power plants, specifies uniform requirements whereby, through systematic and periodic examination, the structural and leak-tight integrity of concrete containment structures can be assessed as demonstrated by achieving the specified requirements, including the operational leakage rate target. This standard describes details on how leak rate is calculated. Periodicity is at least once at every 6 years, imposed by regulator; depending on performance, shorter interval between too consecutive tests may be agreed with the regulator
RO-80 |  | EC | Romania | 07. Concrete containment structures | p122 | The report mentions the licensee experience related to buildings and structures at Cernavoda unit 1 only. What is the licensee experience for the reactor building of Cernavoda unit 2? |  | The Life Assessment report for Unit 1 was issued and approved by Cernavoda NPP in 2017 and for Unit 2 will be ready this year (2018).
RO-81 |  | EC | Romania | 07. Concrete containment structures | p122 | The report mentions life assessment studies recently performed namely for Cernavoda units 1 and 2 containment structures. What are the main recommendations from these studies for the containment structures of both units? |  | Based on the reviewed information, the reactor building structures are expected to continue meeting their intended functional requirements for the period of 30 years initially considered for operation and also for an extended period of another 30 years, provided that ageing management activities are implemented as planned. The recommendations in the life assessment study concerned mainly additional monitoring and inspection activities to ensure that the ageing-related degradation is minimized for all containment structures important to safety.
RO-82 |  | EC | Romania | 07. Concrete containment structures | p4 p114 | 1. What is the design lifetime of the major life-limiting components and structures of Cernavoda NPP? 2. What is in particular the design lifetime of the liners applied on the containment structure to enhance leak-tightness? |  | The reactor building structures are expected to continue meeting their intended functional requirements for the operational life initially planned, of 30 years, and also for an extended life (of additional 30 years), provided that ageing management activities are implemented as planned. The liners are epoxy and polyurethane liners (NORMAC). They are qualified to maintain their function in the harshest boundary conditions and have been tested for conditions that involve radiation levels accumulated from 100 years of normal operation + radiation levels resulting from a Large Loss of Coolant Accident with loss of Emergency Core Cooling. The liners are inspected periodically and repairs are made if any degradation is observed.
RO-83 |  | EC | Romania | 07. Concrete containment structures | p112 p122 | The construction of the Cernavoda Units 1 and 2 mainly took place in the 1980s, however the completion of the construction has been at times significantly stalled and delayed. Unit 1 was commissioned in 1996 and unit 2 only in 2007. 1. Record-keeping of relevant environmental conditions is essential for an AMP. What environmental parameters have been monitored and recorded during the long period when the construction was stopped or delayed, especially for Cernavoda unit 2? 2. In which year were the tendons protected against corrosion using cement grout? During the initial construction period or during the completion period? Did this led to any tendon corrosion? 3. What has been the effect of the long period when the construction was stalled / delayed on the overall ageing of the reactor building structure of Cernavoda unit 2 (freeze-thaw cycles, exposition to moisture, possible rebar corrosion, degradation of exposed anchor bolts, …). 4. How will this period impact the overall lifetime of the reactor building? |  | U1 Life Assessment report is based also on this information. 1. Before 1996, the main / most relevant loads for U1 Reactor Building were not present because the reactor was not in operation (e.g. high temperature, radiation, equipment), but late commissioning was taken into account for both U1 and U2 in the Life Assessment studies. The design manuals for the reactor containment buildings specify the acceptable range of external environmental conditions and these have not been exceeded. 2. The tendons were introduced in stages, in different years, both during the initial construction period and during the completion period, in pipes/tubing, as the construction progressed. In accordance with the pre-tensioning and post-tensioning sequences, the tendons have been grouted immediately after they have been introduced in pipes/tubing and tensioned. There haven’t been any tendons left ungrouted, so there was reason for corrosion (this is actually why there is a specific requirement to grout the tendons immediately, in a few hours, after tensioning). 3. & 4. A life assessment study for the reactor building of Unit 2 is under preparation, to be finalized in 2018 and it will offer detailed information on the status of the containment and on the effects of the deferred construction on the overall lifetime of the reactor building. However, as regards the overall performance of the reactor containment building, this has been tested both during commissioning (by pressure proof test done at a pressure not less than 1.15 times the positive design basis pressure and by leak rate test at design basis pressure) and during operation (by leak rate tests at design basis pressure) in order to demonstrate compliance with the regulations, standards, design basis requirements and safety analysis assumptions.
RO-84 |  | EC | Romania | 07. Concrete containment structures | p116 | The report states that the floor of the pre-stressing gallery is at elevation 89.10m while the ground water elevation is around 90.84m. Has this led to any concrete degradation? Has this lead to water infiltration inside the gallery in unit 1 or 2? How is this monitored through the inspection programme? |  | Inside pre-stressing gallery there are no signs of important concrete degradation. Near the perimetral wall there is a peripheral drain. The water is collected in a pit and is sent outside the reactor building.
RO-85 |  | EC | Romania | 07. Concrete containment structures | p121 | What is the acceptance criterion for cracks and other defects in the reactor building envelope? When are cracks and other defects repaired, and when are they assessed to be acceptable? |  | According to the design Manual, on the internal surface of the reactor building it is not possible for cracks to appear in normal operation time, as it is protected by the pre-stressing system. Usually, repairs to containment surface are performed (with injection material), when the leaking is identified (RBLRT). Also the finishing coatings can be repaired.
RO-86 |  | EC | Romania | 07. Concrete containment structures | p124 | Please precise the detailed content of the inspection programme and associated periodicity related to the concrete containment of the Triga research reactor (inspection programme, existing instrumentation, leak rate tests, …). |  | The TRIGA research reactor does not have a concrete pressure-proof “containment” system. The reactor is placed in a concrete building which, by provisions of isolations, and ventilation, and exhaust systems, constitute a barrier against potential radioactive releases. The inspection programs of these systems is in the framework of the maintenance and repair programme of the research reactor, and includes: periodic maintenance, ventilation tests and preventive maintenance, repairs and corrective maintenance. The instrumentation of the reactor building, related to radiation monitoring is included in the radiation and effluents monitoring systems of the reactor, and also HVAC systems, which are tested semi-annually.
UA-1 | 1 | Poland | Ukraine | 01. General information | p.20, 114 | 1. Does the SNRIU have permanent (on-line) access to AMIAS? 2. Is independent external assessment of ageing management activities carried out only by the SNRIU or also by other external entity? |  | 1. SNRIU has no permanent on-line access to AMIAS. All needed information from this database may be sent by the operator to SNRIU upon corresponding request. 2. Every year the operator sends to SNRIU Reports on implementation of the ageing management program. SNRIU evaluates these Reports by its own staff or involve TSO for evaluation.
UA-2 | 2 | Bulgaria | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | p.15-16 | All Ukrainian units are Russian design. In the list of the international standards there is not a single Russian document. Ukraine doesn’t use at all the Russian standards or they are incorporated in the national legislation? Please clarify. |  | Step by step Ukraine develops and implements national regulatory and normative documents. These documents, as a rule, are based on IAEA and WENRA recommendations and best international practice and experience. At the same time, several documents from the former USSR are still used, these are PNAE G-7-002-86, PNAE G-7-008-89 etc. These documents are listed in the NAR “References” section.
UA-3 | 3 | United Kingdom | Ukraine | 05. Reactor Pressure Vessels | 87 | Section 5.4 – Paragraph 6 mentions the integrated program of testing surveillance samples (Ref. 79 in the report). The report notes that there has been difficulty with compliance with the conditions set within the programme? Please provide further details of the programme and the difficulties that have been experienced. |  | Upon agreement with SNRIU, the operator: a) improves methodologies used to justify safe operation of the reactor pressure vessel in the long-term operation period for: · calculations of neutron fluence, thermal hydraulic parameters (pressurized thermal shock); · strength calculations to decrease the size of the postulated cracks for brittle fracture resistance calculations (taking into account VERLIFE-2008) in the Methodology for Strength Assessment of VVER Reactor Pressure Vessels in Operation, MT-D.0.03.391-09; b) has prepared, upon practical approval results, the new operator standard “Methodology for Determining Radiation Embrittlement of Reactor Pressure Vessel Metal upon Testing of Surveillance Specimens”.
UA-4 | 4 | United Kingdom | Ukraine | 05. Reactor Pressure Vessels | General | General – RNPP unit 1 has experienced significant strain ageing. Is there any experience of have there been any other significant ageing mechanisms on other NPPs? |  | The gained experience has not shown any significant ageing mechanisms. Annealing of reactor pressure vessels has not been done or predicted for other NPP units.
UA-5 | 5 | United Kingdom | Ukraine | 05. Reactor Pressure Vessels | General | General – I have not seen any discussion on hydrogen flaking following the Doel/Tihange discovery. Has this been issue been addressed by the NPP operators across Ukraine? Have any additional inspections been performed? |  | The question should be specified regarding the understanding of the Doel/Tihange discovery. The experience in operation and safety regulation has not revealed any metal hydrogenation issues.
UA-6 | 6 | United Kingdom | Ukraine | 07. Concrete containment structures | 92 | "06.1.2 Ageing assessment for 07. Concrete containment structures. This section includes an interesting discussion on ""heeling"" and settlement of the ZNPP-1 and ZNPP-3 reactor building compartments. Please confirm that the term ""heeling"" is equivalent to an uneven tilting effect on the building foundation. Please can more information be provided on the (i) supporting ground conditions (ii) bearing pressures (iii) extent of the measured tilt and (iv) acceptance criteria. " |  | The “heeling” means deviation from vertical position. According to PiN AE-5.6, the heeling of category I structures under uneven tilting on foundation must not exceed 1/1000. When extreme events are considered, the allowed heeling must not be larger than 3/1000. The reactor compartment heeling is monitored on a permanent basis by an automatic position control system and checked twice a year by geodetic measurements.
UA-7 | 7 | Finland | Ukraine | 04. Concealed pipework | 61 | What are the corresponding safety and operation challenges, like maintaining safe shutdown condition, flooding risks, etc. connected to AMP? |  | The activities on TCA of ESWS underground piping show that the following may be referred to the main ageing management measures: - restore anticorrosion coating of piping in accessible places and places of NDI; - perform diagnostics of ESWS piping sections with low-level anomalies to detect changes in its condition by contactless methods. These measures are included into unit-specific AMP and their adequacy is confirmed by operating experience and practice
UA-8 | 8 | Czech Republic | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 18 | Can you please give some examples of systems/components that fall into the selection for ageing management according to the requiremet of NP 306.2.210-2017 according the 2) bullet |  | The examples are provided in para. 02.3.1.3 of NAR
UA-9 | 9 | Czech Republic | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 19 | Does the SNRIU approve the complete list of components selected for ageing management? And why the list of components subjected to ageing managment may be revised not more than once a year - what this limitation results from? |  | SNRIU approves the list of components subject to ageing management within the AMP for a power unit. This list may be revised upon SNRIU’s evaluation of the operator’s annual report on implementation of ageing management measures (regarding periodic revision of AMP, see para. 0.2.3).
UA-10 | 10 | Czech Republic | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 18 | What does it mean exactly the thermal mechanical equipment and piping - is it possible to define it by temperature/pressure? |  | These are equipment and piping of the plant thermal design covered by requirements of PNAE G-7-008-89, according to which pressures and temperatures are indicated in the respective documents for each piece of equipment and piping.
UA-11 | 11 | Czech Republic | Ukraine | 01. General information | all chapters | According to IAEA research reactors database the research reactor WWR-M KIEV is still in operation. Because of its 10 MWt output, it should be within the scope of TPR. But maybe this database is not actuall. Could you please give me some clarification ? |  | The research reactor WWR-M KIEV is still in operation until 2023 according to the license granted by the regulatory body based on results of Periodic Safety Review. Information on WWR-M is presented in Section 07 of NAR
UA-12 | 12 | Switzerland | Ukraine | 03. Electrical cables | 39 | Textline 20: Why may replaceable cables be excluded from the database? Isn’t it a contradiction to the afore mentioned “cables whose lifetime expires prior to unit LTO expiration” (Textline18)? |  | If a cable is replaced, the status of this cable changes from “operation” to “withdrawn from service” (in the Ukrainian Reliability Database for NPP Equipment). The new cable that replaced the previous one is entered into the database. There is no contradiction to the above-mentioned.
UA-13 | 13 | Switzerland | Ukraine | 05. Reactor Pressure Vessels | 139 | Fatigue management (SP3): Is the influence of environmental effects (FEN-factors) taken into account? |  | The influence of environmental effects under the containment for VVER-1000/320, 302, 338 (local containment building for VVER-440/213 reactor) is taken into account in strength calculations in compliance with PNAE G-7-002-87 and PNAE G-5-006-87 and in measures on equipment qualification.
UA-14 | 14 | Czech Republic | Ukraine | 03. Electrical cables | 37 - 51 | There is any information about WWR-M research reactor included in the report. Could you please provide us some information on how the ageing management for electrical cables of this research reactor is conducted? |  | Ageing management of the reactor cables is described in para. 07.3.3 of NAR. In general, ageing management includes monitoring and technical condition assessment of cables. The electrical cables of the reactor were replaced with new ones (para. 07.3.1 of NAR), which have fire-retardant electrical insulation. The lifetime of the new cables is 25-30 years.
UA-15 | 15 | Czech Republic | Ukraine | 03. Electrical cables | 38 - 40 | Is the technical status of power and control equipment cables that belongs to safety and safety related systems exposed to the mild enviroment (not exposed to conditions of DBA) verified? Are the electrical and mechanical properties measured on such cables to verify the residual lifetime? |  | The technical status is verified for all cables. The electrical and mechanical properties are measured in accordance with developed inspection programs.
UA-16 | 16 | Czech Republic | Ukraine | 03. Electrical cables | 38 - 40 | Is the technical status of safety systems cables, which are not included in the List of Representative Cables somehow verified? Are the electrical and mechanical properties measured on such cables to verify the residual lifetime? |  | The technical status is verified. Measurements are performed and respective conclusions are made on the residual lifetime.
UA-17 | 17 | Czech Republic | Ukraine | 03. Electrical cables | 39 | The report states: It is allowed not to include cables whose replacement is economically and technologically possible and advisable before expiration of their lifetime into the List of Representative Cables. Is the measurement of electrical and mechanical properties for the determination of the residual life of the cables carried out on such cables before the end of their service life? |  | Yes, measurements are performed.
UA-18 | 18 | Czech Republic | Ukraine | 03. Electrical cables | 40 | The report states: If cables were produced by different manufacturers but in compliance with the same TS (GOST), it is allowed to combine cables into one group. Do you perform some verification of the electrical and mechanical properties for cables made by different manufacturers? |  | The cables are verified for compliance with the selected reference sample in laboratory conditions (by a specialized organization).
UA-19 | 19 | Czech Republic | Ukraine | 03. Electrical cables | 37 - 51 | How is ageing management of termination arrangements conducted on NPPs? |  | It is conducted in compliance with the plant ageing management programs for cables
UA-20 | 20 | Finland | Ukraine | 05. Reactor Pressure Vessels | Chapter 5.4 | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? |  | In-service nondestructive inspection of the base metal, welds, and claddings of reactor components (pressure vessel) performed in compliance with TPPK-13 (for VVER-1000) and AIEU-10-09 (for VVER-440) has not revealed any special issues. According to assessments of European experts, the scope of nondestructive inspection is the same as at similar European power units of Soviet design. The calculations performed to determine the residual lifetime of equipment and piping take into account the accumulated loading cycles, whose number is indicated in the Technical Specifications for Safe Operation, and the number of cycles for the period of beyond-design-basis operation (long-term operation) is recalculated in compliance with the Methodology for Recalculating the Allowed Number of Loading Cycles and Technical Condition Assessment Based on Strength of Thermal Mechanical Equipment and Piping under Cyclic Loads, which is agreed by SNRIU.
UA-21 | 21 | Belgium | Ukraine | 05. Reactor Pressure Vessels | 80 | Several inspections are prescribed, and it would be interresting to have more details about the scope of each of them. Which parts of the vessel are inspected (base metal, welds, HAZ) by these diffferent techniques, and from which side are these different |  | The types, scopes and areas for in-service nondestructive inspection of base metal, welds, and claddings of reactor components (pressure vessel) are determined in TPPK-13 (for VVER-1000) and AIEU-10-09 (for VVER-440) and are the same as for European power units of Soviet design, according to assessments of European experts.
UA-22 | 22 | Belgium | Ukraine | 05. Reactor Pressure Vessels | 83 | What is considered as a major repair of the power unit, and have such repairs already been carried out? |  | According to SOU NAEK 033:2015, “a major repair is a repair that is carried out to restore the serviceability and recover the service life of an item fully or almost fully by replacement and recovery of its any parts, including the main ones”. According to practices in the Soviet period, a major repair is carried out once every four years at a power unit since the commencement of its operation.
UA-23 | 23 | Belgium | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 18 | According to the Figure 2,3 it seems that only important to safety SSCs (class 1, 2 and 3) are included in the scope of the ageing management program. Is it true or does the Ukrainian licensee include also non-nuclear safety SSCs (for example, whose failure may impact safety SSCs) in their ageing management program? |  | Regarding non-nuclear structures, systems, and components (that belong to class 4 according to NP 306.2.141-2008) that are included into the scope of the ageing management program, see para. 02.3.1.3.
UA-24 | 24 | Belgium | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 20 | Which company is the supplier/developer of the AMIAS software mentioned and illustrated in the Figure 2.4 of §02.3.1.5? |  | The national supplier of services for Energoatom (Proatom Company) is the developer of the Ageing Management Information Analysis System (AMIAS) software.
UA-25 | 25 | Belgium | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 26 | Which software is used to perform the elastoplastic calculations mentioned in item 4) of the §02.3.2.5? |  | The calculations are performed with the computer codes included in the List of Computer Codes Allowed for Use at Energoatom Company to Justify Safety of Nuclear Facilities in compliance with Enterprise Standard STP 0.41.076-2008 “Procedure for Use of Computer Codes to Justify Safety of Nuclear Facilities” (with SNRIU participation).
UA-26 | 26 | Belgium | Ukraine | 03. Electrical cables | 37 | Are there burried cables important for safety? If yes, how is the ageing of these cables assessed and managed? |  | According to regulatory documents, cables are not allowed to be buried directly in soil. At nuclear power plants, cables of safety systems are laid in cable structures (special cable ducts, etc.)
UA-27 | 27 | Belgium | Ukraine | 03. Electrical cables | 39 | Based on the table 3.2 it seems that the humidity level of the cable's environment is not recorded in the "List of representative cables". Is the presence of moisture systematically monitored and recorded in the cable database? |  | The humidity is not monitored since it is not a substantial external factor in accordance with the ageing management program for cables.
UA-28 | 28 | Belgium | Ukraine | 03. Electrical cables | 44 | It is mentioned "the regular monitoring is performed only in hot spots identified upon the initial monitoring for each type of operated cable on a regular basis until the power unit is decommissioned." Wat is the frequency of the regular monitorings? |  | 1) The rooms where temperature sources are present are monitored on a permanent basis; 2) The rooms where temperature sources are absent are monitored by personnel of respective departments according to schedules (twice a month in the strict access areas of categories 2, 3 and once per year during scheduled outage in the strict access area of category 1), and the monitoring results are entered into respective logbooks.
UA-29 | 29 | Belgium | Ukraine | 07. Concrete containment structures | 94 | What are the acceptance criteria related to the ageing mechanisms listed? |  | The criteria are established in compliance with regulatory document DBN В.2.6-98:2009 “Structures of Buildings and Facilities. Concrete and Reinforced Concrete Structures. General Provisions”.
UA-30 | 30 | Belgium | Ukraine | 07. Concrete containment structures | 94 | Can one example of R&D programmes concerning ageing degradations mechanisms be given? |  | Selection of concrete samples to examine mechanical properties
UA-31 | 31 | Belgium | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 16 | "...which is periodically revised to incorporate updated international recommendations and standards,". Can you precise the maximal period allowed between two updates of this document? |  | The operator revises AMP upon results of effectiveness assessment, but the period between the revisions must not be longer than periodic safety review of the power unit.
UA-32 | 32 | Belgium | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 17 | Could you precise if there is a screening between passive and active components when identifying the components within the overall AMP? Is the AMP apply to both passive and active SSCs? Are those two types of components treated with the same process? |  | Yes, these two types of components are described by the same ageing management process.
UA-33 | 33 | Belgium | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 24 | Can you elaborate on the process for identifying for each group of SSCs the potentially applicable degradation mechanisms? |  | The identification of degradation mechanisms is based on the detection and evaluation of ageing effects for each component and structure. Ageing effects are detected through: - testing and inspections, - acceptance and in-service inspections; - technical examinations; - detection of leaks, vibration monitoring; - assessment of functionality/operability.
UA-34 | 34 | Belgium | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 24 | "In case of change or unforeseen deviations of operational parameters or identification of new degradation mechanisms, NPP AMP is amended." Could you precise at which frequency the various items used for defining the applicable degradation mechanisms are checked and the NPP AMP is amended? |  | The ageing management programs are amended when deviations are revealed or new degradation mechanisms are identified. Notifications of the amendments are prepared and agreed with SNRIU.
UA-35 | 35 | Germany | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 17 | In Chapter 02.3.1.1 the distribution of responsibilities of the licensee tregarding the overall AMP is explained. However, no design authority as per INSAG-19 is mentioned. Who is fulfilling this role in Ukraine and how this istitution is involved in AMP? |  | Chapter 02.3.1.1 indicates the main department of the licensee’s organization dealing with ageing management issues. In Standard AMP PM-D.0.03.222-14, respective NPP departments deal with these issues (such as workshops that operate specific systems, structures and components, maintenance divisions, etc.), which are specifically indicated in unit-specific AMPs. For economic reasons and with development of the service market, the role of design authorities (as former general designers) for operating NPPs decreased compared to the role of specialized organizations.
UA-36 | 36 | Germany | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 28 | Chapter 02.3.3.2 mentions the inspection on implementation of PSR. Are the 15 operational NPP units all having their individual PSR by now, or before the license on LTO is granted? |  | Upon PSR results, the lifetime of seven power units was extended (see Chapter 01.1) and new licenses (for LTO) were granted for these units. PSR in the design-basis period is carried out for Khmelnitsky-2 and Rivne-4 in compliance with the current licenses. PSR within the 20-year LTO is carried out for Rivne NPP units 1 and 2 in compliance with the new LTO licenses.
UA-37 | 37 | Germany | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 32 | In chapter 02.4.2 is mentioned that "SNRIU conducts two comprehensive inspections in power unit preparation for LTO upon completion of the design-basis life. The first inspection is conducted six to eight months before the power unit starts LTO". Can Ukraine explain in more detail what is meant by "start of LTO"? |  | It is considered that design lifetime of Ukrainian NPPs is 30 years. Operation beyond this term is called Long-Term Operation and can be provided only based on results of Periodic Safety Review (PSR) that defines the next period of operation. PSR is conducted every 10 years (or earlier upon request of the regulator or under license conditions). The start of long-term operation means the planned time by which a new license for power unit operation (operation at full power) is to be granted in the period beyond the original design-basis service life.
UA-38 | 38 | Germany | Ukraine | 03. Electrical cables | 37 | Chapter 03.1.1 is pointing on scope of cables under surveillance; followed by results in chapter 03.2. As the functionality of cables is depending very much on interconnections between cable sections, information is missing on classification, selection, testing and results for the connecting elements, e.g. connectors/boxes/terminals. |  | The cable ageing management program is intended to manage the ageing of cables and does not include information on connecting elements. The assessment of cable elements is provided in PM-T.0.03.338-14 "Program for Examination of Technical Condition. Lifetime Extension. Cable Elements of NPP Units".
UA-39 | 39 | Germany | Ukraine | 03. Electrical cables | 44 | Chapter 03.1.3 descibes monitoring, testing, etc. activities for electrical cables. However, there is no reference regarding cables or cable group covered with fire protection coating. Is there any information available on how cables with fire protection |  | These cables were examined in detail in the primary monitoring by a specialized organization. Temperature in the rooms where these cables are located is monitored on a permanent basis.
UA-40 | 40 | Germany | Ukraine | 04. Concealed pipework | 52 | The AMP for concealed pipework as described in chapter 04.1.1 does not include piping inside buildings and channels. These pipes appear to be addressed only by walkdowns. As neither the outside nor the inside surface condition can be assessed by walkdowns, how will the degradation of this piping be determined? |  | This piping undergoes technical examinations. Regarding piping for cooling of group A loads (underground part), the soil surface above the piping is inspected twice a year by a commission to determine whether water leakage is possible if the piping is substantially damaged.
UA-41 | 41 | Germany | Ukraine | 05. Reactor Pressure Vessels | 70 | In table 05.3, it is mentioned that "Accumulated fatigue damageability of safety system components does not exceed the allowable value specified in PNAE G-7-002-87 and is equal to 1." This seems to be a typing error, as this factor must be lower than 1. |  | We thank you for the comment and agree with the specification that this factor must be lower than 1.
UA-42 | 42 | Germany | Ukraine | 05. Reactor Pressure Vessels | 87 | The report does not provide any information on the fatigue usage factor accumulated up to date. Is there any information available about it? |  | The meaning of the “fatigue usage factor” needs to be clarified, which is not indicated on page 87 of NAR. Information on the performance indicators used to assess ageing management effectiveness is provided on page 22 of NAR.
UA-43 | 43 | Germany | Ukraine | 07. Concrete containment structures | 92 | Chapter 06.1.2 reports about monitoring of the settlement and heeling process for ZNPP site. How is the state of these phenomena at the other Ukrainian sites, especially at RNPP1&2, the first site with WWER440-V213? |  | At RNPP-1&2, the settlement and heeling of the reactor compartments do not exceed the regulated values (PiN AE 5.6). At the beginning of operation, measures were taken to reinforce the ground basis under the main buildings of RNPP units 1 and 2. A program was developed and is in operation to monitor the ground basis on the RNPP site. Respective reports are submitted to SNRIU.
UA-44 | 44 | Germany | Ukraine | 07. Concrete containment structures | 94 | Table 6.1, point 12 and table 6.2, point 6 addresses pipe penetrations only. However, the cable penetrations are for safety functions very crucial, and their functionality is influenced by the interface between cable, cable isolation, tightening material and metal of the penetration; all of which may age. Is there any information available on assessment of electrical penetrations? |  | All types of penetrations are assessed for integrity and tightening. (The electrical penetrations are assessed under an individual program)
UA-45 | 45 | Netherlands | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 02.03.2002 | Does Ukraine make use of IRS/IRSRR (IAEA) and CODAP (NEA)? |  | SNRIU and SSTC NRS use IRS information in analyzing the reports on investigation of operational events at Ukrainian NPPs to analyze the level of their consideration during the investigation of the international experience and the need for developing additional corrective measures. In addition, SSTC NRS performs the following during the event process analysis: - review of events submitted to IRS, the information on which can be used to improve safety at Ukrainian NPPs. Analysis of events at NPPs with similar reactor types and equipment, events resulted from administrative drawbacks, events related to external hazards, and general safety issues; - review of special investigations of specific challenges whose results were presented in IRS system. SSTC NRS experts perform similar investigation of national experience (using similar criteria and methodologies) based on the results of such review, if the subject of investigation is urgent for Ukrainian NPPs. Thus, the analysis of events initiated at Ukrainian NPPs resulting from failures and/or incorrect functioning of the information computer system and electrical and technical equipment, etc. was performed. Based on the review results of IRS system information, the recommendations are developed for: - SNRIU to make regulatory decisions and perform appropriate inspections of revealed challenges; - Energoatom to develop preventive corrective measures to prevent initiation of events.
UA-46 | 46 | Netherlands | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 2.4 | Internal NPP self-assessments and SNRIU inspections seem to form the source of updates of the NPP AMP. What about evaluation of company-level AMP? Is there a system of company-internal peer review (teams of company and plant experts)? |  | All ageing management programs developed by NPPs are reviewed and agreed by the operator company experts.
UA-47 | 47 | Netherlands | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 2.4 | Has Ukraine invited external reviews of AMP (as suggested by 02.5)? What were the main findings that had to be implemented? Have they been implemented? |  | External reviews of AMP by European experts have not been conducted. Ukraine takes an active part in the IAEA IGALL project, in which it shares its experience in ageing management of components and structures.
UA-48 | 48 | Netherlands | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 07.2.2 | It is unclear if the NRR has overall AMP and also AMPs for systems and/or components. Please explain. |  | See paras. 02.3.1.1, 02.3.1.4, 03.1.
UA-49 | 49 | Netherlands | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 07.2.3 | Operating experience with similar NRR in Russian Federation is exchanged. Is it also considered to exchange such experience with other countries having NRR? |  | The Kyiv VVR-M NRR was constructed using the same design drawing as for the VVR-M NRR located in the town of Gatchyna (Leningrad region, Russian Federation). For this reason, operating experience of the Russian NRR is most often used to analyze ageing of equipment and systems of the Kyiv NRR. There are no other full analogues to the Kyiv NRR.
UA-50 | 50 | Netherlands | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 07.2.7 | Which external review took place and when? What were the main findings that were implemented? |  | The last external independent review was carried out by SSTC NRS upon SNRIU request in 2013.
UA-51 | 51 | Netherlands | Ukraine | 03. Electrical cables | 3.1.2 / p.43 | Why are there no regular TCA activities regardless of how close the cables are to their lifetime expiration (e.g. this would allow to detect unexpected degradation)? The statement of TCA activities starting 3 years before lifetime expiration does not really match with Fig.3.1 which seems to suggest continuous monitoring of cable conditions. |  | TCA of cables begins two to three years before their lifetime expires. Continuous monitoring of cable operating conditions allows any deterioration to be detected in good time. The monitoring is conducted independently of TCA.
UA-52 | 52 | Netherlands | Ukraine | 03. Electrical cables | 3.1.2 / p.43 | Do the results of the accelerated lab-tests match with historic TCAs of the cables at the NPPs? |  | Laboratory tests are intended to demonstrate that the characteristics of cables comply with requirements of technical specifications.
UA-53 | 53 | Netherlands | Ukraine | 03. Electrical cables | 3.1.2 / p.43 | For the cables that show unsatisfactory results after accelerated ageing in the lab: was this result expected for these ageing phenomena for these cables? Furthermore, is the procedure to replace the counterparts of these cables at the NPPs implemented in and prescribed by the CAMPU? |  | Unsatisfactory results of laboratory tests are not expected since, in this case, it is economically reasonable to immediately replace such cables
UA-54 | 54 | Netherlands | Ukraine | 04. Concealed pipework | Table 4.1, Table 4.2, p.55 | Could you please check table 4.1 and 4.2? There might be a confusion between ageing/degradation mechanisms and ageing effects. |  | Other peer reviewers have not raised such question.
UA-55 | 55 | Netherlands | Ukraine | 04. Concealed pipework | p.52 | Is our understanding correct in the sense that pipes are grouped by their nominal diameter? Could you please motivate this criterion for the grouping? |  | The nominal diameter is the criterion for grouping of pipes for monitoring, taking into account that these piping groups are operated in the same conditions (low pressure, temperature, and quality of cooling water), are made of the same material and have not reached the established number of cycles.
UA-56 | 56 | Netherlands | Ukraine | 04. Concealed pipework | '4.1.2, p.56 | What are the acceptance criteria for the ageing mechanisms that require management?
UA-57 | 57 | Netherlands | Ukraine | 04. Concealed pipework | '04.3, p.60 | It is mentioned that “monitoring of technical conditions of NPP underground piping is performed on a regular bases”. What are the frequencies for the monitoring and testing activities? |  | Underground piping is monitored once a year by contactless technique (acoustic diagnosis), and the groundwater level is monitored once a month.
UA-58 | 58 | Netherlands | Ukraine | 04. Concealed pipework | '4.2, p.60 | Could you please specify in more detail your operational experience for concealed pipework? What are the main trends/results of the contactless monitoring/diagnostics of underground piping? |  | Areas where loads are concentrated and areas with leaks are identified. The identified areas are assessed on a hazard scale and are subject to additional monitoring or elimination of defects.
UA-59 | 59 | Netherlands | Ukraine | 04. Concealed pipework | '4.1.4, p.60 | Since most pipework is not accessible for examination, how would measures for restoration of the anticorrosion coating be conducted? |  | The anticorrosion coating is restored only in places where the pipework is accessible after removal of the previous coating for condition monitoring.
UA-60 | 60 | RPV expert group | Ukraine | 05. Reactor Pressure Vessels | 62-88 | The report gives information on the annealing of weld 4 which has been performed at RNPP-1 RPV. What was the decision making process used for ensuring that this was sufficient and other welds/plants were not required. |  | Para. 05.1.4.2 of NAR indicates that recovery annealing was carried out for weld 4 of RNPP-1 on the basis of relevant calculational justifications that confirmed the need for this measure.
UA-61 | 61 | RPV expert group | Ukraine | 05. Reactor Pressure Vessels | 75-76 | The irradiation embrittlement samples are stated to be located above the core on the internal baffle in section 5.1.2.3, but stated to be on the inner wall of the core barrel between the baffle and upper internals. Could you please clarify this position please? |  | The place where the containers with irradiation specimens are located is described in section 05.1.3.1 and is the same as in European reactors of Soviet design. In VVER-1000 reactors of the Ukrainian NPPs, irradiation specimens are located above the core as required by design documentation – on the internals baffle. According to the world practice, irradiation of the surveillance specimens located in containers on the RPV wall mostly corresponds to irradiation conditions on the VVER-1000 RPV wall in the beltline region. This condition was implemented in the Integrated Surveillance Program at Czech Temelin NPP – see para. 05.1.2.3.
UA-62 | 62 | RPV expert group | Ukraine | 05. Reactor Pressure Vessels | 66-72 | A number of components/areas in tables 5.2 and 5.3 have corrective measures “Repair or replacement”. Have these repair/replacement methodologies been outlined, or are they at a theoretical level only at present? |  | As a corrective repair measure, the sealing surfaces were subjected to recovery/finishing at individual NPP units.
UA-63 | 63 | RPV expert group | Ukraine | 05. Reactor Pressure Vessels | 75-76 | I understand from the documentation presented that the boundaries of the aging management are fundamentally informed by the design code. What is the strategy for dealing with threats to the Safety Case that are outside of the design code? |  | The operator follows the policy of continuous monitoring and analysis of NPP safety through continuous safety improvement considering national and international experience, recommendations of specialized international organizations, and research and engineering results and developments and in line with fundamental and general organizational and technical principles for NPP safety assurance, in particular, safety culture and defense-in-depth strategy. Ageing management of a specific component or structure is organized by the operator as follows: detection of degradation mechanism – identification of ageing effect – location of ageing effect on component or structure – tools and methods to inspect degradation – analysis of inspection results – degradation mitigation measures – effectiveness analysis of ageing management program.
UA-64 | 64 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 89 | 6.1.1 The description of building structures in the reactor compartment of VVER-1000/320, 302, 338 and VVER-440/213 is presented in Annexes D, E, F. Could the Licensee describe the corrosion protection of the pre-stressing tendons of the containments (grease or other) and the corresponding construction arrangements ? 6.1.1 |  | Corrosion-preventive grease is used for corrosion protection of pre-stressing tendons in accordance with GOST 19537-83. The grease layer on tendon wires must be continuous, not less than 5 mm in thickness. The anchoring parts must also be covered with a continuous grease layer. The gaps between the wires and the anchorage sleeve must be sealed. When a tendon is replaced, it is recommended that the wires near the anchorage areas, 10–15 m long, be additionally coated with grease.
UA-65 | 65 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 89 | 6.1.1 The description of building structures in the reactor compartment of VVER-1000/320, 302, 338 and VVER-440/213 is presented in Annexes D, E, F. Could the Licensee describe the monitoring system of the containments (for instance embedded strain gauges, topographic marks...) and the role of that system in the AMP? |  | All jacking anchorages of the containment pre-stressing tendons at VVER-1000 units are provided with gauges of the remote tension monitoring system.
UA-66 | 66 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 93 | 6.1.2 Is the project “Creating a System of Monitoring Technical Condition of NPP Buildings and Structures Based on Modern Methods and Technologies” already finished ? What are the main modifications (extra or modified monitoring for instance) to AMP provided by that project ? |  | The project results were taken into account in adopted operator standards, which are indicated in NRA.
UA-67 | 67 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 94 and 95 | 6.1.2 Table 6.1 - List of ageing mechanisms. Concerning concrete structures, are pathologies such as Alkali-aggregate reaction and Delayed ettringite formation considered in the AMP ? If yes, please describe the periodical actions (inspections, sampling, laboratory tests...) carried out in the framework of AMP. |  | In technical condition assessment and periodic inspections, attention is paid to the condition of the protective concrete layer; if the protective concrete layer is damaged for various reasons (mechanical damage, alkali reaction), the layer is recovered and the damage cause is eliminated (for example, the damaged roof area is repaired).
UA-68 | 68 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 100 | 6.1.3 Monitoring, testing, sampling and inspection activities for 07. Concrete containment structures. Could the Licensee give the value of the design pressure of each type of containment ? Is there any periodical pressure test of the containment structure ? If yes, what are the measurements carried out, the associated criteria (test pressure, maximum leakage, mechanical behaviour of the civil structure) and the typical results gained ? |  | See the answer to question 174. | ref to UA-174
UA-69 | 69 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 100 | 6.1.3 Monitoring, testing, sampling and inspection activities for 07. Concrete containment structures. Could the Licensee precise those activities carried out on pre-stressing tendons and anchorages: for instance tension testing, sampling of tendons, inspection of possible corrosion, ... ? Please precise the periodicity and the number of tendons concerned for those activities. Please provide the typical results gained from those activities. |  | See the answers to questions 70 and 174. The tension of each pre-stressing tendon is measured annually with a dynamometer; the measurement results are considered to determine the scope of monitoring and preventive measures for the containment pre-stressing system for each power unit (including tensioning or replacement of individual tendons in the containment dome or cylindrical part). | ref to UA-70 & UA-174
UA-70 | 70 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 101 and 102 | 6.1.3.3 Monitoring of the technical condition of building structures and components of the containment is carried out on a continuous basis and is a combination of regular technical inspections, visual and specialized instrumental observations, and continuous monitoring of parameters of the boundary conditions of building structures. Could the Licensee provide a detailled description of those technical inspections, visual and specialized instrumental observations, and continuous monitoring of parameters ? Please precise the periodicity of those activities, and the monitoring devices that are used. |  | The technical condition of building structures and components of the containment is monitored on a continuous basis and is a combination of regular technical inspections, visual and specialized instrumental observations, and continuous monitoring of parameters of the boundary conditions of building structures. a) periodicity: current (technical inspection); scheduled; extraordinary special; b) methods: visual; instrumental; c) scope: selective; complete. See also answers to questions 170 and 174. | ref to UA-74 & UA-174
UA-71 | 71 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 95 | 6.1.2 Table 6.1 - List of ageing mechanisms. Item 7 - Containment prestressing system The pre-stressing tendons of the reactor containments are anchored in the support ring located between the dome and the cylindrical wall of the structure. Therefore, the good condition of the concrete and metallic embedded parts located on the dome and on the support ring is an important issue. No significant cracking, no significant rust, and sufficient cleanlyness of the surfaces should be required and checked. Question: what are the provisions included in the AMP of the reactors to address the above mentionned issue ? Please describe the scope and the periodicity of the inspections, and the corresponding operating experience. |  | Visual and instrumental inspections are conducted every five years according to the operator standard.
UA-72 | 72 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 121 | 7.5.2 NUCLEAR RESEARCH REACTOR The report states that ' Monitoring of NRR buildings and facilities includes (...) inspection system for technical condition |  | The question is not finished. The system for technical condition inspection of NRR buildings and civil structures, parameter monitoring and diagnostics is designed to obtain the data on actual geometry, physical and mechanical characteristics and capabilities of structural elements to withstand the loads and changes of the state of civil structures | Full text of question was provided in Excel file of questions. The full question is copied in the next column | 7.5.2 NUCLEAR RESEARCH REACTOR The report states that ' Monitoring of NRR buildings and facilities includes (...) inspection system for technical condition of civil structures'. In addition, ' Monitoring and observation of civil structures (...) include periodic control of (...) :  geodesic observations of the parameters of basements and structures ;  hydrogeological observations;  visual inspection of structures;  instrumental inspection of structures' Could the Licensee give some detailled information about that monitoring (devices used, measurements, acceptance criteria, periodicity, results...) ?
UA-73 | 73 | Concrete containment PCPV expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 17 | 2.3.1.1 Energoatom carries out ageing management of NPP components and structures on a systematic basis beginning from the design stage. Is this valid for V-213 type reactors also ? |  | According to regulatory documents, the operator carries out ageing management for each power unit at each life cycle stage.
UA-74 | 74 | Concrete containment PCPV expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 19 | 2.3.1.3 How often the list of components and structures subject to ageing management is revised in practice ? The above description seems to contain everything in the list, is it necessary to review it? |  | The list is revised no more than once a year (see para. 02.3.1.3).
UA-75 | 75 | Concrete containment PCPV expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 22 | 2.3.1.4 How do the listed data (change in costs for scheduled outages, deviations from operating parameters) to be used as performance indicators to assess efficiency of ageing management for NPP units ? |  | Equipment failures caused by ageing resulting from malfunctions, deviations from operating parameters, etc. are taken into account in effectiveness assessment of the ageing management program.
UA-76 | 76 | Concrete containment PCPV expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 22 | 2.3.1.4 What are the consequences if the indicator is changed ? |  | The question needs to be clarified.
UA-77 | 77 | Concrete containment PCPV expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 22 | 2.3.1.4 Would the value of the performance indicator change if the heeling of ZNPP1 would now occur? |  | See the answer to question 75. | ref to UA-75
UA-78 | 78 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 95 | 6.1.1 What does it mean: general corrosion ? What is the difference between general and local corrosion? |  | The corrosion mechanism is the same. General corrosion is the damage of metallic surface caused by chemical or electrochemical interaction with the active environment (corrosive atmosphere, acid, alkali, or salt solutions, etc.). Local corrosion is a type of corrosive damage that affects individual areas (spot corrosion, pitting corrosion). Local corrosion can be caused by the local influence of corrosive environment (for example: boric acid solution).
UA-79 | 79 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 95 | 6.1.1. (table 6.1. (5)) Have they been investigating what the root cause of corrosion of steel and of damage of paint coating ? Possible preventive maintenance? |  | The causes may be increased moisture, degradation (aging). The preventive measures include preventive maintenance and restoration of paint and varnish coating in places where it is damaged.
UA-80 | 80 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 95 | 6.1.1. (table 6.1. ) The tendon relaxation was not mentioned as ageing mechanisms. Why? |  | The tendons at VVER-1000 unit are replaceable components. The tension of tendons is checked every four years (about 25% of the tendons annually) during scheduled outages with the use of dynamometers. Visual inspections in accessible places are conducted with the same frequency. A remote tension monitoring system is additionally installed at the power units, which allows the tension of all tendons to be monitored almost in real time mode. If inspection reveals that a tendon does not comply with the established criteria, it is tensioned or replaced with a new one.
UA-81 | 81 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 100 | 6.1.3.1 Could you give examples how the information system works ? How the NDI, and visual inspection data are collected, processed and stored ? In what form - photo, description …? |  | The automated ageing management system (AAMS) is intended to: - make and keep a list of components subject to ageing management (AMP components); - keep a list and attributes of ageing management procedures and their sections; - keep a list and attributes of regulatory, technical, reporting and other documents associated with technical condition assessment of components; - plan, record, and monitor technical condition assessment of components and ageing management measures; - record and monitor results of tests, current values of parameters and criteria for technical condition assessment of components; - prepare a report on AMP implementation and a report on ageing management measures for power unit components; - exchange AAMS data between the plant and central AAMS parts; - administer access to data.
UA-82 | 82 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 100 | 6.1.3.1 "The models for prediction of the technical condition are intended to define life of NPP building structures." What type of models are used for prediction of the technical condition ? Do you have a program of model validation ? Are the trending of measured data to taken into account ? |  | The lifetime is assessed by one of the following methods: - probabilistic method; - linear extrapolation method. In the probabilistic method, the lifetime of a structure, building, or facility is determined considering the potential boundary values of the main technical condition parameters that may be reached by their individual components based on verifying calculations. In the linear extrapolation method, the life of structures is determined on the assumption that the temperature dependence of the main parameters is linear. To assess the lifetime of structures, it is needed to determine the rate of changes in the main parameters. The lifetime of a component is equal to the minimum value from all the lifetimes calculated for this component. The lifetime of a structure or a facility is equal to the minimum lifetime among all components (SOU NAEK 109:2016). The technical condition is predicted to determine the life of NPP structures according to methodologies provided in standard programs for technical condition assessment and reassignment of service life. In order to specify the technical condition predictions and, where appropriate, revise the lifetime of structures, AMP includes inspections and technical condition assessments to be conducted every 5 years, which also involve additional assessment of degradation mechanisms and comparison of assessment results with data obtained in previous inspections and specification of the rates of degradation mechanisms.
UA-83 | 83 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 100 | 6.1.3.2 What is determine the frequency of control and observation ? 6.1.3.2. |  | The frequency of inspections and observations is in compliance with SOU NAEK 109:2016.
UA-84 | 84 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 101 | 6.1.3.3. Tests of building structures that shall be obligatory subject to the periodic control procedure includes the integral leak rate test and local leak tests of VVER-440 units ? |  | Periodic integral leak rate tests of the reactor building containment are carried out (before scheduled outage and upon its completion). Local leak tests for the containment are also conducted and the revealed defects are eliminated.
UA-85 | 85 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 101 | 6.1.3.3. Are there predefined quantitaive criteria for classification of condition of structures ? Who defines the need of analyses or verification calculations ? |  | The standard programs for technical condition assessment and reassignment of the lifetime of structures contain the section “Boundary Values of Defects and Damage of Components and Structures”. The need for analysis is determined in review of technical documentation and development of working programs. The calculations are verified by expert assessment of SNRIU (SSTC NRS).
UA-86 | 86 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 102 | 6.1.3.4 Do I understand well: the AM measures described in a living document ? How often is it updated ? 6.1.3.4. Я розумію правильно: Заходи з управління старінням описані в робочій документації? Як часто вона оновлюється? |  | The ageing management measures are described in unit-specific (living) AMS, which are revised as measures are implemented and agreed with SNRIU.
UA-87 | 87 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 103 | 6.1.3.4 "Preventive and corrective measures for concrete structures of the containment." Is this sentence a subtitle (ch. 6.1.3.5) ? |  | This sentence if the title of chapter 6.1.3.5.
UA-88 | 88 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 105 | 6.4 Automated Ageing Management System for Power Unit Components (AAMS). Are the data of maintenance also collected in AAMS ? |  | The AAMS purpose is described in answer 81 of this table of comments on Ukrainian NAR. AAMS collects the following operational data for components and structures for their ageing management:  operating modes of components and structures;  lifetime characteristics;  operating time of components;  loading cycles and actuation of components;  defects and failures;  results of metal inspection for components and structures;  results of technical examination of components and structures;  data obtained in scheduled maintenance of components and structures (revealed damage, its causes, compensatory measures etc.). | ref to UA-81
UA-89 | 89 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 106 | 6.4 "Ukrainian NPPs are currently operated at tendon tension different from the design-basis one" Were the tendon tensions deliberately changed ? Are the tendon tension measured continuously ? Were the containment seismic and over-pressure fragility curves updated time to time according to the measured tendon tension? |  | VVER-1000 NPPs are currently operated with the tendon tension which is somewhat lower than the originally determined in the design upon agreement with SNRIU.
UA-90 | 90 | Concrete containment PCPV expert group | Ukraine | 07. Concrete containment structures | 106 | 6.4. What does it mean MDBA, SSE ? (MDBA - Medium break design basic accident, loca ? If yes, why only MDBA and not LDBA (Large break LOCA) was taken into account ? SSE =Beyond Design Basic Earthquake ?) |  | The combination of loads used in calculations, such as MDBA+DBE and MDBA+SSE means the following:  MDBA – maximum design basis accident;  DBE – design-basis earthquake;  SSE – safe shutdown earthquake, in compliance with NP 306.2.208-2016 that replaced PNAE G-5-006-87.
UA-91 | 91 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | 57 | It is stated that separate “Methodology for Strength Calculation of Underground Piping of the Zaporizhzhya NPP Essential Service Water System Considering Seismic Impacts” was developed for strength calculation of concealed (underground) piping. Why this methodology was developed only for Zaporizhzhya NPP and is it intended to use this methodology for others Ukrainian NPPs? |  | Yes, the separate "Methodology for Strength Calculation of Underground Piping of the Zaporizhzhya NPP Essential Service Water System Considering Seismic Impacts" was developed for ZNPP and is also used for other NPPs.
UA-92 | 92 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 53-53 | The report states in page 52 that the ESW underground pipes are grouped in the ageing management programme according to their operation condition and their diameter, namely 2240, 1620 and 820. However, in figure 1 the diameter of the elbowed pipe situated on the left hand side of the picture seems to be inconsitent with the 3 diameter values provided. Could Ukraine clarify this point? Could Ukraine provide typical pipe wall thickness? |  | The sizes of piping for observation group 1 (discharge piping near the reactor compartment, discharge water lines): Ø820×9 Ø630×8 Ø1620×14. The sizes of piping for observation group 2 (supply piping near the reactor compartment, supply water lines): Ø1020×10 Ø1620×14. See Annex A of NAR.
UA-93 | 93 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 54 | In page 54 of the Report, it is stated that in each "observation group" piping operated with the worst ground conditions and experiencing the most operation cycles is subject to inspection. Could Ukraine specify the frequency of the inspections and how this frequency is determined? |  | No more than every 10 years
UA-94 | 94 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 54 | According to the Report on page 54, it seems that 100% of ESW underground piping of all Ukrainian NPPs is inspected annually using contactless diagnostics. Does Ukraine confirm this statement? |  | 100% of NPP underground piping (systems important to safety) are inspected annually using contactless diagnostics.
UA-95 | 95 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 54, 56, 59 | Could Ukraine detail the capabilities of its contactless diagnostics is evaluating piping condition? What kind of defects are they able to detect? Are they able to measure an overall thinning? Could Ukraine provide references 53, 54 and 55? |  | Acoustic diagnostics reveals “through defects”. Magnetometric diagnostics detects places where metal stresses are concentrated. Overall thinning can be revealed by nondestructive inspection. The referenced documents can be provided to European experts within a workshop on discussion of the peer review results or within visits to NPPs for independent evaluation of ageing management activities.
UA-96 | 96 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 56-57 | Could Ukraine provide references 11, 43, 44 and 63? |  | The referenced documents can be provided to European experts within a workshop on discussion of the peer review results or within visits to NPPs for independent evaluation of ageing management activities.
UA-97 | 97 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 58 | In figure 4.4 of the Report, the quality analysis of service water is mentioned. Could Ukraine specify the nature of this analysis, its frequency and whether its results are used to assess piping condition? |  | The quality analysis of service water is carried out not less than once per month in accordance with SOU NAEK 067:2013. The analysis includes check of pH, water hardness, suspended substances, and sulfur, chlorine, phosphorus, and nitrogen oxides. The results are analyzed when the technical condition of piping is evaluated.
UA-98 | 98 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 60 | Could Ukraine specify why the ageing management measures for ZNPP-1 do not include performing of "contactless diagnostics of certain piping sections with detectcted 'anomalies' " whereas this measure is prescribed for ZNPP-2? |  | Para. 04.1.4 provides examples from the list of ageing management measures established for ZNPP units 1&2. Considering accumulated experience, additional ageing management measures may be identified, which involves changes to the ageing management documents. The ageing management measures for ZNPP-1 will be appropriately revised.
UA-99 | 99 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 60-61 | In page 60 of the Report, it is stated that the monitoring of technical condition on undergroung piping envisages to forecast its technical condition and assess its service life. However the Report does not provide any detail on how this assessment is performed. Could Ukraine explain how monitoring is used to assess piping service lifetime, in particular, taking into account that the main monitoring method is contactless diagnostics as stated in page 61? |  | Forecast of the technical condition and assessment of residual life of underground piping are based on analysis of static and cyclic calculations provided in TCA reports, in accordance with appropriately agreed TCA programs, which include, among other things, strength calculations (see para. 04.4). TCA involves ultrasonic thickness measurement of piping walls. The change in piping wall thickness is predicted by analysis of the actual piping wall thickness and its comparison with the minimum allowed thickness.
UA-100 | 100 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 52 | The second paragraph states that there are no concealed piping other than ESW. The usual setup for VVER1000 unit inludes main condenser cooling water embeded in a undurground concrete block together with non-ESW. The block is between unit a pump station and a turbine building. Does the statement aply for safety related piping only? Or is the Ukrainian setup different? |  | The extension of experience in ageing management and technical condition assessment for concealed piping important to safety to other underground pipping of safety class 4 (for example, circulation water piping) is being considered by the operator.
UA-101 | 101 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 54 | The grouping of lines is based on temperature and pressure. An OpEx from worldwide is that oxygen content and flow/stagnant conditions affects uniform corrosion and pitting.
UA-102 | 102 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 55 | Why is a particular attention paid to places with the most stress concentration? Is SCC considered as important degradation mechanism? |  | Elements with places with the highest stress concentration are “representative elements” that characterize the consequences of impacts, including those for less stressed piping elements.
UA-103 | 103 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 55 | Penetrant testing and magnetic testing is used for questionable places assesment. What kind of ageing effects are addressed? Is it cracks? Is the testing caried out from outer diameter? |  | For underground piping, all diagnostics are carried out from outer diameter, without direct contact with the piping.
UA-104 | 104 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | P 55 | Why is hardness measurement performed? Is there any degradation mechanism changing mechanical properties of steel in place? Or is there a OpEx of using other/worse material than listed in documentation? |  | High loads (temperature, pressure) may cause metal ageing and change in mechanical properties. Based on inspections, no other/worse material, different from the design one, was used for piping.
UA-105 | 105 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | Table 4.1 | FAC is a degradation mechanism typical for oxygen-free environment of secondary circuit. ESW circuit is protected by oxygen. Is there any proof of FAC at ESW in Ukraine? |  | At present, the impact of FAC is not indicated for concealed pipelines. This aspect is under investigation. The corresponding corrective actions will be added to AMP (if needed) according to results of investigations. FAC is typical for secondary loop. Concealed pipelines belong to the 3rd loop.
UA-106 | 106 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | Table 4.1 | What is meant by electrochemical corrosion? Does it mean galvanic corrosion? |  | Electrochemical corrosion is absent on piping of the essential service water system.
UA-107 | 107 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | Table 4.1 | Why is Erosion considered as ageing effect instead of ageing/degradation mechanism? |  | Erosion processes are absent on piping of the essential service water system.
UA-108 | 108 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | Table 4.1 | What is basis for considering of fatigue as a key degradation mechanism of ESW piping? |  | The key degradation mechanism for piping of the essential service water system is metal corrosion and change in mechanical properties.
UA-109 | 109 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | Table 4.1 | What is a diference between general corrosion and corrosive wear? |  | General (continuous) corrosion covers all or a substantial part of metal surface. The criterion to assess general corrosion is corrosion penetration depth (millimeters per year) or weight corrosion indicator (grams per square centimeter an hour). Corrosive wear is the ability of material to form oxide films resulting from metal surface oxidation due to chemical, electrochemical or any other process, which makes the metal passive. Nevertheless, it is not excluded that corrosion can penetrate into the metal to a certain depth.
UA-110 | 110 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | Table 4.1 | What is crumbling? |  | The ability of material to be destroyed without noticeable residual strains (property opposite to ductility).
UA-111 | 111 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | 56 | Are Workings programs available for ZNPP Units 3-6 too? |  | Yes
UA-112 | 112 | Concealed pipework expert group | Ukraine | 04. Concealed pipework | 55 | Ageing effects in tables 4.1 and 4.2 are not related |  | Yes. The Table 4.1 comprises ageing mechanism and ageing effects that have to be monitored. The table 4.2 comprises dominant current technical state parameters of concealed pipelines that are the basis for evaluation of their further operation.
UA-113 | 113 | Cables expert group | Ukraine | 03. Electrical cables | 39 | The NAR states that "It is allowed not to include cables whose replacement is possible in a List of Representative Cables". Could you please clarify that statement. It looks logical that the replacement of a cable might be one of the advisable LTO (or pre-LTO) actions, so what would be the reason not to include those cables in the representative list? |  | It is allowed not to include cables whose replacement is economically and technically feasible before expiration of their service life into the list of representative cables. The cables not included in the list are thus replaced before their service life expires.
UA-114 | 114 | Cables expert group | Ukraine | 03. Electrical cables | 39 | How many cables and how many cable commodities (groups of cables, with similar characteristics, degradation mechanism) are covered by CAMP for a typical WWER 1000 and for WWER 440? |  | The number of cables depends on NPP and the power unit. On average, there are 10,000-12,000 cables of systems important to safety per power unit. At RNPP -1,2 (VVER-440), there are on average 12,000 cables of systems important to safety per power unit.
UA-115 | 115 | Cables expert group | Ukraine | 03. Electrical cables | 40 | Table 3.3 (for RNPP Unit 4, which is used as an example) indicates expected lifetime of cables listed as being 20, 25 and 30 years. Were the same cables (i.e. manufactured to the same standard) installed at other units, including the older ones like Rovno 1-2 and South Ukraine units? If yes, were all of those cables already replaced? |  | Different units of Ukrainian NPPs operate cables with lifetimes of 20, 25 and 30 years. Part of these cables was replaced (before expiration of their lifetime) and part was subjected to TCA and their life was extended.
UA-116 | 116 | Cables expert group | Ukraine | 03. Electrical cables | 43 | The Nar states " TCA activities to start three years before lifetime expiration". However, the Table 3.3 seems to indicate that the lifetime of some of the cables is shorter than the lifetime of the plant, so actions (replacement) might be needed well before the NPP are reaching the end of their lifetime. could you please clarify. |  | TCA of cables starts two to three years before their lifetime expires, but not the lifetime of the power unit.
UA-117 | 117 | Cables expert group | Ukraine | 03. Electrical cables | 44 | The hot spots along the cable routes are identified by visual inspections, which is looking for visible effects decolouration, sheath cracking, etc. Are you using thermography to identify hot spots? |  | Hot spots are identified using many indicators. Visible effects are only one of these characteristics. To specify areas with increased heat, a thermal surveillance device is used.
UA-118 | 118 | Cables expert group | Ukraine | 03. Electrical cables | 44 | For known (identified) hot sport, what would be the frequency of " regular monitoring"? Is the frequency adjusted depending on the e.g. temperature or e.g. already identified effects (decolouration)? |  | Measurements are conducted on a permanent basis. When temperature in a room increases, corrective measures are taken.
UA-119 | 119 | Cables expert group | Ukraine | 03. Electrical cables | 45 | Upon analysis of the monitoring results, how do you specify remaining lifetime of a cable if e.g. it operates in a higher temperature than given by the design? Are there established criteria for various combination of temperature/cable types and also for radiation damage? |  | It is not allowed to operate a cable at temperatures higher than given in the design. The remaining lifetime of a cable is established by a specialized organization depending on actual temperature in a room.
UA-120 | 120 | Cables expert group | Ukraine | 03. Electrical cables | 45 | The NAR indicates that the " viable specimens are placed at NPP in accordance with the programme". Could you specify 1) how many specimen are in place now at specific units 2) how do you decide which specimen to place and where and 3) how (methodology) and with which frequency are those specimens tested ? |  | There are specimens for 19 types of cables at KhNPP-1 and for 13 types of cables at KhNPP-2. The specimens are placed in the harshest operating conditions.
UA-121 | 121 | Cables expert group | Ukraine | 03. Electrical cables | 45 | Do you have any agreement in place with similar units internationally that might be using similar cables ( e.g. Kozloduy, Dukovany/bounce) for using common specimens of interest? |  | There are no agreement with other states at international level.
UA-122 | 122 | Cables expert group | Ukraine | 03. Electrical cables | 48 | The NAR states that in parallel with the replacement of the instrumentation and control (some of the ) cables were replaced, so there are no more of the cables (for example, of KMPEVE, KPoSG, KPOESV types) in the rooms having harsh environment. Does it means that other cables (that might be subject to similar degradation mechanisms) remain in rooms with harsh environment? |  | Part of cables may be located in rooms with harsh environments. Safety upgrades implemented at NPP units also envisage replacement of cables with those that comply with modern requirements.
UA-123 | 123 | Cables expert group | Ukraine | 03. Electrical cables | 48 | Does the " harsh environmental conditions" include HELB in all the rooms when such could occur? |  | In the framework of equipment qualification, a list of initiating events with indication of rooms where harsh environments may occur was developed for each power unit and agreed with SNRIU.
UA-124 | 124 | Cables expert group | Ukraine | 03. Electrical cables | 48 | Are there any buried cables or cables in the (e.g. underground) ducts, where those could be affected or even submerged in water (causing e.g. water tree) found at Ukrainian NPPS? What kind of AMPs are applied to such cables? |  | According to regulatory documents, cables are not allowed to be buried directly in soil. At nuclear power plants, cables of safety systems are laid in cable structures (special cable ducts, etc.)
UA-125 | 125 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 17 | Division of responsibility for AMP by operator 02.3.1 Scope of the overall AMP 02.3.1.1 Distribution of responsibilities within the licensee to ensure development and implementation of the overall AMP: The operator conducts ageing management of component |  | Comment is accepted.
UA-126 | 126 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 17 | Scope of Age Management Plans According to NP 306.2.141-2008 [5], NP 306.2.099-2004 [6], NP 306.2.210-2017 [7] and SOU NAEK 141:2017 [75], AMP includes: All critical components and structures of NPP unit1 that include but not limited to: • RPV, closure head, internals and support elements; • reactor coolant piping, particularly RCP casing and MGV and surge line; • steam generators; • pressurizer; • ECCS accumulators; • pressure relief tank, emergency cooldown heat exchange, regular heat exchanger of spent fuel pool; • high-pressure system piping; • feedwater system piping; • emergency and auxiliary feedwater system piping; Noncritical components important to safety whose regular scope of inspection and maintenance does not allow identifying ageing affects and mitigating degradation or whose maintenance revealed defects; Buildings and structures containing systems and components important to safety; Instrumentation and control systems (I&C), cables (power and control) and cable structures are included into the list in one line with references to: • equipment qualification programs for I&C; • AMPs for cables (power and control) and cable structures and equipment qualification programs for cables (power and control). The operator may also decide to include normal operation components into AMP that has no impact on safety and cannot be replaced or recovered for technical or other reasons, such as:   turbine facilities with a condenser;   turbine generators;   power transformers. The list of components and structures subject to ageing management is developed individually for each power unit and included into NPP AMP or unit-specific AMP. Based on AMP implementation and operating experience, the operator may revised the list of components and structures subject to ageing management (not more than once a year). |  | Comment is accepted. Thank you for the assessment.
UA-127 | 127 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 21 | Commendable practice: Establishment of a common database for collection and analysis of data relevant to age management of structures and components Collection and analysis of data 02.3.1.5 Quality assurance of the overall ageing management program The quality assurance requirements for ageing management are established in the Standard AMP [11] and in the operator’s document “Quality Assurance Program for Ageing Management at NPP Units. PK-Ch.0.08.410-07” [29]. Collection and storage of data and analysis of trends in the maintenance history and operating data To ensure effective ageing management of components and structures, all data important for ageing management are collected and processed. For this purpose, an electronic database that represents an Ageing Management Information Analysis System (AMIAS) was developed and implemented. A separate module was developed for each NPP as a software application integrated with lists, directories and classifiers of the Ukrainian reliability database for NPP equipment. AMIAS is intended to ensure effective ageing management of components and structures of all NPP units. AMIAS provides information support of the main functions, such as:  analysis of design, operational and maintenance documents, operating and maintenance history of components and structures;  monitoring of ageing processes and technical condition;  technical condition assessment of components and structures and prediction of their changes resulting from ageing relative to safety functions;  development and technical and administrative measures to keep degradation of power unit components and structures resulting from ageing;  collection and recording of data on components;  recording of the actual number of loading cycles and those caused by actuation of components;  planning, recording and monitoring of ageing management activities for components and structures;  reporting on ageing management;  assessment of ageing management efficiency using corresponding performance indicators;  exchange and provision of information on ageing management of single-type components and structures of NPP units in the industry. AMIAS collects and stores information containing design data (in particular, regulatory requirements), data on manufacturing (in particular, properties of applied materials and required operating conditions), data on maintenance history, inspection results and research findings. |  | Thank you very much for the favorable assessment for the benefit of European cooperation and contribution to positive practices of operation and nuclear safety regulation and development and future of nuclear energy.
UA-128 | 128 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 22 | Regulator’s conclusion of the effectiveness of AMP In summary, data are provided on the presence or absence of failures caused by equipment ageing during each year and improvement or deterioration of the performance indicator for efficiency of ageing management at each NPP unit. Performance indicator for efficiency of AMP implementation at Ukrainian NPPs for 2016 are considered to be satisfactory. Failures or abnormal operation due to ageing effects were not observed. AMPs are recognized as effective. |  | Comment is accepted. Thank you for the assessment.
UA-129 | 129 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 27 | Systematic incorporation of research and experiences gained into AMPs: 02.3.2.6 Use of internal and external operational experience Energoatom revises AMP to incorporate operating experience feedback and research, as well as results of self-assessments and expert judgements. In determination and analysis of degradation mechanisms, summarized national and international operating experience is taken into account (for example, international generic lessons learned program (IGALL)). In particular, Ukraine implemented a number of international projects, ... The conclusions and recommendations of foreign partners made in the implementation of these projects are considered in unit-specific AMPs and regulations on ageing management. Operating experience may also be used to revise the lists of components and structures subject to ageing management and determine ageing management measures. For higher efficiency, planning of ageing management activities for components and structures includes collection and analysis of information obtained in the industry and from foreign sources on operating experience of components and structures and uses results of ageing management analysis. NPPs also systematically collect information on operating experience and research findings and assesses their applicability to a specific NPP. Acceptance criteria, operating experience and research and development findings are described in detail in AMPs for individual components and structures. |  | Comment is accepted. Thank you for the assessment.
UA-130 | 130 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 27 | Similar to other countries’ reports 02.3.3.1 Programs for monitoring of indicators and parameters of the condition and analysis of trends To monitor the technical condition of power unit components and structures and assess ageing effect, in-service inspection, maintenance, testing and inspection programs for components and structures were developed and are systematically optimized. The specific examples include programs and documents that are regularly revised and updated:... Based on in-service and inspection programs for power unit components and structures:  additional scope of condition-based maintenance and lifetime monitoring of NPP components is determined;  necessary changes to in-service inspection programs are introduced or new inspection programs are developed in compliance with the NPP procedures. Based on monitoring of ageing processes and analysis of tendencies in condition parameters of power unit components and structures, measures are implemented to optimize:  frequency of inspection to check operability of components;  frequency and scope of measurements and testing of components and structures;  in-service metal inspection of components and structures;  maintenance of components and structures. |  | Comment is accepted. Thank you for the assessment.
UA-131 | 131 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 32 | When in connection with application for LTO the schedule for AMP is fixed to the start of LTO; with the new documents entering force (p.36), which schedule will then be used? Results of AMP implementation are also considered in SNRIU inspections. According to established practice, SNRIU conducts two comprehensive inspections in power unit preparation for LTO upon completion of the design-basis life. The first inspection is conducted six to eight months before the power unit starts LTO and is intended to check preparations for LTO. Significant attention is paid to implementation of ageing management measures. The second comprehensive inspection is conducted about one month before the power unit starts LOT and focuses on completed measures and power unit preparedness for LTO. Based on inspections, AMP may be amended in compliance with SNRIU prescriptions. |  | Comment is accepted. Thank you for the assessment.
UA-132 | 132 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 32 | Quite similar to UK report 02.4.2 Review of the time limited ageing analysis (TLAA) Time limited ageing analysis demonstrates that TCPs for a specific component or structure will not exceed criteria established in NRS regulations, standards and rules and design documentation over the entire period for which analysis is carried out. A specific listof TCPs considered in time limited ageing analysis is made upon TCA results and operating experience .... and p. 33: 4. For cables:  thermal degradation of insulation materials;  loss of isolating properties of materials under the action of electrical field and moisture. Time limited ageing analysis is considered acceptable if it meets one of the following criteria:  analysis remains valid for the intended period of LTO. TCPs of components and structures will not exceed the value accepted in ageing analysis that determines the lifetime;  analysis has been projected for the design-basis/long-term operation period. Analyzed TCP value changes with time but continues to meet the acceptance criteria at the end of the design-basis/long-term operation period;  effects of ageing on the intended function of a structure or component will monitored for the design-basis/long-term operation period. AMP ensures that a component or structure performs design functions by monitoring of TCP compliance with acceptance criteria over the entire power unit operating period and timely implementation of compensatory measures, in particular, degradation mitigation measures. .... The above-mentioned analyses are carried out in power unit preparation for LTO. Results of the analysis serve as a basis for developing additional (if necessary) ageing management measures, which in turn leads to AMP revision/updating. Measures added to AMP based on TLAA results may also serve as a basis for new or continuation of existing research activities. |  | Comment is accepted. Thank you for the assessment.
UA-133 | 133 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 35 | Comment: It is unclear whether this is the regulator’s or the operator’s conclusion on existing AMP, in particular on the AMP subdivisions being “provided with adequate financial, material and human resources”. 02.5 Summary of ageing management processes and key findings by the licensees Upon summary of the ageing management processes by the licensee, the following conclusions are made:  in compliance with regulatory requirements, the operator developed detailed technical requirements that cover all aspects of ageing management activities. These requirements were developed considering international and national experience and practices, IAEA recommendations and provisions of WENRA documents;  operator established subdivisions at each NPP that carry out ageing management activities. These subdivisions are provided with adequate financial, material and human resources;  regulatory documents were developed to clearly determine requirements for the selection of components and structures for ageing management;  regulatory requirements were established for timely implementation of preventive and remedial measures to mitigate degradation;  AMP efficiency is assessed and the operator’s self-assessment and independent assessment of ageing management activities are carried out on a permanent basis;  results of ageing management activities are properly recorded and included into AMIAS. Results of independent assessments by international organizations indicate that current Ukrainian regulatory requirements on ageing management form a strong framework for the solution of these issues. The Ukrainian regulations in this area were developed considering IAEA and WENRA recommendations and the best international experience and practices. The regulations are revised and improved in a planned manner. to centrally collect relevant experiences and continuously incorporating them in a standard AMP for all NPPs is a good practice, provided that all changes are emphasized/underlined, preferably with information on the date of the change, to assure consequential revisions of local AMPs 02.6 Regulatory oversight The main regulatory requirements for ageing management and associated processes are set forth in NP 306.2.141-2008 [5], NP 306.2.099-2004 [6] and NP 306.2.210-2017 [7]. During development of the National Report, the regulatory document “Requirements for Periodic Safety Review of Nuclear Power Plants (NP 306.2.214-2017)” [89] came into force. To implement overall regulatory requirements, the operator developed a number of documents with detailed technical requirements for ageing management and Standard AMP [11], which were assessed by SNRIU for compliance with NRS regulations, standards and rules, international experience and practices and IAEA and WENRA recommendations. All documents developed by the operator were favorably evaluated after resolution of SNRIU comments and agreed for application. The Standard AMP [11] was developed by the operator in 2004, and implementation of ageing management approaches at Ukrainian NPPs has begun since that time. Ageing management components (maintenance, in-service nondestructive and destructive metal inspections, definition of degradation mechanisms and development of measures for their prevention and mitigation) have been present in the operational practices since NPP commercial operation. The Standard AMP [11] is regularly revised by the operator with introduction of changes and updates to incorporate experience in implementation of ageing management measures, results of new research activities on ageing management and other measures. It should be separately noted that regulatory oversight of completeness and adequacy of the operator’s detailed technical requirements is conducted on a permanent basis. |  | Thank you for the assessment. The regulatory framework must be developed and at the same time updated to incorporate the operator’s experience with science and industry. See para. 02.5 – this is the operator’s conclusion. “Subdivisions” of the operator at NPPs are meant here, which deal with ageing management activities, but not “subdivisions” of the program. The regulator’s conclusion is in para. 02.7.
UA-134 | 134 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 36 | Good practice: As ageing management is also necessary before the time of “Long Term Operation”, the regulator has demanded separate documents for the two issues. These are now almost finished as “industry standards”. 02.7 Regulator’s assessment of the overall ageing management program At present, the Standard AMP [11] is the main document of the operator and establishes overall requirements for the procedure for ageing management of components and structures and determines the scope and sequence of LTO activities. The main drawback of the Standard AMP [11] is that it combines aspects of AM and LTO, while they should be governed by separate documents of the operator, as required in NP 306.2.210-2017 [7]. This drawback is noted in the SSTC NRS Report “Generalized Analysis of Documentation on TCA and LTO and Ageing Management of NPP Units. Recommendations on Revision of Regulatory Framework” [72], prepared upon SNRIU request to find drawbacks in the regulatory framework related to AM and LTO. Currently, this drawback has been practically removed by the operator through development of two separate industry standards that govern AM and LTO: SOU NAEK 080:2014 [14] and SOU NAEK 141:2017 [75]. SOU NAEK 141:2017 [75] is currently in the final agreement stage. When this standard comes into force, the Standard AMP [11] will become invalid. SNRIU conducts continuous oversight and monitoring of AMP implementation at Ukrainian NPPs. According to NP 306.2.210-2017 [7], the operator annually submits reports on AMP implementation to SNRIU. SNRIU assesses and checks information provided in the operator’s reports during scheduled inspections at NPPs, particularly in assessment of issues related to ageing management. |  | Thank you for the assessment. The regulatory framework must be developed and at the same time updated to incorporate the operator’s experience with science and industry.
UA-135 | 135 | General AMP expert group | Ukraine | 03. Electrical cables | 37 | Very similar to UK report 03.1.1 Scope of ageing management for electrical cables Cable ageing management envisages the following activities: Cable ageing management envisages the following activities:  develop cable AMP for power units considering features of the NPP cable system;  monitor operating conditions;  identify cables and make a list of representative cables for inspection;  place (deposit) surveillance specimens;  develop TCA working programs and methodologies for groups of single-type cables;  perform TCA of cables;  record results and keep databases;  ensure quality. |  | Comment is accepted.
UA-136 | 136 | General AMP expert group | Ukraine | 03. Electrical cables | 38 | Comment: The problem with using unit CAMPs (instead of using a common, centrally updated CAM) is keeping them up-to-date “Cable Ageing Management Program for Nuclear Power Plants” PМ-Т.0.08.121-14 (CAMP) [12] was developed for cable ageing management. This Program is standard and applies to control (management, instrumentation, alarm and interlock) cables with plastic and rubber insulation and to medium-voltage (from 380 V to 3 kV) and high-voltage (over 3 kV) cables with plastic and paper-oil insulation, which are operated at NPP units and belong to the systems and components important to safety (safety classes 2 and 3) in compliance with NP 306.2.141-2008 [5]. CAMP [12] specifies:  content of ageing management activities;  requirements for the “Cable Ageing Management Program for Nuclear Power Plant Unit” (CAMPU);  requirements for the contents of “Working Programs for Technical Condition Assessment of Cables”;  requirements and principles for the development of lists of cables subjected to TCA;  procedures to monitor operating conditions of cables and detect hot spots;  methods for cable TCA;  requirements for cable TCA aimed at their lifetime extension;  requirements for databases and information on cables to be included into databases on cable operation;  records on ageing management measures;  content of scientific and technical support and assistance to activities;  requirements for quality assurance. |  | CAMPs are periodically updated. This is a comment rather than a question.
UA-137 | 137 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation |  | Regarding chapter 02 the Ukrainian report is following the technical specifications. The information in well presented and covers the requested subchapters. The information about the research reactor is given in a sparate chapter - 07 which is deviation form the techincal specifications. Neverhteless it covers all aspects of AMP requested in chapter 02 for NPP but summarised in one chapter dedicated to the research reactor. |  | Comment is accepted. Thank you for the positive assessment.
UA-138 | 138 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 13 | Instead of "equipment, systems and components please write "systems, structures and components". |  | Meaning is the same. In compliance with NP 306.2.210-2017, “systems, components and structures” may be an option.
UA-139 | 139 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 14 | In the list of ageing management activities: mitigation is missing. |  | The list of ageing management measures in bullets 2), 3) includes degradation mitigation measures. To ensure unique understanding, it is reasonable to complete the list with “degradation mitigation measures”.
UA-140 | 140 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 18 | Figure 2.3: "Maintenance scope allows revealing ageing effects" is correctly: "Inspection scope allows…" |  | The question depends on the interpretation/understanding of the terms “maintenance” and “inspection”. According to practices, maintenance cannot be considered an inspection.
UA-141 | 141 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 18 | Figure 2.3: Arrow is missing from box "Maintenance scope alows revealing ageing effects" to box "Maintenance scope allows elimination of degradation". |  | Yes, there must be an arrow. Thank you for the indication of weak point.
UA-142 | 142 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 19 | Footnote 1 defines critcal components that "…whose replacement... is impossible…". Replacement of many components in the list is not impossible. It is a contradiction. |  | Replacement of this equipment is not economically feasible.
UA-143 | 143 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 22 | Performance indicators of ageing management efficiency: some of the indicators (first two for sure) refer to effectivenes and not efficiency. |  | Comment is accepted.
UA-144 | 144 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 24 | 02.3.2.3: list of data to collect seems too eclectic (some of the data do not have direct relation to ageing). |  | Comment is accepted.
UA-145 | 145 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 26 | Telelin NPP is correctly: Temelin NPP. |  | Thank you very much, a typing error.
UA-146 | 146 | General AMP expert group | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 32 | TLAA list: which penetrations are included? Also: corrosion resistance of which components? Please write these terms precisely. |  | In this case the penetrations of containment are considered. Corrosion resistance of equipment and pipelines.
UA-147 | 147 | EC | Ukraine | 01. General information | - | Could it be possible also for the research reactor to record the data with AMIAS database? |  | No. NRI of Ukraine keeps its own database on defects. At present, this database is not electronic.
UA-148 | 148 | EC | Ukraine | 01. General information | Chapter 07.6, page 122 | In page 122 is mentioned: "Operation of the NRI VVR-M research reactor was started on 12 February 1960. The design did not establish its lifetime, and not the research reactor is in LTO.". Comment: The research reactor has been in operation during 57 years. In the opinion of the reviewer this reactor is really in LTO. Please clarify this issue. |  | Most of VVR-M components and systems important to safety were replaced by new ones, whose lifetime is indicated in respective operational documents. The reactor vessel (tank) and part of primary piping have been in operation without replacement since 1960. The lifetime of these components is established upon results of Periodic Safety Review. All these factors in combination allow long-term operation to be conducted in accordance with license conditions. The current license of the research reactor is effective until 31 December 2023.
UA-149 | 149 | EC | Ukraine | 01. General information | pg. 9 - 01.1 Table 1.1 | Ukraine is referring to extended in life time installations: 7 extended and 3 to be extended. Are you taking into account the last reference of the IAEA for LTO (Ageing for management and Development of a Program for Long Term Operation of Nuclear Power Plant)? Are you developing a specific program for this all extended installations? Could we have a description of this program, different respect to the other installations? |  | See IAEA documents - para. 02.2.
UA-150 | 150 | EC | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | 17 | "...NPP AM Services developed the following unit-specific AMPs in compliance with requirements of the Standard AMP [11] and agreed them with Energoatom and SNRIU…" Could you please indicate when these AMPs where developed and if some support from TACIS or INSC projects was used for this development? |  | The ageing management programs within TACIS project were developed in 2013 and are used in preparation of ageing management documents.
UA-151 | 151 | EC | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | pg. 16 - 02.3 | "Description of the overall ageing management program" is written that it is described in reference [11] (on the website it is not available). At least could it be possible to have a description of this overall ageing management program, as indicated in the title of the paragraph? |  | Document “PM-D.0.03.222-14. Standard Program for Ageing Management of NPP Components and Structures” can be provided within a workshop on discussion of the peer review results.
UA-152 | 152 | EC | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | pg. 17 - 02.3.1.1 | The overall AMP is developed following the "unit-specific". Could we have an example, a description, instead of having just pointed out in the reference? |  | The overall (standard) AMP is used to develop AMPs for specific power units, as indicated in para. 02.3.1.1. These AMPs can be provided to European experts within a workshop on discussion of the peer review results or within visits to NPPs for independent evaluation of ageing management activities.
UA-153 | 153 | EC | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | pg. 19 - 02.3.1.4 | Referring to the development of the methodology for the AMP for each NPP, can more details be provided of the SSC chosen for each installation, chosen tensors for the analysis, surveillance program, sampling if any, inspection frequency, a program to follow? |  | The NPP components and structures are chosen according to the safety classification of power unit components, design documents, installation and operational diagrams, certificates and other operational documents.
UA-154 | 154 | EC | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | pg. 21 - 02.3.1.5 | AMIAS is a good example: an electronical database to collect the information. Could it be generalized for all countries, as a product? Is it only a database to collect information or as you write in the description it is able to monitor the ageing process? This means that is it also a live process for some surveillance, is it also elaborating data or is it only a collector of data? |  | Thank you very much for the favorable assessment for the benefit of European cooperation and contribution to positive practices of operation and nuclear safety regulation and development and future of nuclear energy. The European experts can get familiar with AMIAS and decide if it can be used at European NPPs within a respective project.
UA-155 | 155 | EC | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | pg. 22 - 02.3.1.5 | It is a good practice to have indicators as a method of evaluation: which is the percentage that you consider satisfactory, which is the reference that you follow? |  | The operator developed and use performance indicators to evaluate the effectiveness of ageing management activities and use them in reports submitted to SNRIU. Compliance with 9 effectiveness attributes is also acceptable.
UA-156 | 156 | EC | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | pg. 25 - 02.3.2.4 | Which are the references for the acceptance criteria, which are their limits? |  | The acceptance criteria are 9 ageing management effectiveness attributes, which are indicated in NP 306.2.210-2017 and operator standards.
UA-157 | 157 | EC | Ukraine | 02. Overall Ageing Management Programme requirements and implementation | pg. 28 - 02.3.3.1 | For the inspection program you refer to specific unit and to your internal documents, could it be possible to have a description of the general approach of the monitoring, testing, sampling and inspection activities? |  | The general approaches are indicated in regulatory documents provided in para. 02.3.3.1
UA-158 | 158 | EC | Ukraine | 03. Electrical cables | 46 | What is the frequency of analysing surveillance specimens installed in hot spots, and when were these specimens installed? |  | 1) The rooms where temperature sources are present are monitored on a permanent basis; 2) The rooms where temperature sources are absent are monitored by personnel of respective departments according to schedules (twice a month in the strict access areas of categories 2, 3 and once per year during scheduled outage in the strict access area of category 1), and the monitoring results are entered into respective logbooks.
UA-159 | 159 | EC | Ukraine | 03. Electrical cables | 46-47 | Concerning the inspections and testing of cables in operating conditions, could you please provide more information on frequency and acceptance criteria for the applied methods? |  | The inspections and testing are carried out in compliance with maintenance schedules. The criteria are indicated in the programs for inspection of technical condition.
UA-160 | 160 | EC | Ukraine | 03. Electrical cables | Generic 37-51 | The report doesn't refer to the cable categories defined in the TRP Technical Specifications. |  | The report indicates the main groups of cables used at NPPs.
UA-161 | 161 | EC | Ukraine | 04. Concealed pipework | 52-61 | Diagnostic methods (magnetometric diagnostics method and acoustic tomography method) are the key inspection methods for essential service water (ESW) piping. Are these diagnostic methods qualified, i.e. has their effectiveness and reliability been sufficiently demonstrated? If not or uncertain it would be desirable to implement additional measures, like monitoring of water chemistry and measures to reduce possible pipe degradation as much as possible, e.g. applying protective coating on inner surface of ESW pipes or installation of cathodic protection. |  | The diagnostic methods (magnetometric diagnostics method and acoustic tomography method) were not chosen without a reason. Their efficiency and reliability has been confirmed by international experience in their application at gas and oil networks and water conduits. Before application, they were tested also at ZNPP and their effectiveness was confirmed. These methods are included into working programs 01.GTs.VF.VG.PM.08 and 02.GTs.VF/VG.PM.19-13 3ON, which are indicated in NAR and were agreed by SNRIU.
UA-162 | 162 | EC | Ukraine | 05. Reactor Pressure Vessels | Chapter 05.1.3.1, page 78 | What is the reason for the different embrittlement behaviour of Unit 2 and Unit 1 of Rivne reactor pressure vessels?. Is only due to the different phosphorus content of the vessel welds? |  | The different embrittlement behaviors of Rivne unit 1 and unit 2 is due to differences in the chemical composition of steels (see para. 05.1.3.1, page 78).
UA-163 | 163 | EC | Ukraine | 05. Reactor Pressure Vessels | Chapter 07.2.3, page 110 | In page 110 is indicated: "An example of the list of components and structures included in the NRR AMP is presented in Annex H". But Annex H is missing in the national report. |  | Typing/editorial error. It should be Annex G. Annex G is the last Annex of NAR.
UA-164 | 164 | EC | Ukraine | 07. Concrete containment structures | 89 | It is said that ageing mechanisms are defined from monitoring and TCA. There is no mention of the application of international standards, practices, guidance, own and international operating experience feedback and results of research. How is it ensured that exhaustive consideration of the applicable ageing mechanisms for each component is performed? |  | The methodology of activities on VVER-1000 containment structures complies with Standard Program PM-T.0.03.181-13, which takes into account international experience (see para. 06.1.2).
UA-165 | 165 | EC | Ukraine | 07. Concrete containment structures | 91 | Figure 6.1: At the first decision point, it is written 'Did mechanical properties and /or defects change in operation of inspected CSS components?'. Please could you provide some further explanation of this step. On the basis of which data from which sources is this decision made? When is the methodology shown in Figure 6.1 applied? With what frequency? |  | It is based on analysis of operating and technical documentation and results of previous inspections.
UA-166 | 166 | EC | Ukraine | 07. Concrete containment structures | 94 | Table 6.1, item 6: If carbonation is identified as a degradation mechanism of concern, how is carbonation depth measured? |  | The depth of concrete carbonation is determined by calorimetric method: concrete splits or cores drilled out of concrete are broken and the freshly formed cleaved concrete surface is wetted with a 0.1% alcohol solution of phenolphthalein. When the concrete with pH ≥ 8.3 is wetted with a phenolphthalein solution, magenta coloring appears on it, while concrete with pH <8.2 retains its original color, which indicates that it has undergone carbonation and no longer protects the reinforcement from corrosion.
UA-167 | 167 | EC | Ukraine | 07. Concrete containment structures | 94 | Table 6.1, item 7: How is the tendon tension measured? Are these measurements made during every outage? Has there been any unexpected decrease in tendon tension? Can you provide more details about the process 'Optimize tendon tension'. Has tendon tension. |  | During each scheduled outage, the tension of each pre-stressing tendon is measured with a dynamometer; the measurement results are considered to determine the scope of monitoring and preventive measures for the containment pre-stressing system for each power unit (including tensioning or replacement of individual tendons in the containment dome or cylindrical part).
UA-168 | 168 | EC | Ukraine | 07. Concrete containment structures | 98 | Table 6.2, item 3: It is not clear what the walls and coverings of the foundation part are? Does this include all the walls, ceilings and floors of the hermetic containment structure, as these are not included elsewhere in Table 6.2? |  | The walls and coverings of the foundation part of the reactor compartment are walls and coverings at elevation 0.000 and below. The containment above and below elevation 0.000, part of the reactor cavity and rooms of ventilation systems that belong to the containment.
UA-169 | 169 | EC | Ukraine | 07. Concrete containment structures | 100 | The WENRA Technical Specification requests that the NAR describe the monitoring, testing, sampling and inspection activities, their frequency and acceptance criteria. The report does not provide much detail about individual inspection and testing activities and their frequencies, and no acceptance criteria are mentioned. Could you provide some further information on these aspects? |  | See the answers to questions 170 and 174. | ref to UA-170 & UA-174
UA-170 | 170 | EC | Ukraine | 07. Concrete containment structures | 101 | Parameters of building structures that shall be obligatory subject to periodic control. Seven bullet points are listed. Please can you provide information on the periodicity of these controls. Also, regarding the 6th bullet, please can you give more details about the physical and mechanical properties controlled and for which structures and components |  | The control of buildings and structures is based on the system of technical observations including various inspections conducted with different frequency depending on the required intensity of control. The condition of structures is monitored through: - current periodic inspections (current inspections); - overall periodic inspections (overall inspections); - extraordinary inspections (extraordinary partial or overall inspections); - observations and technical condition assessment of structures by certified and qualified specialized organizations. According to the required intensity of engineering observations and maintenance, buildings and structures are divided into 3 groups: 1 – group subject to active observations (A) – 4 times per year; 2 – group of moderate observations (M) – 3 times per year; 3 – group of placid observations (P) – 2 times per year. The reactor building belongs to group 1; hence, 2 overall periodic inspections and 2 scheduled inspections as per approved schedule are conducted annually. There are also observations in compliance with the Rules for Technical Operation of Power Plants and Networks, GKD 34.20.507-2003, conducted every 5 years.
UA-171 | 171 | EC | Ukraine | 07. Concrete containment structures | 144 | Figure D.3: In the row before the last row of the table, in the column 'Ageing effect', it is written 'Uncovering of valves'. Should this read 'Uncovering of reinforcement'? Otherwise, please can you clarify the meaning. |  | Yes, the example in Fig. D.3 means the uncovering of concrete reinforcement.
UA-172 | 172 | EC | Ukraine | 07. Concrete containment structures | 94 & 98 | Tables 6.1 and 6.2; item 1: Please can you clarify exactly what the Reactor compartment base comprises, both for the VVER-1000 and VVER-440. It is not clearly described in Appendix D. |  | The description of the reactor compartments for VVER-1000/320 and VVER-440 provided in Annexes D and F is the same as for European reactors of Soviet design.
UA-173 | 173 | EC | Ukraine | 07. Concrete containment structures | 94-99 | Tables 6.1 and 6.2: In some rows it is not clear how the listed 'Technical condition parameters' can be assessed by the stated 'Method for inspection of the technical condition parameter'. As an example, decrease in mechanical properties in rows 2 and 3, by visual inspection. |  | According to Tables 6.1 and 6.2, visual inspection is used to monitor ageing effects that results from changes in the mechanical properties of components and structures
UA-174 | 174 | EC | Ukraine | 07. Concrete containment structures | general | Are containment leak tightness tests performed? What is the acceptance criteria for the VVER-1000 and VVER-440 units? Has there been any deterioration in leak-tightness in previous tests that have been due to ageing of the containment structures? |  | Periodic integral leak-tightness tests (before scheduled outage and upon completion of scheduled outage) of the reactor containment are carried out; for RNPP-1&2, SNRIU approved the criterion of 20 vol.% per day. Defects of RNPP-1&2 containment are not associated with ageing effects. According to PNAE G-10-021-90, the containment is tested for strength one time over the entire lifetime of the NPP unit, during its commissioning. Repeated strength tests must be performed only if elements of the containment that influence its strength were repaired or replaced in the operation process. According to Technical Specifications for Safe Operation: • monitored design parameters: V-302, V-338, V-320:  temperature in the containment no more than 90 °С;  containment rarefaction no less than 15 mm H2O;  containment pressure no more than 1.3 kgf/cm2 (abs.) (1.2 kgf/cm2 (abs.) for V-320);  leak-tightness tests at 0.7+0.02 kgf/cm2 before startup after refueling outage;  rarefaction tests before leak-tightness tests;  preventive measures on the containment pre-stressing system – upon results of previous measures, but not less than every 4 years;  containment leak rate LK1.15Lcr (%/day) according to PNAE G-10-021-90. V-213:  containment rarefaction within 1520 kgf/m2;;  temperature in the containment no more than 60 °С;  annual leak-tightness tests during scheduled outage.
UA-175 | 175 | EC | Ukraine | 07. Concrete containment structures | general | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? |  | As an example, the AMP for South Ukraine unit 1 includes additional inspection of containments-1,2 for:  experimental study of the containment fragment (containment reinforced concrete structure with hermetic steel lining) to check the integrity of the hermetic steel lining (including welds);  analysis of the confinement function (penetration resistance) of concrete in the pressurized area of the containment reinforced concrete structure;  calculations to examine different tensions of tendons. The AMP includes individual inaccessible parts of the reactor compartment, which are monitored by indirect methods (for example, foundation plate).
DE-1 | DE - 1 | Poland | Germany | 03. Electrical cables | 37, 38 | 1. What kind of tests do you perform to check if electrical cables are operable under LOCA conditions? 2. How old are the oldest safety-related cables in nuclear power plants in Germany? When did you start to place cable samples in cable depositories? | Licensee | 1.Real Tests under LOCA-conditions according to KTA 3504 (after thermal and radiological pre-ageing as functional test under LOCA-conditions, additional humididy-tests for long-term LOCA-resistance) 2. Cables in operated NPP in Germany were usually installed during commisioning of the plants. Change of aged cables if necesseary as a result of AM. The cable-depository-system started in 1980. Additionally elongation at break tests on insulating-materials and sheath-materials of aged cables in the depositories were performed to generate service life curves which are used to determine the proven liftime.
DE-2 | DE - 2 | Bulgaria | Germany | 02. Overall Ageing Management Programme requirements and implementation | Table 1-1 | Table 1-1 Nuclear Power Plants in Operation contains data of site, licensee, manufacturer, major shareholder, reactor type, construction line, date of first partial licence, first criticality, shutdown date acc. to AtG. According to data, put in the table, Konvoi reactors are commissioned in 1988 and shall be decommissioned in 2022, i.e. design lifetime is 34 years. BWR reactors are commissioned in 1984 and they have different term of operation (33 and 37). Reactors of construction line 3 also have difference in design lifetime (35, 37 and 35). Would you explain the reasons for such a difference in design lifetime even in reactors from the same construction line. | Regulator | The shut-down dates in Table 1-1 are based on a political decision taken by the Federal Goverment of Germany to phase out the use of nuclear power for the commercial generation of electricity. The period between first criticality and shut-down are shorter that the design lifetime of approximatly 40 years.
DE-3 | DE - 3 | Bulgaria | Germany | 05. Reactor Pressure Vessels | Chapter 5 | The information, presented in chapter 2, represent yours attitude about aging management and that SSC ageing is taken in account in design, manufacturing, commissioning and operation of German NPP, ageing processes are monitored, assessed and corrective actions are taken when necessary. Chapter 5 reveals that the reactor pressure vessels have large margins to known degradation mechanisms (fatigue, embrittlement, etc.). In this respect would you provide some information about German policy of lifetime extension of NPP and if the German policy do not envisage lifetime extension ot NPP what are the reasons for such decision? | Regulator | The Federal Goverment of Germany took the decision to phase out the use of nuclear power for the commercial generation of electricity in a controlled and structured manner. As a legal basis for the operation of the German nuclear installations, the AtG was amended in 2002. The Act laid down the electricity production rights for each nuclear installation. With the amendment of the AtG of 6 August 2011 (13th AtG amendment), further operation of eight nuclear installations for electricity generation (power operation) was terminated, whereas additional dates for the latest possible termination of power operation were fixed for the remaining nine nuclear installations. The last nuclear power plants will be shutdown in 2022.
DE-4 | DE - 4 | United Kingdom | Germany | 07. Concrete containment structures | 103 | Section 7.1.2a describes the ageing phenomena for concrete structures in order to be able to explain their relevance in a comprehensible manner. There appears to be no mention of degradation mechanisms for the steel liner for the BWR or for any waterstops, seals and gaskets. Please confirm the ageing mechanisms for these items (if present) and describe the associated monitoring, testing, sampling and inspection activities and acceptance criteria. . | Licensee | The steel liner and it's piping and cable penetrations are regularily testet. Please look for details at KTA 3401.4, 3403, 3405 and KTA 3407. Gaskets are regularily checked and, if necessary, replaced. Steel liner coatings are also regularly inspected, the interval for example for the condensation chamber water area coating inspection is once in 4 years. Only minor deviations were found and immediately fixed up to now.
DE-5 | DE - 5 | United Kingdom | Germany | 07. Concrete containment structures | 104 | Section 7.1.3.a describes the monitoring, testing, sampling and inspection activities for concrete structures. This section does not appear to mention any leak tests being undertaken. Please confirm whether any global or local leak rate tests are carried out on the containments and if not please explain why they are not done. | Licensee | Leak tests are performed according to KTA standards. Please look for details at KTA 3401.4, 3403, 3405 and KTA 3407. The standards are available in the internet (http://www.kta-gs.de/common/regel_prog1.htm)
DE-6 | DE - 6 | Slovenia | Germany | 02. Overall Ageing Management Programme requirements and implementation | 30 | Effectiveness assessment of the existing ageing management programme (Page 30): To what kind of level of details are nuclear power plants providing the information in annual reports to nuclear regulatory authority about ageing management implementation evaluation against requirements provided in standard KTA 1403? Are there written also results of ageing management programs implementation and operational experience feedback evaluation information? | Licensee/Regulator | The annual ageing-management status report complies with the requirements of the KTA 1403. It updates the basic report and makes qualitative and quantitative statements on ageing-relevant activities and measures, findings and results from in-plant surveillance and external sources. It summarizes statements on the scope, the relevant damage mechanisms and the effectiveness of the ageing-management with respect to the damage mechanisms and about the qualitative conditions of the SSCs. The effectiveness of the aging management is mainly measured against the results of the internal experiences gained by maintenance measures and periodic testing. The evaluation of the external experience feedback is also part of the report.
DE-7 | DE - 7 | Slovenia | Germany | 02. Overall Ageing Management Programme requirements and implementation | 30 | How regulators assess effectiveness of the ageing management program based on annual reporting? | Regulator | In addition to annual reporting, the authority uses other supervisory instruments to verify the effectiveness of ageing management. On the one hand, ageing management itself is reviewed, on the other hand e.g. it is checked within the scope of supervisory activities in other inspection areas (quality assurance, maintenance, modifications, evaluation of special events, fulfilment of certain requirements, PSR and operational monitoring) whether ageing effects are adequately taken into account by the operator. Another indicator to assess the effectiveness of the measures are the results of operational monitoring (fatigue monitoring, vibration, loose parts and leakage monitoring, RPV irradiation surveillance, chemical monitoring coolant, etc.), special tests and PSRs.
DE-8 | DE - 8 | United Kingdom | Germany | 03. Electrical cables | 37 | Section 3.1.2a highlights the inspection of the signal tranmission behaviour. Does this include carrying out Time Domain Reflectometery (TDR) tests? | Licensee | The functional requirements are relevant. Signal-transmission-behaviour is tested usually only on I&C-cables. These tests do not include TDR-tests. Such special tests only in case of findings during standard tests. Depending on the function chain cables are tested with their signal transmission behaviour I&C cables or power cables.
DE-9 | DE - 9 | Slovenia | Germany | 07. Concrete containment structures | 94 | reports and 10year structure condition reports on safety relevant structures in accordance with KTA 1403 more in detail. There is mentioned in the report, that ISIs results and operating experience feedback is provided in annual reports. What is the extend of this information and are these reports prepared by all individual power plants separately and reviewed by the regulatory body? | Licensee/Regulator | Each nuclear power plant creates an individual ageing management report. Annual reports are the basis for the 10year structure condition reports. The 10year structure condition reports are reviewed by the regulatory body.
DE-10 | DE - 10 | Slovenia | Germany | 07. Concrete containment structures | 94-104 | Ageing assessment of concrete structures (Page 94-104): In this chapter beside KTA 1403, there are no other international standard, guidance or R&D activities or programs considered. Even if, when Ageing management program (AMP) was established in Germany not a lot of other documents were available, but has AMP been later compared with other international standards, such as IGALL? | Licensee | International standards are considered in the development and the regular check (5 years) of KTA Safety Standards.
DE-11 | DE - 11 | Slovenia | Germany | 07. Concrete containment structures | 104-105 | Monitoring, testing, sampling and inspection activities for concrete structures (Page 104-105): Are described maintenance activities for concrete structures stated in this chapter also provided or evaluated by third party certification organizations? | Licensee/Regulator | The described maintenance activities for concreate structures are executed with the support of certified partner companies. Independent evaluation is carried out in accordance with the licensees quality assurance program.
DE-12 | DE - 12 | United Kingdom | Germany | 04. Concealed pipework | 53 | Section 4.1.2.a (experience feedback) discusses two GRS information notices (2005/06 and 2007/02). Please provide copies of these. | Regulator | Information notices contain confidential information (business, security, personal etc.). They can be supplied on bilateral request with the restriction that any third party information in the information notice will be deleted.
DE-13 | DE - 13 | United Kingdom | Germany | 04. Concealed pipework | 53 | Section 4.1.2.a (experience feedback) discusses the GRS information notice 2007/02 and the assessment undertaken in response to this. Pigging (for internal inspection) and digging (for external inspection) are highlighted. Is there a view on the extent of each system that these inspections covered i.e. did pigging cover 100% of the system, was it one or two trial digs per system etc.)? | Licensee | Pigging and digging were done as representative examinations on a plant individual basis and strongly dependent on nominal diameters of the systems. For pigging, an overall average percentage was not determined and would not be helpful. For digging there was typically more than one dig for chosen major diameter systems.
DE-14 | DE - 14 | United Kingdom | Germany | 04. Concealed pipework | 57 | Section 4.1.3.a (implementation in nuclear power plants) highlights that the recommendations for non-destructive testing have been implemented. Does this mean that a significant number of systems have already been inspected or are they planned for inspection over a period of time? If a number of systems have already been inspected, please provide further information on the results. | Licensee | Based on the experience feedback described in chapter 4.1.2 a), the recommendations for suitable periodic non-destructive testing have been implemented and approved in the plant specific test instructions of German nuclear power plants on a plant individual basis in the last few years. The positive experiences of the AM coupled with ISI are described at the last paragraph of chapter 4.1.3.
DE-15 | DE - 15 | United Kingdom | Germany | 07. Concrete containment structures | 107 | Section 7.1.4.a presents useful information on the remedial and preventative works for the concrete containments. The section discusses that in 2002, additional strain measurements were carried out on the prestressed concrete containment of a BWR. It would be of interest to understand these additional measures. Please can further information be provided that explains the detail of the additional strain measurements and how these were successfully implemented. | Licensee | Together with an integral leak rate test, strain gauge measurements were performed. Other insights additional to what visual inspections for possible cracks that are associated with tendon failure are able to reveal could not be gained. Therefore strain measurements were not implemented in AMP.
DE-16 | DE - 16 | United Kingdom | Germany | 07. Concrete containment structures | 108 | Section 7.2.a provides an overview of the Licensee's experience of the application of AMPs for concrete structures. Compliance to KTA1403 is observed as a strength of the AMP strategy. This emphasises the benefits of setting down a set of common fundamental principles which provide consistent rules for the systematic ageing management of the concrete structures. Please provide further information on the strategies adopted by Licensees to comply with KTA 1403. It would also be of value to understand whether KTA 1403 is regarded as setting a minimum level of compliance and whether this perhaps restricts innovation and a wider thinking of ageing management issues. | Licensee/Regulator | The KTA 1403 describes the general approach to practise AM and fosters wider thinking of ageing management issues. KTA 1403 is revised every 5 years, whereby the current state of technology is integrated if needed.
DE-17 | DE - 17 | United Kingdom | Germany | 07. Concrete containment structures | General | There is little discussion on the presence and ageing management issues associated with embedded instrumentation. Please provide information on the operational experience and ageing issues associated with the long term safety functionality of containment instrumentation. | Licensee | There is no embedded instrumentation in the concrete containment. See question DE-15. Containment instrumentation is accessible, can be periodically maintained and checked in periodic tests. There are no specific ageing issues with this instrumentation. | ref to DE-15
DE-18 | DE - 18 | United Kingdom | Germany | 07. Concrete containment structures | 94 | Section 7.1.2.a discusses ageing mechanisms affecting 07. Concrete containment structures. There is no discussion on the effects of hot pipework penetrations that pass through the containment wall. Please provide information on surveillance of the hot penetrations that pass through through the containment wall with emphasis on monitoring and assessing the concrete temperatures and long term structural condiiton locally to these locations. | Licensee | Hot piping penetrations through concrete structures are provided with pipe in pipe system, limiting the temperatures at the concrete to a level, where no special focus needs to be put on ageing mechanisms for concrete structures. Piping penetrations are nevertheless inspected by the normal visual inspection of structural elements.
DE-19 | DE - 19 | Finland | Germany | 04. Concealed pipework | 47 | Concerning the scope of AMP, what is the amount of concealed pipelines in concrete in NPPs and other nuclear facilities? | Licensee | For NPP in a few cases the service water system pipework for normal power operation is made from prestressed concrete. Concerning the scope of the TPR, the safety relevant secured service water pipework is made of steel, see chapter 4.1.1a. The well water supply line of RR FRM II is buried, with the exception of the passage from the well house and into the pump cellar. The diesel tank line is buried, with the exception of its passage into the emergency diesel building. In both cases, the lines run in concrete over a length of approx. 1 m.
DE-20 | DE - 20 | Finland | Germany | 04. Concealed pipework | 60 | What are the corresponding safety and operation challenges, like maintaining safe shutdown condition, flooding risks, etc. connected to AMP? | Licensee | The task of these systems is to remove excess heat from the secured intermediate coolant circuit under all operational and emergency conditions, see also chapter 4.1.2 a). A large break of the multiple-redundant pipes shall be avoided by the ageing management. The functional capability and the compliance with the protective goals are not questioned due to local leaks.
DE-21 | DE - 21 | Finland | Germany | 07. Concrete containment structures | 92 | What is the procedure, frequency and ac-ceptance criteria of BWR containment leak tightness tests related to AMP? | Licensee | Please look for details in KTAs 3401.4, 3403, 3405 and KTA 3407. All standards are available on the internet.
DE-22 | DE - 22 | Finland | Germany | 07. Concrete containment structures | 94 | How monitoring systems are used in measuring creeping and tension losses of pre-stressed BWR containment related to AMP? | Licensee | The licensee uses visual inspections to evaluate creeping and tension losses of pre-stressed BWR containment related to AMP. The ageing phenomenas are given in section 7.1.2a particularly with regard to subsection "Loss of prestress of prestressing steel (only BWR)". Losses of prestress are already taken into account in the dimensioning of the initial tension. Tension losses as damage phenomena during the course of the ageing process (creep and shrinkage, prestressing steel relaxation) are detectable from an increase of deformations and thus from initial cracking.
DE-23 | DE - 23 | Czech Republic | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | "The process orientation of ageing management ensures defined responsibilities for SSCs also across different technical departments." Assignment of responsibilities within the licensee’s organisation to ensure an overall AMP is developed and implemented is not clear from the document. Could you please provide us more details? | Licensee | All work is organized and carried out in the NPPs based on an integrated management system. The associated processes define the responsibilities of all organizational units and their collaboration. The ageing-management process is controlled and coordinated by an ageing manager. The assessment of experiences regarding SSCs are performed by specially designated system engineers. The external experience feedback is also evaluated by these engineers within the established processes of the integrated management system.
DE-24 | DE - 24 | Czech Republic | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | "In safety standard KTA 1403, the specific extent of safety-related SSCs is divided as follows:  mechanical systems and components  SSCs of electrical and I&C systems  structures including structural elements  auxiliary and operating supplies of the SSCs" From the document it is not clear which methods are used for identifying SSCs within the scope of overall AMP. Could you please provide us more details? | Licensee | The KTA 1403 has defined a procedural framework for the implementation, the database and the reporting of ageing-management. It is reported on damage mechanisms and the effectiveness of ageing-management of SSCs. By definition, the SSCs include all safety-related mechanical components and systems, electrical and instrumentation and control equipment and components as well as structural components.
DE-25 | DE - 25 | Czech Republic | Germany | 02. Overall Ageing Management Programme requirements and implementation | Chapter 2.3.1. a | From the document it is not clear if any indicators are used to assess the effectiveness of the ageing management process. Could you please clarify how do you assess the effectivness of this proces? | Licensee | The annual status reports are presented to the regulatory body and their TSO in the form of an annual review. Inspections can complement the review. During the year, ISI and the maintenance measures on the SSCs are randomly supervised by the regulatory body and its TSO. Explicit indicators for the ageing-management process or its results are not recorded. An essential evaluation criterion for the effectiveness of the ageing-management process are the results of the internal experience feedback.
DE-26 | DE - 26 | Switzerland | Germany | 03. Electrical cables | 34 | Textline21:‘… of safety-related SSCs ..., only electrical cables with polymer insulation are used.’ Are there no mineral-isolated cables in use? | Licensee | Mineral-isolated cables are not used for signal- or energy-transmission. Partly inside components - in these cases mineral-isolated cables are taken in consideration to the components itself.
DE-27 | DE - 27 | Switzerland | Germany | 07. Concrete containment structures | 104 | How can it be verified that the "...prestressed structure of the BWR does not require monitoring for the planned operation ..."? Are there inspection concepts applied at prestressed containment walls in BWRs? (monitoring of prestress losses, corrosion potential) | Licensee | All ageing phenomena can be surveilled by regular visual inspections, see answer to question DE-22. | ref to DE-22
DE-28 | DE - 28 | Switzerland | Germany | 07. Concrete containment structures | 105 | How are acceptance criteria for the inspected concrete structures defined? (crack width and depth, crack patterns, carbonation depth, prestress loss, ...) | Licensee | What is also essential for the assessment is to identify cracks change over time. Possible crack widths not exceeds limits given by DIN 25449 or DIN 25459. Section 7.2a "The design rules, which also ensure the durability of the structures, had already matured at the time of construction. Even then, the state of the art in science and technology behind these design rules essentially corresponded to the current level of knowledge and was already taken into account conservatively in their preparation." If cracks were observed, evaluation would be carried out by expert judgement with involvement of independent experts acting in support of the regulatory body. The crack patterns, including the crack width and length on the component surface, are determined and documented.
DE-29 | DE - 29 | Switzerland | Germany | 07. Concrete containment structures | 105 | How is the collection and investigation of concrete and reinforcing steel from structural interventions (reconstruction, partial demolition, ...) organized? | Licensee | Licensee does not see additional benefit in structural interventions.
DE-30 | DE - 30 | Switzerland | Germany | 07. Concrete containment structures | 105 | How are the structures and the structural elements assessed which are inaccessible for visual inspections (indirect/indicative methods)? | Licensee | Structural elements are sufficiently accessible to judge the impact of all possible ageing mechanisms by visual inspections.
DE-31 | DE - 31 | Switzerland | Germany | 07. Concrete containment structures | 105 | KTA 1403 requires the condition assessment for different types of structures and structural elements, such as secondary structures, anchorage elements, waterproofing sealings, drainage, coatings, fire-retarding sealings, etc. Are all these types included in the inspection programs? | Licensee | Basis of AMP is the knowledge of all possible ageing mechanisms. Possible ageing mechanisms are described for all different types of structures and structural elements. All possible elements such as anchorage elements, waterproofing sealings, drainage, coatings, fire-retarding sealings are addressed with there possible ageing mechanisms and inspected within AMP.
DE-32 | DE - 32 | Switzerland | Germany | 07. Concrete containment structures | 105 | Are there specific testing and inspection requirements for safety related anchorage elements? (e.g. pull-out tests with acceptance criteria) | Licensee | Installed anchors are inspected by visual inspections.
DE-33 | DE - 33 | Switzerland | Germany | 07. Concrete containment structures | 105, 107 | Are concrete structures monitored by visual inspections only? Do you not consider using onsite instrumental inspections and laboratory material testing as part of the aging management? (e.g. carbonation progress, corrosion potential of reinforcement, material strength, concrete cover depth, ...) | Licensee | Yes, concrete structures are monitored by visual inspections only. Please see answer to question DE - 15 and DE - 22. | ref to DE-15 & DE-22
DE-34 | DE - 34 | Czech Republic | Germany | 03. Electrical cables | 34 | "Other sources of knowledge regarding the ageing management for cables are: • contractor reports (VGB system for the assessment of contractors)" (3.1.2) Could you please give us brief information about the content of the report? | Licensee | The reports contain the manufacturers' statements on the maintenance of the qualification and also on the operating experience from the manufacturer's point of view. The reports are part of the Quality-Assurance-System, they are based on KTA-standard KTA 1401.
DE-35 | DE - 35 | Bulgaria | Germany | 03. Electrical cables | p.39 | Would you please share with us your experience of how was monitored the technical condition of the electrical cables penetrations and electrical cables hermetic penetrations? | Licensee | Cable-penetrations were not subject of the TPR and not part of the technical specifications of TPR. The ageing management of cable-penetrations (containment-penetrations) are investigated in another VGB working group.
DE-36 | DE - 36 | Bulgaria | Germany | 03. Electrical cables | p.34 | With the aim to evaluate the ageing mechanisms for electrical cables, would you please clarify whether you have used special facilities/laboratories for artificial ageing, where cables may be affected by radiation exposure as well? | Licensee | The radiological ageing of cables is done in the cable depository in the NPP (see also Figure 3-2 of the German NAR). If necessary, additional pre-ageing is performed in testing-institutes or laboratories under use of Co60-radiation-sources.
DE-37 | DE - 37 | Finland | Germany | 05. Reactor Pressure Vessels | Chapter 5.3a | What are the main safety and operation challenges associated with AMPs. For example, are safe shutdown conditions addressed in a proper way? | Licensee | There are no operational challenges associated with AMP for the RPV in German plants. The ageing management assessment demonstrates big margins for the RPV. This also includes the P-T limiting curve, which is known to be sometimes challenging in some foreign reactor designs. There are also no safety challenges including brittle fracture assessment under all operational and emergency conditions.
DE-38 | DE - 38 | Slovenia | Germany | 03. Electrical cables | 34 | Why does not the report consider R&D programmes, objectives, contents, internal and external operating experience (page no. 34). | Licensee/Regulator | As mentioned in section 3.1.2, R&D programmes are used as one possible sources of knowledge regarding the ageing management for cables. These R&D-programmes are part of the operators AM-programmes. Their results are owned by the operators. Internal and external operating experience is another source of knowledge. This includes overall maintenance inspection outage reports, GRS information notices (WLN), reportable events from the operator's plant and from other German plants, event reports from nuclear power plants outside Germany, national and international research projects, evaluation of experience by the manufacturers, and exchange of experience among the operators.
DE-39 | DE - 39 | Slovenia | Germany | 03. Electrical cables | any | Why does not the report discuss the acceptance criteria frequencies? | Licensee | The activities are part of the periodic testing programs during the lifetime of the NPP. Acceptance criteria are given by standards or the manufacturers qualified specifications.
DE-40 | DE - 40 | Slovenia | Germany | 03. Electrical cables | 39 | Why does not the report discuss third party certification organisations (page no. 39). | Licensee | The NPP licensees are working together with third-party technical certification organisation, their contribution is presented as licensee activities.
DE-41 | DE - 41 | Slovenia | Germany | 03. Electrical cables | 32 | The report states that only cables which supply safety-related SSC are considered in AMPs. Does AMP also consider cables which supply important non-safety related SSC (e.g. Fire Protection System…) (page no. 32)? If not, how are they treated then? | Licensee | The results of the AM on SSC-cables are applied on non-safety-related cables and vice versa. (see 3.1.1a, page 32)
DE-42 | DE - 42 | Slovenia | Germany | 03. Electrical cables | 32 | How many cables are buried or inaccessible (page no. 32)? | Licensee | Only a few SSC-cables are inaccessible, if ducted to outlying buildings.
DE-43 | DE - 43 | Slovenia | Germany | 03. Electrical cables | 34 | What kind of problems/operating experience do you have with buried or inaccessible cables (page no. 34)? | Licensee | No specific ageing-problems are reported according to these cables.
DE-44 | DE - 44 | Slovenia | Germany | 03. Electrical cables | 39 | Who are third party certification organisations in Germany (page no. 39)? | Licensee/Regulator | The NPP licensees are working together with third-party technical certification organisation, their contribution is presented as licensee activities.
DE-45 | DE - 45 | Slovenia | Germany | 03. Electrical cables | 39 | Why does not the report (Chapter 3.1.3) consider acceptance criteria, frequencies according to TS (page no. 39)? | Licensee | The activities are part of the periodic testing programs during the lifetime of the NPP. Acceptance criteria are given by standards or the manufacturers qualified specifications.
DE-46 | DE - 46 | Slovenia | Germany | 04. Concealed pipework | 51 | - Section 4.1.2, page 51: Is there any involvement in other R&D programmes regarding pipe aging management, apart from the gained experience from older nuclear and fossil power plants? | Licensee | According to 2012 revised German atomic law, the last operating German NPPs have to finish operation end of 2023, which is in less than six years from now. Taking the good operational experience including from the older German NPP now out of service into account, there is no more need to involve in any R&D program.
DE-47 | DE - 47 | Czech Republic | Germany | 05. Reactor Pressure Vessels | chapter 5 | TPR is aimed on reactor pressure vessel, so probably, the containers were exluded from TPR because of required scope. Are containers selected equipment (safety classified) or not? Do you evaluate the technical status of the reactor vessel? If yes, how? | Licensee | According to the WENRA Technical Specification for the National Assessment Reports, the required scope of chapter 5 is the RPV. Chapter 5 contains all relevant information about the technical status of the RPV.
DE-48 | DE - 48 | Netherlands | Germany | 02. Overall Ageing Management Programme requirements and implementation | 2.2 | Please explain in sufficient detail how SSG-10 has been implemented in the German system of AM. | Licensee/Regulator | In Germany, ageing management for research reactors takes place within the scope of maintenance (in-service inspections, plant inspections) as described in the NAR, following safety standard KTA 1403 "Ageing Management for Nuclear Power Plants" using the aspects of ageing management mentioned therein as a basis to identify a possible need for modification and for ensuring compliance with the state of the art in science and technology. The requirements of safety standard KTA 1403 is basically in line with the recommendations in the IAEA Specific Safety Guide No. SSG-10 “Ageing Management for Research Reactors”.
DE-49 | DE - 49 | Netherlands | Germany | 02. Overall Ageing Management Programme requirements and implementation | 2.3.1b | Please elaborate on the appropriate application of KTA1403 to RR. Why has there been no application of KTA1402 and or SSG-10 allthough mentioned in 2.2? | Regulator | The KTA safety standards are principally also applied by the operators of research reactors (see Figure 2-1 "National regulatory pyramid”).While they are primarily applicable to nuclear power plants, the competent licensing and supervisory authorities require the operators of research reactors to apply the KTA safety standards as appropiate. Accordingly, the research reactors have implemented ageing management according to KTA 1403. Likewise, an “Integrated Management System for the Safe Operation of. Nuclear Power Plants “ according to KTA 1402 or "Safety Requirements for Nuclear Power Plants" has been implemented in the research reactors, as it is also required by § 7c(2)(1) of the Atomic Energy Act (AtG).
DE-50 | DE - 50 | Netherlands | Germany | 02. Overall Ageing Management Programme requirements and implementation | 2.3.2a | Please elaborate on the international R&D in which Germany participated or from which Germany uses the results to improve the AM | Licensee | Experts from German operators exchange views on all potentially safety-related topics in VGB working groups. This exchange also includes information from international conferences. Furthermore, agreements with the plant manufacturer were made about informing the operators about new safety-related findings.
DE-51 | DE - 51 | Netherlands | Germany | 02. Overall Ageing Management Programme requirements and implementation | 2.4 | How is Germany using IRS and IRSRR? Which organisations are involved? | Regulator | Germany is involved in various international activities for the exchange of operating experience. These include the participation in the International Reporting System (IRS) and Incident Reporting System for Research Reactors (IRSRR). The expert organisation GRS evaluates systematically the events reported in the IRS with regard to their applicability to German installations. On behalf of the BMU, GRS submits the results of their analyses to the nuclear licensing and supervisory authorities of all Länder with nuclear installations, the expert organisations, the licence holders of the nuclear installations and the manufacturers in monthly reports. Should the analyses of reportable events at foreign nuclear installations with current or potential safety relevance show an applicability to German nuclear installations, GRS prepares information notices on behalf of the BMU. After approval by the BMU, these are also submitted to all interested parties mentioned above. For more information please see German CNS report 2017. The IRSRR reports are sent to the licensing and supervisory authorities of the Länder and to the operators of the research reactors by GRS on behalf of the BMU. The licensing and supervisory authorities of the Länder requested the operators of the research reactors to check these reports for applicability and to report to the Land authorities, e.g. within the framework of regulatory meetings.
DE-52 | DE - 52 | Netherlands | Germany | 02. Overall Ageing Management Programme requirements and implementation | 2.7b | In the NPP community the change to an integrated overall AMP has been made. In line with this development, in many countries SSG-10 is currently considered to be the "state-of-the-art" for RRs and this is (or has been) an incentive for changing or having changed the "old" AM of RRs. Please explain why Germany is not following that trend. | Regulator | The research reactors in Germany basically apply the KTA safety standards. While they are primarily applicable to nuclear power plants, the competent licensing and supervisory authorities require the operators of research reactors to apply the KTA safety standards mutatis mutandis. Accordingly, the research reactors have implemented the ageing management according to KTA 1403. Since the requirements of KTA 1403 are basically in line with the recommendations of the des IAEA Specific Safety Guide No. SSG-10 "Ageing Management for Research Reactors", it is currently not planned to adapt ageing management specifically according to the SSG-10.
DE-53 | DE - 53 | Netherlands | Germany | 03. Electrical cables | section 3.1.2.a | In section 3.1.2.a, 'national and international research projects' are given as source of knowledge regarding ageing mechanisms for cables. Please elaborate which specific projects are meant. | Licensee | Part of the AM is check of the state of the art by using the PCDA-cycle. If findings relevant to AM are given, the results are taken into the AM-process. Examples für research projects are cable-depository and the tracing of life-cycle curves (see page 38 fig 3-1)
DE-54 | DE - 54 | Netherlands | Germany | 03. Electrical cables | section 3.1.2.a | In section 3.1.2.a, it is mentioned that relevant degradation mechanisms are determined on the basis of manufacturer's specifications, which in turn are based on national and international regulations. Please specify, for example in the form of listing of the main documents. | Licensee | The applied standards are KTA-regulations, IEC, EN, DIN-VDE, IAEA.
DE-55 | DE - 55 | Netherlands | Germany | 03. Electrical cables | section 3.1.3.a, p.39 | In 3.1.3.a, is stated that since the electrical cables are simple and robust components for which extensive operating experience also exists from the non-nuclear field, a comprehensive application of the methods is not required. Does this conclusion holds when it is taken into account that conventional circumstances do not involve effects specific for nuclear applications, such as radiation induced material degradation? | Licensee | The qualification-procedures for safety-related cables under harsh environment-conditions comprise tests of radiation induced material degradation.
DE-56 | DE - 56 | Netherlands | Germany | 03. Electrical cables | section 3.1.2.a | A description of monitoring, testing, and inspection activities is given in section 3.1.2.a. The acitivties are described in a clear and concise manner. What are the activity frequencies and acceptance criteria? | Licensee | The activities are part of the periodic testing programs during the lifetime of the NPP. Acceptance criteria are given by standards or the manufacturers qualified specifications.
DE-57 | DE - 57 | Netherlands | Germany | 04. Concealed pipework | p.52; p.59 | How often ageing mechanisms that require management (and their significance) are evaluated? | Licensee | AM is a continuous improvement process concerning to a closed PDCA cycle in accordance with KTA 1403. Therefore it´s a living process with an updated knowledge base.
DE-58 | DE - 58 | Netherlands | Germany | 04. Concealed pipework | 4.1.1, p.47 | Is there any difference in ageing management of the concealed pipework in PWRs and BWRs? | Licensee | As systems are comparable, there is no difference needed concerning AMP.
DE-59 | DE - 59 | Netherlands | Germany | 04. Concealed pipework | p.54, 4.1.3a | What are the frequencies for inspections by walkdowns of accessible area of pipework? Does it concern all group M2 systems (p.47)? | Licensee | Frequencies for German NPP M2 system walkdown inspections have been implemented and approved in the plant specific test instructions on a plant and system individual basis.
DE-60 | DE - 60 | Netherlands | Germany | 04. Concealed pipework | p. 58, 4.1.4a | What are the remedial actions to be taken? Only replacement or also repair? | Licensee | Both actions are possible. Decision depends on nominal diameter, leak size and the safety-related significance.
DE-61 | DE - 61 | Netherlands | Germany | 07. Concrete containment structures | 7.3a | Does the regulator limit the basis for its assessment to KTA1403 or are OEF and other regulations also used in the evaluation of the quality and measures? | Regulator | KTA 1403 describes the ageing management process. The KTA safety standards for concrete structures define the design requirements to be met and the inspections to be performed within the framework of regulatory supervision for which the relevant conventional regulations are referred to. These requirements are also the basis for the assessment of the quality requirements in the context of ageing management.
DE-62 | DE - 62 | RPV expert group | Germany | 05. Reactor Pressure Vessels |  | NDE of welds at the RPV bottom for BWR are carried out from the outside of the RPV. What methods are used? Can the used methods detect cracks close to the inside surface? What are the detections limits for a crack like defects? | Licensee | NDT of RPV bottom welds is carried out by rail mounted mechanized UT technique. This NDT technique is designed and qualified to detect safety relevant cracks including close to the inside surface. The Inspection technique is approved by the regulatory body. The requirements of KTA 3201.4 are fulfilled. See also Ch. 5.1.3 a) of the German report.
DE-63 | DE - 63 | RPV expert group | Germany | 05. Reactor Pressure Vessels |  | How are the test intervals between the periodic non-destructive tests determined? | Licensee | Inspection intervals are fixed in the plant specific test instructions of German nuclear power plants based on KTA 3201.4 requirements, see German report chapter 5.1.3, tables 5.2 and 5.3.
DE-64 | DE - 64 | RPV expert group | Germany | 05. Reactor Pressure Vessels |  | What are the requirements for the laboratories that perform the periodic non-destructive tests? | Licensee | Requirements are defined in KTA 3201.4 and referred standards as DIN 25435, see chapter 5.1.3 a) of the German report. This includes requirements to the NDT personnel according to DIN EN ISO 9712.
DE-65 | DE - 65 | RPV expert group | Germany | 05. Reactor Pressure Vessels |  | What type of defects are used for the qualification if the non-destructive test methods? | Licensee | Qualification of NDT is based on KTA 3201.4 requirements, see page 77 and 81 of the German report. For more details see KTA 3201.4, for example chapters 4.1.1 "Selection of test procedures and techniques" and 4.1.2 "Suitability of test procedures"
DE-66 | DE - 66 | RPV expert group | Germany | 05. Reactor Pressure Vessels |  | The purpose for the withdrawal of capsules with irradiated specimens are to measure changes of mechanical properties of the test specimens and to evaluate the fluence monitors to calibrate the fluence calculations. There is only few capsules with irradiated specimens in the PWRs and BWRs. How is the calibration of the fluence calculation done? Are external dosimetry used? Have the P-T limiting curves been updated recently? Which methods are applied for the analysis of the P-T limiting curves? | Licensee | The irradiation surveillance program is performed according to KTA 3203, see page 86 of the report. According to KTA 3203, Neutron detectors inside the capsules containing irradiation exposure specimens are used to verify the fluence calculation. The P-T limiting curves of the RPV are evaluated according to KTA 3201.2 chapter 7.9 (procedure is in line with procedure of ASME XI, App. G). Update of P-T limiting curves is in general not necessary for the operating German NPP because End-of-life brittle to ductile transition temperature (RT-NDT) is much lower than assumed in the design, see chapter 5.1.3 page 87 of German report.
DE-67 | DE - 67 | RPV expert group | Germany | 05. Reactor Pressure Vessels | P68 | 5.1.1 states that “…of the group M1 according to KTA 1430…”. In this case, it is needed to clarify what group “M1” means. Corresponding clarifications should be provided as an answer. | Licensee | Definition of Group M1 components: (see chapter 4, page 47 of the German report and KTA 1403) a) Group M1 shall comprise all components and component parts whose failures are specified as being impermissible. b) Based on plant specific conditions, additional components shall be integrated into the extent of ageing-related observation of Group M1 if, during full power operation or during mitigation of design basis accidents, a failure of these components is not covered by plant design.
DE-68 | DE - 68 | RPV expert group | Germany | 05. Reactor Pressure Vessels |  | Is it possible to clarify which TLAAs are used for RPV safety substantiations? | Licensee | Main ageing mechanisms (page 74): - fatigue (e.g. mechanical and thermal loads, closing studs), - irradiation embrittlement, - corrosion AM assessment: Fatigue analysis (page 86 of the report), design by analyses of normal, upset, emergency and faulted conditions (page 70/71), fracture analyses (ideal thermal shock analysis and Pressurized Thermal Shock analyses), page 71, irradiation surveillance program (page 71 and 86f), ISI and other monitoring results (page 77ff) are assessed and also P-T limiting curve. Irradiation program demonstrates very low End-of-Life brittle to ductile transition temperature (RT-NDT), see page 87 of the report. Result: the ageing management assessment demonstrates big margins for the RPV.
DE-69 | DE - 69 | RPV expert group | Germany | 10. References |  | 1.3.2 Almost all documents in chapter “10 References” (e.g. /BET17/, /DAF 86/, /DAF 89/, /KTA 00/, /KTA 01/, /KTA 10/, /KTA 12/, /KTA 13a/) are written in the German language and this situation does not allow correct understanding of their contents. It is needed to get the answer on this comment and additional list of references in English. | Regulator | The KTA Program of Standards is available online (http://www.kta-gs.de/common/regel_prog1.htm). Most of the standards are also provided in English.
DE-70 | DE - 70 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 94 | KTA 1403 requires a structure condition report to be provided every 10 years. Is there a common structure and layout for all NPPs? Are the detailed inspection reports for the safety related structures included in the structure condition report? | Licensee/Regulator | The objective of the structure condition report is to demonstrate that all safety-relevant buildings, partial structures, structural systems and components are assessed with regard to their ageing condition. A common layout is not required in the KTA 1403. The inspection reports of the individual work sections are part of the respective annual status report or subject of the construction supervision meeting and/or the inspection reports of the individual buildings are summarised in a structure condition report at intervals of ten years and submitted separately to the supervisory authority.
DE-71 | DE - 71 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 104 | How can it be verified that the "...prestressed structure of the BWR does not require monitoring for the planned operation ..."? Are there inspection concepts applied at prestressed containment walls in BWRs? (monitoring of prestress losses, corrosion potential) | Licensee | Please see answer to question DE - 27 | ref to DE-27
DE-72 | DE - 72 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 105, 107 | Are concrete structures monitored by visual inspections only? Do you not consider using onsite instrumental inspections and laboratory material testing as part of the aging management? (e.g. carbonation progress, corrosion potential of reinforcement, material strength, concrete cover depth, ...) | Licensee | Please see answer to question DE - 33 | ref to DE-33
DE-73 | DE - 73 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 105 | How are acceptance criteria for the inspected concrete structures defined? (crack width and depth, crack patterns, carbonation depth, prestress loss, ...) | Licensee | Please see answer to question DE - 28 | ref to DE-28
DE-74 | DE - 74 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 105 | How are acceptance criteria for the monitored settlements? What is the long term experience on settlements? | Licensee | Settlement acceptance criteria have been taken into account in the design. Predicted settlement measurements are much higher then the real measured values for all plants. After commissioning of the plant settlements were measured once a year. Because of the very positive results of these measurements the interval was increased plant specifically.
DE-75 | DE - 75 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 105 | How is the collection and investigation of concrete and reinforcing steel from structural interventions (reconstruction, partial demolition, ...) organized? | Licensee | Please see answer to question DE - 29 | ref to DE-29
DE-76 | DE - 76 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 105 | How are the structures and the structural elements assessed which are inaccessible for visual inspections? (indirect/indicative methods?) | Licensee | Please see answer to question DE - 30 | ref to DE-30
DE-77 | DE - 77 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 105 | KTA 1403 requires the condition assessment for different types of structures and structural elements, such as secondary structures, anchorage elements, water-proofing sealings, drainage, coatings, fire-retarding sealings, etc. Are all these types included in the inspection programs? | Licensee | Please see answer to question DE - 31 | ref to DE-31
DE-78 | DE - 78 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 105 | How are the fire protecting structural elements monitored? | Licensee | All structural elements of safety related buildings have to be inspected at least once in 10 years. This includes fire protecting structural elements.
DE-79 | DE - 79 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | 105 | Are there specific testing and inspection requirements for safety related anchorage elements? (e.g. pull-out tests with acceptance criteria) | Licensee | Please see answer to question DE - 31 | ref to DE-31
DE-80 | DE - 80 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | All | ch. 2 & 7: Please clarify if the German nuclear power plants participate in any reserch and development programmes? | Licensee | Research on concrete containment structures and their ageing was comprehensively done before construction begins and the results were deeply analysed in the licensing process of the plants. No safety relevant insights indicating a need of new research have been found so far.
DE-81 | DE - 81 | Concrete containment PCPV expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 13, 14 & 16 | Description of the overall ageing management programme - This section describes the central incident reporting and evaluation office ZMA and the information notices (WLN) as the systems for German operators to exchange experience. However, these two bodies seem to report incident and reportable events. Do the German operators have a vehicle to meet and exchange good practices and technical experiences? Please provide more information regarding the VGB | Licensee | As part of the cooperation within the VGB, the exchange of plant-specific experiences takes place in various working groups (e.g., AG "Component Integrity", "Machine and Process Engineering", "Electrical and Control Engineering").
DE-82 | DE - 82 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | All | Chapter 7 seems to be heavily based on visual observations of the concrete structures, does the German operator carry out trending studies, TLAA or other type of tests, such as settlement tests or electronic strain measurements? | Licensee | Yes, the ageing phenomenas on concrete structures are in first line controlled by visual inspections. Furthermore settlements are monitored. The added value of strain measurements was evaluated. Together with an integral leak rate test, strain gauge measurements were performed. Other insights additional to what visual inspections for possible cracks that are associated with tendon failure are able to reveal could not be gained. Therefore strain measurements were not implemented in AMP.
DE-83 | DE - 83 | Concrete containment PCPV expert group | Germany | 07. Concrete containment structures | All | Chapter 7 provides a detail explanation of the degradation mechanism. Please could you provide more information on the acceptance criteria? How changes on the design conditions are taken into account in the AMP? | Licensee | see answer to question DE-28 | ref to DE-28
DE-84 | DE - 84 | Concealed pipework expert group | Germany | 04. Concealed pipework | 61 | Has the regulatory body performed periodic inspections in each NPP to control the ageing management acitvities of the licensee? Also to control the results that have been described by the licensee in its annual report (paragraph 4.3 a) | Regulator | Yes, it has. Supervision of ageing management is anchored in the annual inspection programme. In addition to random inspections by the supervisory authority or by the authorised expert, expert inspections are also carried out to a large extent e.g. in connection with in-service inspections, maintenance and modifications. In case of findings with indications of ageing effects, this will be communicated to the supervisory authority.
DE-85 | DE - 85 | Concealed pipework expert group | Germany | 04. Concealed pipework | 57 | “For non-coated pipelines or pipework areas, ultrasonic wall thickness measurement of test sections accessible from the outside is a suitable test method to obtain a representative statement about the presence of a local damage. The test results can also be transferred to buried pipework areas with the same design of the coating system.” Please provide details of how you account for the differences in environment between the buried and accessible regions of pipework. For example additional moisture levels and soil pH values may result in differing corrosion rates to exposed pipework. | Licensee | As described in ch. 4.1.2 a) the relevant ageing mechanisms are corrosion mechanisms from inside. Transfer of inspection results from ultrasonic wall thickness measurement is possible due to same environmental conditions at inner surface of inspected pipes/systems with same design of the inner coating system. The design of the outer coating systems is not relevant.
DE-86 | DE - 86 | Concealed pipework expert group | Germany | 04. Concealed pipework | 58 | Section 4.1.4.a – The report states that “Remedial actions to restore the required quality level are carried out in the event of detected leaks.” Please can you provide some detail of any additional remediation that takes place more pro-actively, i.e. before there is evidence of a leak? | Licensee | As described in ch. 4.1.4 a) in some older German nuclear power plants, condition-oriented replacement measures of complete buried lines have already been carried out. Here, the non-coated pipes of the plant installation were replaced by new pipes coated with cement mortar lining on the inside.
DE-87 | DE - 87 | Concealed pipework expert group | Germany | 04. Concealed pipework | N/A | General comment - A very detailed and comprehensive description of the strategy used to manage the integrity of concealed pipework. | - | Thank you very much for this comment.
DE-88 | DE - 88 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | The Aging Management is considered a part of the Periodic Safety Review for the NPP. Are the same requirements for PSR applicable for research reactors?? | Regulator | Since 2010, all research reactors (including homogeneous zero-power reactors) are required by law to carry out a PSR every ten years (according to § 19a(3) of the Atomic Energy Act – AtG). Larger facilities (FRM II and BER II) have already been required before to carry out periodic safety reviews according to specific requirements/ancillary provisions from the licensing procedure. For the German research reactors, periodic safety reviews are carried out in analogous application of the corresponding regulatory guidelines of the Federation and the Länder. Here, the ageing analysis of SSCs is part of the deterministic safety status analysis.
DE-89 | DE - 89 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | The Partial Licenses are issues to RRS FRM II, BER II, and FRMZ. What is the difference between a full license and a partial license? | Regulator | § 18 of the Nuclear Licensing Procedures Ordinance (AtVfV) stipulates that a partial licence may be granted upon application, provided that a provisional examination has shown that the licensing prerequisites will be fulfilled with respect to the construction and operation of the installation as a whole and further provided that the applicant has a legitimate interest in the granting of such a partial licence. There is no difference whether a licence licenses the construction and operation of the research reactor, or whether the construction is licensed by a partial licence and the operation by another partial licence.
DE-90 | DE - 90 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 23 | The information notices on operation feedback from NPP is distributed to all NPPs by VGB and GRS. Are those information distributed also to research reactors? | Regulator | Yes, information notices are also distributed to research reactor licensees based on the relevancy and applicability of the information noticed.
DE-91 | DE - 91 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 24 | Research projects were initiated to clarify the findings of experience at research reactors. Are the results of these publicly available ? | Licensee/Regulator | These are internal research projects of the operators. The results are generally not publicly available.
DE-92 | DE - 92 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 23 | The information notices on operation feedback from NPP is distributed to all NPPs by VGB and GRS. Are those information distributed also to research reactors? | Regulator | Yes, information notices are also distributed to research reactor licensees based on the relevancy and applicability of the information noticed.
DE-93 | DE - 93 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 31 | The graded approach is implemented for RR. Is there a guide on this graded approach? | Regulator | There is no guide on graded approach. Principally grading is performed based on the single case decision. Each Länder authority is responsible to concretize the frameworks for research reactors under their nuclear control. Nevertheless, there is an advice on, how to classify the research reactors depending on their individual risks potential. Furthermore, in the special case of regulations for periodic safety review the suggestions on its applicability for different research reactor groups are given.
DE-94 | DE - 94 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation |  | General comment As for other countries, large amounts of text are reused in different chapters, instead of referring to the first time used in the report, making reading tedious and time consuming | - | Thank you for your comment
DE-95 | DE - 95 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 9 | The Safety Requirements for Nuclear Power Plants /SIC 15/ include requirements for an integrated management system (IMS) that must also take into account objectives and requirements in terms of ageing. A specific requirement for levels 1 to 4 of the defence-in-depth concept is to draw up a monitoring concept for the detection of ageing degradation. Furthermore, it is required that precautions are to be taken against failure due to fatigue, corrosion and other ageing mechanisms, as far as ISIs cannot be performed to the required extent. | - | Thank you for your comment
DE-96 | DE - 96 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 10 | The Interpretations of the Safety Requirements for Nuclear Power Plants /INT 15/ also include requirements for ageing management. Accordingly, they stipulate to use operating experience for ageing management. The central requirement is laid down in Section 2.5.1 (9) of the Interpretation I-2 of the Safety Requirements for Nuclear Power Plants: “An ageing management system shall be implemented for the systematic detection, monitoring or prevention of ageing effects on the integrity of the components.” | - | Thank you for your comment
DE-97 | DE - 97 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 10 | Are the standards of KTA reviewed with a fixed frequency, or are they reviewed when new versions/standards within their scope are published? The safety standards of the Nuclear Safety Standards Commission (KTA) have the task of specifying safety requirements in order to achieve the protection goals laid down in the AtG and in the Radiation Protection Ordinance (StrlSchV) and further concretised in the Safety Requirements for Nuclear Power Plants to be able to prove that the necessary precautions have been taken in the light of the state of the art in science and technology to prevent damage resulting from the construction and operation of the facility (§ 7(2)(3) AtG). The KTA safety standards are reviewed to ensure that they are up to date and revised if necessary. Here, in particular, the further development of the international rules and regulations is taken into account. | Regulator | The KTA safety standards are subject to regular reviews. The texts of the adopted safety standards are reviewed at least every five years in accordance with the statutes and, where required, adapted to the state of the art in science and technology in terms of the necessary precautions to prevent damage. It is planned to review all KTA safety standards again until the spring of 2018 to achieve validity in accordance with the statutes until at least the end of 2022 (end of power operation of the last nuclear installations in Germany).
DE-98 | DE - 98 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 10 | Interesting that this standard also includes “basic qualification and maintenance of competence and know-how of the personnel” in ageing management The general requirements for the integrated management system from the safety requirements are concretised in safety standard KTA 1402 /KTA 12/ The special requirements for ageing management were defined in safety standard KTA 1403 /KTA 17/. KTA 1403 applies to the safety-related SSCs, including the respective auxiliary and operating supplies, specified in the plant-specific licensing documents and operating procedures, of nuclear power plants still in operation. It deals with physical ageing taking into account new findings with regard to ageing processes. This safety standard applies, furthermore, to the procedures of ageing-management regarding the basic qualification and maintenance of competence and know-how of the personnel and, also, to the documentation and the data from information and operation management systems. | - | Thank you for your comment
DE-99 | DE - 99 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 10 | Accordingly, the licensees have to set up a systematic and knowledge-based ageing management system as part of the integrated management system, which shall be organised, documented, assessed and updated. Ageing management shall be implemented in a process-oriented manner and integrated into the operational processes. For this purpose, the following basic requirements shall be implemented by the operator:  The extent of ageing-related observations shall be defined and documented. The observations shall include - ageing of the auxiliary and operating supplies of the respective SSCs, and - ageing-related influences on the data from information and operation management systems including documentation.  The procedures of ageing management shall ensure that safety-related degradation mechanisms are identified. The causes and/or consequences of these degradation mechanisms shall be controlled by appropriate measures.  The further development of the state of the art in science and technology shall be monitored and assessed.  The measures taken with respect to ageing management and the results achieved shall be documented and assessed. Corresponding reports shall be drawn up at regular intervals. Ageing-management shall be continuously optimised based on the assessments carried out. Impermissible deviations from the required quality shall be eliminated. | - | Thank you for your comment
DE-100 | DE - 100 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 11 | It is important to also exploit experiences gained outside the area of nuclear safety components and systems Process orientation and relevant aspects of a PDCA cycle are dealt with in safety standard KTA 1402 “Integrated Management Systems for the Safe Operation of Nuclear Power Plants”. If ageing effects are detected on non-safety-related technical installations that are applicable to similar SSCs considered within ageing management, these findings shall be integrated into the ageing management. KTA 1403 contains further specific requirements for various groups of SSCs, such as mechanical systems and components, components of electrical and instrumentation and control (I&C) systems, structural elements and auxiliary and operating supplies. | - | Thank you for your comment
DE-101 | DE - 101 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | Good practice having included ageing in the PSRs as a specific issue In addition to ageing management, the periodic safety review, which has been carried out in all German nuclear power plants since the mid-nineties, comprehensively assesses the aspects of conceptual ageing. | - | Thank you for your comment
DE-102 | DE - 102 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | Albeit outside the scope of the TPR, this is a good practice In addition, KTA 1403 deals with non-technical aspects. These include the basic qualification and maintenance of competence and know-how of the personnel and, ageing of the documentation and the data from information and operation management systems. | - | Thank you for your comment
DE-103 | DE - 103 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | Even before KTA 1403 came into force, extensive measures were carried out in the German nuclear power plants with the aim of ensuring the necessary functional features of the SSCs in the required quality meeting the requirements in the long term, i.e. taking into account the effects of degradation mechanisms. In terms of the technological aspects, the measures were already applied during the design of the nuclear power plants and the manufacturing of their components and continued by regulations for the operation of nuclear power plants. | - | Thank you for your comment
DE-104 | DE - 104 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 13 | The cooperation through VGB is good practice In order to further develop the knowledge base for ensuring the required quality in the long-term, the German operators established an intensive exchange of information on technical as well as organisational issues at an early stage under the umbrella of the VGB together with the manufacturing companies. Information on and experiences with degradation mechanisms are exchanged in numerous working panels. This cooperation among the operators ensures that all relevant findings and experiences are available in a timely manner. A common, standard compendium on ageing management /VGB 97/ was established due to the work of the VGB already in the 1990s, long before the entry into force of KTA 1403. The contents of ageing management of German nuclear power plants existing at that time had been summarised in this compendium. | - | Thank you for your comment
DE-105 | DE - 105 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 13 | Since the entry into force of KTA 1403, the processes of ageing management have been uniformly implemented in German nuclear power plants. If necessary, the processes are adapted or further developed and implemented in the organisational process and workflow. The extent of ageing related observation of the SSCs has been adapted to the respective technical requirements. In addition, the degradation mechanisms that are to be considered for the individual nuclear power plant according to KTA 1403 have been catalogued and systematically characterised in terms of their relevance for the SSCs | - | Thank you for your comment
DE-106 | DE - 106 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 13 | The non-technical requirements contained in KTA 1403 have also been integrated into the ageing management process so that ageing-related impairments can also be identified and controlled in these areas in a timely manner. In accordance with the specifications of KTA 1403, these concepts were summarised in basic reports for each plant and their effectiveness is assessed annually in the form of status reports. For the structures and structural elements, this is done in a separate structure condition report, which is prepared at intervals of ten years. | - | Thank you for your comment
DE-107 | DE - 107 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 13 | A common organisation for collection, analysis and distribution of information is good practice The central incident reporting and evaluation office (ZMA) of the VGB organises the nationwide exchange of information on reportable events according to the AtSMV /ATS 92/ and other incidents in German plants and abroad. These events also include events of relevance in terms of ageing management. For these events, the ZMA organises any necessary statements of the manufacturers and distributes them to the operators, | - | Thank you for your comment
DE-108 | DE - 108 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | Reportable events of German nuclear power plants or events of foreign plants of major importance are additionally examined by GRS on behalf of the Federal Ministry for the Environment, Nature Conservation, Building and Nuclear Safety (BMUB) and, if necessary, the results distributed to the operators with recommendations of GRS within the framework of so-called information notices (WLN). | - | Thank you for your comment
DE-109 | DE - 109 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | Repeat on good practice (regulator’s conclusion on the issue?) Overall, the German operators have a comprehensive system for the exchange of experience. In combination with the process of national and international exchange of experience of the nuclear regulatory authorities, this leads to an intensive exchange of experience on ageing-related degradation mechanisms and their assessment. | - | Thank you for your comment
DE-110 | DE - 110 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | The plant-specific scope of the SSCs that are subject to systematic ageing management has also been described in basic reports on ageing management in accordance with the requirements of KTA 1403. The plant operators have assigned a plant-specific programme of measures to control ageing-related degradation mechanisms to the correspondingly defined categories or groups of SSCs. The quality requirements have also been already available in the required form in the German nuclear power plants. The related specifications are contained in the operating manuals and other plant-specific documents on the issue-related and administrative procedures. | - | Thank you for your comment
DE-111 | DE - 111 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | It worries me that operational data are only “kept for several years” and then transferred to “log-term storage”. Such information should be readily available for reference at all plants until after closure. Could you elaborate? The maintenance and ISI measures are recorded in the operation management systems or in the accompanying documents. The operating data of operational monitoring are kept for several years and transferred into an appropriate long-term storage. | Licensee | Operational data is evaluated in periodic safety reviews, e.g. during system evaluations, so that the operating experience is available in an aggregated form. For specific questions, a revaluation of the long-term stored data is possible at any time. Effective data exchanges are organised and performed by the VGB working groups. Due to differences between the plants (e.g. regarding specific components) the utilization of information from other NPPs needs to be checked and gives additional input only in certain cases.
DE-112 | DE - 112 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 15 | 2.3.2 Ageing assessment 2.3.2.a Nuclear power plants Effective management of ageing of SSCs requires a comprehensive knowledge base. It forms the basis of ageing management. The main quality features of the SSCs relevant for the knowledge base and the handling of deviations were already defined with the commissioning of the power plants. This was written down in the licensing documents, the operating manuals and the derived ISI requirements for the different SSCs and supplemented where necessary. The knowledge base also has to include knowledge of the relevant degradation mechanisms to which the SSCs are subject to. On this basis, the necessary monitoring and testing measures were derived. | - | Thank you for your comment
DE-113 | DE - 113 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 15 | This text is reused in several chapters Another part of the knowledge base of ageing management are the information and findings from the operating history of the SSCs of the respective nuclear power plant. As relevant information, the following documents and sources are used to build up the knowledge base:  quality certificates from the manufacturers  documents from the design and design assessments  results from monitoring and their assessment  results from ISIs and their assessment  results from maintenance measures  fault/defect reports and their assessment  events from the operator’s plant and from other German plants  GRS information notices  event reports from nuclear power plants outside Germany  national and international research projects (e.g. VGB/MPA projects)  evaluation of experience by the manufacturers  exchange of experience among the operators (e.g. VGB)  contractor reports (VGB system for the assessment of contractors) This information is collected with the use of databases and assessed. | - | Thank you for your comment
DE-114 | DE - 114 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 16 | The VGB working panel on electrical and I&C engineering deals with ageing management of electrical and I&C systems and the provision of a module for the knowledge base for processing ageing management of electrical and I&C systems in accordance with KTA 1403. A database was created for safety-related components, which includes their function-relevant parts, the relevant degradation mechanisms and the respective diagnostic options. This part of the knowledge base has been integrated into the database of the VGB power plant information system, which is used today in all German nuclear power plants. The linking of the components to type classes (group of components with comparable technical and ageing-relevant properties, such as rectifiers, high-voltage converters, magnetic drives, etc.) in a central catalogue of the database allows direct assignment of the degradation mechanisms to plant-specific component types. This makes it possible to check in the nuclear power plants whether the servicing and maintenance measures carried out reveal specific ageing-related degradation mechanisms. | - | Thank you for your comment
DE-115 | DE - 115 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 17 | Good practice that operators cooperate on research – and its incorporation ino recommandations In addition, research projects carried out by the operators under the umbrella of the VGB have led to a comprehensive expansion of knowledge about relevant degradation mechanisms. Where necessary, research projects were carried out by and for the nuclear power plant operators to build and expand the knowledge base on the required quality and relevant ageing mechanisms of the SSCs, and to qualify test methods that enable the detection of relevant phenomena. Basic findings on ageing were also obtained in publicly funded research projects. The findings and recommendations from these have meanwhile been taken into account by the operators. Where appropriate, measures have been implemented (see Chapter 3.1.3.a in conjunction with Chapter 3.1.4 and 5.1.2). | - | Thank you for your comment
DE-116 | DE - 116 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 18 | Integrated automatic monitoring takes place by means of automatic monitoring systems (particularly applicable to electrical and I&C systems), which are designed to be self-monitoring. This monitoring is integrated in the reporting concept of the nuclear power plant. The reports show deviations at an early stage before impermissible changes in the quality of the systems might occur. The independent automatic monitoring takes place by means of independent monitoring systems. The monitoring results are evaluated systematically. These systems are mainly integrated in the reporting concept of the nuclear power plant and show deviations from the operating parameters at the control room. | - | Thank you for your comment
DE-117 | DE - 117 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 19 | Good an common practice In the case of findings (failures, faults or deviations from the specified condition) measures are generally taken – such as repair, replacement, etc. – to restore the required condition (quality). In the case of relevant findings, appropriate measures (servicing, assessment, inspection, repair) are also carried out on comparable components in order to exclude common-mode failures. Since ageing degradation mechanisms often develop slowly over time, trend analyses on the long-term behaviour can be conducted based on the evaluation of the measured data and possible degradation developments on SSCs can be identified at an early stage. | - | Thank you for your comment
DE-118 | DE - 118 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 21 | For I&C components, there are several certified workshops in Germany that are allowed to repair discontinued safety-related modules. The experiences and repair reports are exchanged via the VGB. This often resulted in comprehensive remediation projects, such as the exchange of wet capacitors of whole module families. | - | Thank you for your comment
DE-119 | DE - 119 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 22 | In the case of modifications to the nuclear power plant or its operation, all affected organisational units will be involved in accordance with safety standard KTA 1402 /KTA 12/. In addition, modifications to SSCs and the operation of safety systems are generally subject to approval in Germany and are thus assessed by the nuclear supervisory authority and by any authorised experts consulted by them prior to implementation. The entirety of the measures ensures that all safety-related aspects are taken into account in planned modifications. In this respect impacts from plant modifications on the ageing management are also considered. | - | Thank you for your comment
DE-120 | DE - 120 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 30 | Regulator’s assessment of overall AMP Experiences with the application of the overall AMP in the German nuclear power plants show that ageing phenomena at the safety-related SSCs can be identified at an early stage. Remedial actions were implemented in a timely manner. | - | Thank you for your comment
DE-121 | DE - 121 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 31 | Regulator’s assessment of overall effectiveness of AMP Through the annual reporting, the assessment processes of the nuclear power plant operators are presented in a transparent and comprehensible manner. The ageing management documentation regarding the SSCs is updated continuously. The current ageing management results are assessed in a timely manner. There are no conceptual weaknesses in the ageing management process for overall ageing management. Found!!!! | - | Thank you for your comment
DE-122 | DE - 122 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 37 | The electrical operability under LOCA conditions is a special aspect of the ageing management of cables. With the above-mentioned measurands and associated monitoring methods, it is only possible to detect and asses the ageing effects from the loading of the cables by normal system operation. Cables needed for the electricity supply of electrical components or for the transmission of instrumentation and control signals under the aggravated ambient conditions of a LOCA must have the corresponding characteristics even after advanced ageing. These properties are checked during tests as part of the qualification of the cables. The temperature- and/or radiation-induced ageing of the cables caused by the loads from plant operation is already taken into account in the corresponding test specifications. | - | Thank you for your comment
DE-123 | DE - 123 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 37 | (Chapter 3.1.2.a) In addition, cable samples stored in so-called cable depositories in areas of a Konvoi-type PWR (representative for the nuclear power plants) with high radiological and thermal loads (reactor coolant line) are monitored for their ageing behaviour. At regular intervals (approximately every three years), individual cable samples are taken and the change in the relative elongation at break is used as a guide to assess the change in the polymer material. In addition, such pre-aged cable samples are subjected to electrical tests under LOCA conditions (high-pressure and high temperature steam atmosphere). The electrical operability under LOCA conditions is specified as an acceptance criterion for each cable type; this is derived from the typical applications of the cable type. The results obtained can be applied to the cables that are used in the nuclear power plants and which must fulfil the corresponding requirements. The test results are summarised in so-called service life curves. The graph of a service life curve can be used to determine the proven lifetime (relative to the cumulative radiological loading of the cable in its installation position). For this purpose, material-specific service life curves are generated from the results of the above-mentioned LOCA tests and from the ageing parameters of the specimens that have come out of the tests positive. | - | Thank you for your comment
DE-124 | DE - 124 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | In the Chapter 2.2 is stated: 'The following gives an overview of the international requirements that have been taken into account in the national regulatory framework.' and further different international requirements are stated. But stays not clear how these international requirements are implemented in the German law& regulation. Could you please give more detail about this matter. | Regulator | Germany closely follows the development of international requirements such as the IAEA safety standards and the WENRA Safety Reference Levels. Newly published international requirements are systematically compared with the German rules and regulations to identify gaps in national nuclear rules and regulations and supervisory practices. Furthermore, Experts from Germany participate in the international development of nuclear rules and regulations. On the one hand, the aim is to ensure with the help and support of the international nuclear rules and regulations best possible protection against damages and to effect a comparable further development of the national regulatory framework. On the other hand, these international developments are to make a contribution to European harmonisation.
DE-125 | DE - 125 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | In the Chapter 2.2 description about use of the IAEA regulation are described. Here the IAEA 'Safety Reports Series No 57: Safe Long Term Operation of Nuclear Power Plants, 2008' report is not mentioned. Please clearify if this IAEA report is taken into account in the national regulatory framework. | Regulator | Due to the phase out decision and legally defined shut-down dates, long term operation of NPP is not relevant for Germany.
DE-126 | DE - 126 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | Comment: The overall AMP basically is based on KTA 1403. The reference (/KTA 10/ is givven to safety standard which is issued in 2010. In the chapter 2.2 no other reference is given for KTA 1403 and could be confusing which version of stqndard is described in the text. | Regulator | The current version of KTA 1403 was published in November 2017 and is used in the NAR. The KTA 1403 from 2010 is only mentioned to describe the historical context.
DE-127 | DE - 127 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | From the scope of the overall AMP description remains unclear assignment responsibilities of the ageing management programme implenentation at NPP's. | Licensee | All work is organized and carried out in the NPPs based on an integrated management system. The associated processes define the responsibilities of all organizational units and their collaboration. The ageing-management process is controlled and coordinated by an ageing manager. The assessment of experiences regarding SSCs are performed by specially designated system engineers. The external experience feedback is also evaluated by these engineers within the established processes of the integrated management system.
DE-128 | DE - 128 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | Do the indicators are used (quality assurance) of the overall AMP to assess the effectiveness of the process? | Licensee | Explicit indicators for the ageing-management process or its results are not recorded. An essential evaluation criterion for the effectiveness of the ageing-management process are the results of the internal experience feedback.
DE-129 | DE - 129 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | In the description is stated: 'An independent ageing management programme, as implemented in nuclear power plants, does not exist for German research reactors. In the German research reactors FRM II, BER II and FRMZ, ageing management takes place within the framework of maintenance (safety standards KTA 3301 and 3501).' Are there plans in Germany the ageing management programme, as implemented in nuclear power plants, to implement in the research reactors in future? | Regulator | Currently, there are no plans for the research reactors to implement an ageing management programme as implemented in nuclear power plants. It has been shown that from the point of view of the competent nuclear licensing and supervisory authorities the entirety of the measures presented by the operators of the FRM II, BER II and FRMZ are appropriate to identify and address ageing-related degradation mechanisms at an early stage
DE-130 | DE - 130 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 15-16 | In the description is stated: "As relevant information, the following documents and sources are used to build up the knowledge base:…". Few separate documents are described other there. Please provide more detailed information about if you have processes/ procedures for the assessment/ implementation of all these documents/ results. | Licensee | All documents or groups of documents listed in this chapter are filed in analogue and often also digital form in accordance with documentation guidelines and are accessible to users. The content of the NPPs documentation and the work with this knowledge base is also defined in the processes of the integrated management system.
DE-131 | DE - 131 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 15-16 | "The criteria for compliance with the required quality regarding ISIs of SSCs are described and subject to regulatory supervision." Please provide information on which (specific) procedures/ instructions are used. | Regulator | The tests are carried out according to the KTA safety standards specific to SSCs (e.g. KTA 3201.4). The basic parameters for these tests are shown in the testing schedule in accordance with the requirements of KTA 1202 which, as a licensing document, is subject to the approval of the supervisory authority. Detailed specifications for the performance of in-service inspections are laid down in testing instructions and are reviewed by the competent regulatory authorities. Alternatively, elaborate qualification measures with accelerated irradiation of specimens are also carried out for certain components in order to demonstrate the suitability of a component also and in particular with regard to ageing effects. This applies, in particular, to properties relating to ageing mechanisms in connection with certain requirements which can only be demonstrated by destructive tests (e.g. for LOCA resistance of electrotechnical components and of components in the instrumentation and controls) (type tests according to KTA 3503/3505/3507). There is also a test programme to evaluate this suitability.
DE-132 | DE - 132 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 18 - 20 | Do the activities/ inspections are performed by 'third party certification organisations' ? If so, please give more details about that. | Regulator | Inspections, including in-service inspections, and monitoring measures are generally initiated by the operator (licensee) and subject to the supervision by an independent expert organisation. The expert organisation is commissioned by the supervisory authority.
DE-133 | DE - 133 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 22 - 23 | Do you have the requirements for evaluation of ageing analyses that are time limited? If so, please describe it. | Regulator | The German regulatory framework with respect to ageing management does not use the term time limited ageing analysis (TLAA). However, the concept is used for certain safety demonstrations (like RPV, or major components). Such demonstrations includes brittle fracture analysis procedure (KTA3201.2) or maximum allowed load cycles (KTA 3201.2).
DE-134 | DE - 134 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 22 - 23 | From the description remain unclear if regulatory does inspections on implementation of the overall AMP. If so, how often are inspections carried out? | Regulator | For the implementation of KTA 1403, a so-called basic report was prepared by the operators, which is updated annually by status reports. The basic report describes the establishment of systematic and effective ageing management, also taking into account the relevant requirements of KTA 1402 regarding management system and organisation. Based on this, the status reports report on the ageing-relevant findings in the year under review. The evaluation of these annual status reports by the authority with its authorised experts allows for the early identification of trends and sources of common-mode failures. Audits on individual aspects deepen the assessment and can lead to specific plant walkdowns or to dealing more intensively with them.
DE-135 | DE - 135 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 31 | Please provide more detailed information with the conclusions on the adequacy of the (RR) licensee's overall ageing management programme (s). | Regulator | The safety regulations for power reactors are applied mutatis mutandis to research reactors. Application depends on the hazard potential of the respective research reactor and is carried out by the nuclear licensing and supervisory authorities of the Länder in a graded approach. Accordingly, a graded approach regarding the overall requirements of the German regulations presented in the NAR is permissible for the research reactors and varies depending on the individual research reactor. For example, for the FRM II, an important aspect of the graded approach is that the hazard potential of the FRM II (only a single fuel element, lower activity inventory, no high-energy systems (p < 20 bar and T < 100°C) is decisive for the review and assessment of the facility. Safety is always the top priority for the review and assessment of research reactors. Thus, in this respect, there is no difference in supervision between research reactors and nuclear power plants.
DE-136 | DE - 136 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | Section 2.3.1.a confirms that KTA 1403 applies to mechanical components and systems, electrical, instrumentation and control and structural elements. The section also provides examples of structural elements, confirming that this term includes buildings, partial structures, structural systems and components. Please could you confirm whether flood defences are included within the requirements of KTA 1403. | Regulator | Safety standard KTA 1403 applies to the procedures of ageing- management regarding the safety-related Technical Facilities that are specified in the licensing documents and operating instructions of light water reactors still in operation. In addition KTA 2207 provides further guidance on the design and ISI of flood defences.
DE-137 | DE - 137 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | Section 2.3.1.a confirms that KTA 1403 applies to mechanical components and systems, electrical, instrumentation and control and structural elements. Please could you explain how ageing of equipment and facilities provided for emergency response at NPPs is considered within the framework established by KTA 1403. | Licensee/ Regulator | According to KTA 1403 the safety standard applies to the procedures of ageing management regarding the safety-related technical facilities – including the respective auxiliary and operating media – that are specified in the licensing documents and operating instructions of light water reactors still in operation. According to KTA Basic Principles the KTA rules establish requirements that "...shall be met with regard to precautions to be taken in accordance with the state of science and technology against damage arising from the construction and operation of the plant (Sec. 7, para. (2), subpara. (3) Atomic Energy Act - AtG)". Generally speaking it applies to all equipment needed for DID levels 1 to 3, i.e. equipment needed for DBA (safety systems). Mobile equipment for DID level 4 (DEC or BDBA) measures is generally not covered by KTA rules. This mobile equipment is typically stored in well protected areas and is not subjected to operational loads like radiation or high temperatures. Generally mobile equipment is also included in the periodic test program. Mobile equipment specific ageing issues have not been identified.
DE-138 | DE - 138 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | Section 2.3.1a describes the WLN Information Notice system used to inform operators of learning identified from events at German or foreign nuclear facilities. Please could you summarise the instances where this system has been used (in recent years) to support ageing management? | Licensee/Regulator | Examples of information notices which could support ageing management are: - WLN 2014/01: broken fuel assembly alignment pins - WLN 2014/05: broken springs of flow restrictor assemblies - WLN 2014/09: aging degradation of heat exchanger tubes - WLN 2015/04: failure of a draining line due to uniform corrosion - WLN 2015/09: indications of hydrogen embrittlement / cracking on stud screws - WLN 2016/03: mechanical fatigue of thermal sleeves (in injection nozzles of the residual heat removal system into the main coolant line) - WLN 2016/05: broken water channel of a BWR fuel assembly - WLN 2016/07: wall thinning of a vent line due to fretting
DE-139 | DE - 139 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 14 | Section 2.3.1a states that KTA1403 requires that for, some groups of SSC, higher ageing management requirements apply than for others. Please explain which groups of SSC's merit additional attention and the key differences in the requirements for SSCs of principal importance to nuclear safety and other SSCs. | Licensee | Ageing-management in the context of the KTA 1403 is only carried out for safety-related SSCs. For mechanical equipment special categories are defined, which require different procedures in the context of the aging management according to KTA 1403. This is related to groups of mechanical components, where a failure mode according to the safety demonstration is excluded as part of the design precautions. These include e.g. the reactor pressure vessel, reactor coolant pipes, the main steam pipes and the feed water pipes as far as rupture preclusion is required for these components.
DE-140 | DE - 140 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 19 | Section 2.3.3.a highlights examples of long term monitoring systems in service at German NPPs. Please explain how the fatuge monitoring system (FAMAS) is used to monitor the intergrity of SSCs and inform decisions regarding component repair/replacement. | Licensee | FAMOS is an example of fatigue monitoring systems. By positioning a large number of additional measuring points, parameters for the system status and the operational behaviour of SSCs are recorded. Therefore phenomena for example temperature stratification and unusual temperature gradients can be determined. From the evaluation of these measurement results special information or measures are deduced, e.g., assessments of the fatigue state of components, technical adjustments or design changes.
DE-141 | DE - 141 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 20 | Section 2.3.3a summerises the actions taken analyse and trend complonnt failures, faults and deveiations. Please expain how this data is evaluated against relaiablity claims for SSCs within the safety case. | Licensee | The goal of plant design and preventive maintenance is that increased failure rates don't occur. If there are indications of increasing failure rates, the concept of preventive maintenance is adapted or components are replaced preventively.
DE-142 | DE - 142 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation | 24 | Section 2.4a descibes how VGB coordinates and promotes the exchange of operatating experaince, relvent to ageing management. Please descibe how research reactor operators are able to access relevent learning from VGB. | Licensee | FRM II is a member of VGB and participates in various working groups (e. g. KSB, training). As part of its membership, FRM II has access to the VGB database in some cases. There is informal direct interaction between the relevant parties involved. . In case a RR is not member of VGB there is no direct exchange. The exchange of operating experience is ensured vie WLN and KTA.
DE-143 | DE - 143 | General AMP expert group | Germany | 02. Overall Ageing Management Programme requirements and implementation |  | FRMII, BER II and FMRZ research reactors: Do all the research reactors within the scope of the TPR have an ISI programme specified in their license? What kind of SSC requires an authorized expert to perform an inspection or a test? Are they similar for the three research reactors? Is the need to involve an authorized expert to perform an inspection or a test determined by the regulator? What is the amount of this kind of tests (which involve an authorized expert) compared to the routine inspections? | Regulator | For the FRM II, for example, three manuals have been developed, reviewed and assessed for in-service inspections (ISI) within the framework of the licensing procedure: the testing manual and the checklist according to KTA 1202 for tests according to nuclear law, the manual for conventional tests (HKP) and the manual for internal tests (HIP). The HKP and HIP have been reviewed by the authorised expert within the framework of the licensing procedure and must be sent to the supervisory authority and the expert for information (licensing provision). Changes to the checklist must be submitted to the supervisory authority and the authorised expert consulted according to § 20 AtG and require approval by the supervisory authority (licensing provision). The authorised experts according to § 20 AtG are involved in the ISIs according to the checklist (testing manual) and conventional experts in the tests according to the HKP. The BER II and FRMZ basically apply the same approach.
DE-144 | DE - 144 | Cables expert group | Germany | 03. Electrical cables | 33 | Is the evolution of insulation resistance with time (e.g. polarization index, dielectric absorption ratio …) being measured and what are the acceptance criteria used ? | Licensee | Acceptance criteria are given by standards or the manufacturers specifications. Trending of measuring results are possible if necessary.
DE-145 | DE - 145 | Cables expert group | Germany | 03. Electrical cables | 33 | Considering that only neutron flux instrumentation cables were addressed in the NAR for Research reactors, please provide more information on the analysis of cable ageing mechanisms in relation to research reactors conditions that support this choice, i.e. that the ageing of other cables is managed as appropriate. | Licensee/Regulator | The required tests are carried out and evaluated within the scope of the in-service inspections and measures derived where necessary. If required according to the testing manual, the tests are carried out in the presence of experts in the nuclear or conventional sector.
DE-146 | DE - 146 | Cables expert group | Germany | 03. Electrical cables | 35 | Are there any measures implemented to protect the cables against rodents attacks. | Licensee | No specific measures necessary, cables are situated in closed building-structures.
DE-147 | DE - 147 | Cables expert group | Germany | 03. Electrical cables | 37 | Observation from the visual inspection could initiate further measures. Are there any predefined criteria in this respect? | Licensee | There are no predefined criteria for visual inspections on cables.
DE-148 | DE - 148 | Cables expert group | Germany | 03. Electrical cables | 37 | To which extent is the thermography used to detect hot zones near the cable terminations, and what is the periodicity of such assessments ? | Licensee | Thermography is not used as instrument of periodic testing-procedures. Thermography is used as an additional test when triggered or as random sample-test. The thermal stress at cable trays depends on the load distribution during operation. Therefore it would be difficult to compare the result of periodic thermography-tests. Furthermore thermal limit values of thermography have to be defined for each cable type.
DE-149 | DE - 149 | Cables expert group | Germany | 03. Electrical cables | 37 | Regarding thermographic investigation, is there a requirement for a periodic assessment of all cables to identify possible hot spots? Was a thermographic " baseline" established at the plant's start up (the report said that " if the cables are designed in accordance with the rules, there should be no hot spots- was that verified?) | Licensee | Thermography is not used as instrument of periodic testing-procedures. In German NPPs the electrical components are designed to operate at low voltage levels (70-75%) which means that the thermal layout for cables is robust. Therefore ageing due to self-heating is not main-aspect of the AM because of the conservative cable-calculation. This was verified during the licensing-process.
DE-150 | DE - 150 | Cables expert group | Germany | 03. Electrical cables | 38 | For RR cables, apart from checking the conditions and manufacturer's specifications, are there are any other means of determining the aging phenomena? | Licensee | At FRM-II, BER II and FR MZ, ageing is dealt with within the framework of the in-service inspections. In this context, e.g. insulation resistance, corrosion, breakages, etc., are examined, evaluated and appropriate measures derived where necessary.
DE-151 | DE - 151 | Cables expert group | Germany | 03. Electrical cables | 38 | The cables that are potentially subject to LOCA environment are tested and qualified for such an environment. Are there separate requirements for cables that might be subject to HELB, i.e. the harsh environmental conditions but without the radiation effect? | Licensee | In Germany no cable-types are especially designed or qualified for HELB-conditions. If cables used with HELB-requirements, cable-types qualified for LOCA-conditions are installed.
DE-152 | DE - 152 | Cables expert group | Germany | 03. Electrical cables | 39 | Under which conditions (temperature/irradiation) are K1-cables in deposit and when were these deposit put in place for each type of K1-cables ? | Licensee | Conditions are approximately temperature 40 °C and a dose-rate of approximately 3,5 kG/a. The cable-depository-system put im place in 1980.
DE-153 | DE - 153 | Cables expert group | Germany | 03. Electrical cables | 39 | The cables from deposits are submitted to tensile test on 3 years interval. Are the results of those text compared with the results of the tensile test results implemented at the initial qualification and what are the lessons learned? | Licensee | Yes, the results of these tests are compared with the results of the tensile test results implemented at the initial qualification. The results are included in the material-specific service-life-curves.
DE-154 | DE - 154 | Cables expert group | Germany | 03. Electrical cables | 41 | The TPR report seems to suggest that the cables in the depository would not be subject to the dose of up to 150 kGy, which is necessary to prove the qualification of cables subject to LOCA. IS this correct? | Licensee | The radiation applied in the deposits are only a part of radiological pre-ageing before a LOCA-test. Before the LOCA-test will be performed the deposit cables will get a radiological pre-ageing which cover the radiological stress during an LOCA event.
DE-155 | DE - 155 | Cables expert group | Germany | 03. Electrical cables | 42 | The testing of insulation resistance was introduced for the PVC-insulated cables " in connection with their replacement". Was such a testing introduced prior to the replacement (and therefore served as the basis for the decision making related with the replacement) or the testing mentioned applies to the replacement cables? . | Licensee | Replacement of PVC-insulated high-voltage-cables can be a result of the insulation-tests. Conservative insulation resistance limits are given.
DE-156 | DE - 156 | Cables expert group | Germany | 03. Electrical cables | 42 | The indications and failures identified in the cables are low, and due to random failures. Was there root cause analysis undertaken to corroborate this findings? | Licensee | Root cause analysis was undertaken in case of new phenomena on cables .
DE-157 | DE - 157 | EC | Germany | 01. General information | P11 | Question: Before KTA 1403 (2010) which framework was used for ageing management? VGB97? | Regulator | Before KTA 1403 has been released, the specific requirements for maintenance, surveillance and inspections defined in other KTA standards have been applied.
DE-158 | DE - 158 | EC | Germany | 01. General information | P13 | "the degradation mechanisms that are to be considered for the individual nuclear power plant according to KTA1403 have been catalogued and systematically characterised" Question: Are the catalogue of each individual power plant shared with other NPPs? How? | Licensee | As part of the cooperation within the VGB, the exchange of plant-specific experiences takes place in various working groups (e.g., AG "Component Integrity", "Machine and Process Engineering", "Electrical and Control Engineering").
DE-159 | DE - 159 | EC | Germany | 01. General information | P13 | Status reports on AMP "these concepts were summarised in basic reports for each plant and their effectiveness assessed annually…" Questions: Assessment performed by whom? Only internal or also external assessment? | Licensee/Regulator | The evaluation is carried out by the operator and presented to the supervisory authorities.
DE-160 | DE - 160 | EC | Germany | 01. General information | p15/16 | Questions: What is the specific role of the regulatory body (national/regional) for ageing assessment? Inspections ? Annual assessment of the yearly report? | Regulator | The role of BMU and nuclear supervisory authorities of the Länder is described in section 2.6 of the NAR.
DE-161 | DE - 161 | EC | Germany | 01. General information | p16 | Ageing assessment, Knowledge base: "…this information is collected with the use of databases and assessed". Question: By whom? | Licensee/Regulator | Each operator or NPP has its own, plant-specific knowledge base. As a rule, the gathering and evaluation is carried out by the plant operator. The plant manufacturer or external experts are consulted as needed. In electrical engineering and control technology, a database was created jointly by the VGB plant operators, to which all operators have access.
DE-162 | DE - 162 | EC | Germany | 01. General information | P20 | Research reactors: Question: It seems that the monitoring activities are not specifically dedicated to the ageing management? | Licensee/Regulator | At the German research reactors, ageing management takes place within the scope of maintenance (in-service inspections, plant inspections) as described in the NAR, following safety standard KTA 1403 "Ageing Management for Nuclear Power Plants" using the aspects of ageing management mentioned therein as a basis to identify a possible need for modification and for ensuring compliance with the state of the art in science and technology.
DE-163 | DE - 163 | EC | Germany | 01. General information | P22 | "the evaluation and analysis of experience feedback…take in place in German power plants on the basis of a structured process" "The entire ageing management process…reviewed and adapted on the basis of a structured process" Questions: Are these processes structured the same way for each NPPs? Could you provide more details of this process? | Licensee | According to KTA 1402, an integrated management system has to be installed in the NPPs. It describes and controls the aspects of nuclear safety, quality management, environmental and energy management, occupational health and safety as well as explosion protection. The management system is described in a manual, which includes all processes in the NPPs. Due to different organizational structures, NPPs have different organization and responsibilities. The ageing-management process is build up as a classic PDCA cycle. Based on the structured knowledge base for SSCs, measures are planned, carried out, evaluated and, if necessary, corrected to monitor and maintain the functional features of SSCs.
DE-164 | DE - 164 | EC | Germany | 01. General information | P22/23 | Role of the nuclear authority in the review and assessment of the AMP Questions: How is the nuclear authority involved in the review and assessment of the AMP? Are AMPs specifically assessed? Is each NPP assessed separately? Frequency of external assessment of the AMPs? Assessment by international organisation (IAEA)? | Regulator | For the implementation of KTA 1403, a so-called basic report was prepared by the operators, which is updated annually by status reports. The basic report describes the establishment of systematic and effective ageing management, also taking into account the relevant requirements of KTA 1402 regarding management system and organisation. Based on this, the status reports report on the ageing-relevant findings in the year under review. The evaluation of these annual status reports by the authority with its authorised experts allows for the early identification of trends and sources of common-mode failures. Audits on individual aspects deepen the assessment and can lead to specific plant walkdowns or to dealing more intensively with them.
DE-165 | DE - 165 | EC | Germany | 01. General information | P24 | Research reactors: "The ageing management of the operators of the research reactors is considered in the context of the periodic safety review in accordance with the technical specification quoting WENRA Safety Reference level I2.2 …" Questions: Does the periodic safety review include a chapter specifically addressing ageing management? Since when have periodic safety reviews been performed at research reactors in Germany? | Regulator | For the German research reactors, periodic safety reviews are carried out in analogous application of the corresponding regulatory guidelines of the Federation and the Länder. Here, the ageing analysis of SSCs is part of the deterministic safety status analysis. For example, the first PSR for the FRM II was carried out 10 years after commissioning. It does not contain a specific chapter addressing ageing management. However, reference is made to the results of tests and analyses in the context of ageing. These relate e.g. to the capacity of batteries or the overall annual evaluation of all in-service inspections. Since 2010, all research reactors are required by law to carry out a PSR every ten years (according to § 19a(3) of the Atomic Energy Act – AtG). Larger facilities (FRM II and BER II) have already been required before to carry out periodic safety reviews according to specific requirements in the license.
DE-166 | DE - 166 | EC | Germany | 01. General information | P27 | "In German reactors, there is no independent ageing management programme as it is implemented in the nuclear power plants. However, the aspects of ageing management referred in KTA1403 are implemented within the framework of maintenance" Has it been demonstrated that this is sufficient (external assessment)? Can we say that the ageing management is based on a structured and comprehensive approach for research reactors? | Regulator | The safety regulations for nuclear power plants are applied mutatis mutandis to research reactors. Application depends on the hazard potential of the respective research reactor and is carried out by the nuclear licensing and supervisory authorities of the Länder in a graded approach. Accordingly, a graded approach regarding the overall requirements of the German regulations presented in the NAR is permissible for the research reactors and varies depending on the individual research reactor. For example, for the FRM II, an important aspect of the graded approach is that the hazard potential of the FRM II (only a single fuel element, lower activity inventory, no high-energy systems (p < 20 bar and T < 100°C) is decisive for the review and assessment of the facility. Safety is always the top priority for the review and assessment of research reactors. Thus, in this respect, there is no difference in supervision between research reactors and nuclear power plants.
DE-167 | DE - 167 | EC | Germany | 01. General information | P8 | "ensuring the testability of the SSCs by means of appropriate design requirements, e.g. grinding on inner and outer surfaces of welds, accessibility, irradiation of material…" Question: Does it mean that most of the SSCs are accessible for test and monitoring? | Licensee | Yes.
DE-168 | DE - 168 | EC | Germany | 02. Overall Ageing Management Programme requirements and implementation | 12 | Have the WERNA Safety Reference Levels, including Issue I “Ageing Management” of the WENRA SRLs been formally adopted in the German national nuclear safety legislation in a binding form? | Regulator | Issue I “Ageing Management” of the 2014 WENRA Safety Reference Level has been fully implemented in the Geman regulatory framework.
DE-169 | DE - 169 | EC | Germany | 02. Overall Ageing Management Programme requirements and implementation | 15 | At what level of the regulatory framework, e.g. ordinance, guidance or plant level document, are the acceptance criteria for aging effects/acceptance criteria to ensure that SSCs can maintain their intended function/acceptance criteria for taking corrective action specified? | Regulator | This is different and depends on the topic. Acceptance criteria are defined in the operating limits and conditions as well as in technical specifications, in the relevant industry standards and from the manufacturer's specifications (for cables) and in KTA (for RPV).
DE-170 | DE - 170 | EC | Germany | 02. Overall Ageing Management Programme requirements and implementation | 15 | Sampling and testing of relevant SSCs of the power reactors which have recently been shutdown definitively and subject to decommissioning could be of value for obtaining further data on ageing effects, that could yield useful information for similar reactors still in operation in Europe and worldwide. In the scope of research activities to support ageing management, are there plans to conduct such sampling and testing? | Licensee | No. Compared with international practice Germany shuts down its nuclear power plants after a relatively short service life (~32a). We do not expect new findings from the investigations of the SSC of shut-down reactors for the lifetime left.
DE-171 | DE - 171 | EC | Germany | 02. Overall Ageing Management Programme requirements and implementation | 17 | Section 2.3.1 lacks clear information on the methods used for identifying SSCs to be included in the scope of an overall AMP, as well as how acceptance criteria for ageing are established. In particular, are probabilistic safety analyses or risk-informed methods used to identify SCCs to include in the scope? | Licensee | All safety-related SSCs are in the scope of the ageing-management. The scope is derived from the operating documents. PSA methods are not used for the selection of SSCs.
DE-172 | DE - 172 | EC | Germany | 02. Overall Ageing Management Programme requirements and implementation | 29 | The regulator's assessment declares that there are no conceptual weaknesses in the aging management process for overall ageing management. Are there improvements identified in the frame of operational experience of the AMP? | Regulator | Yes, potential for improvement was identified and modifications have been implemented in the respective nuclear power plants. Modifications included optimising the operating mode, adjusting maintenance intervals and optimising the materials used, as well as routine programmes for preventive replacement of individual components or parts.
DE-173 | DE - 173 | EC | Germany | 02. Overall Ageing Management Programme requirements and implementation | 30 | How is the effectiveness of the AMP assessed? Are there criteria or key performance indicators specified for assessing the effectiveness of the ageing management programme, and as part of a quality management system as per the attributes of an effective ageing management programme NS-G-2.12 and its revision. | Licensee | Explicit indicators for the ageing-management process or its results are not recorded. An essential evaluation criterion for the effectiveness of the ageing-management process are the results of the internal experience feedback.
DE-174 | DE - 174 | EC | Germany | 03. Electrical cables | 39 | The section 3.1.3.a provides only a list of ageing management activities. What are the frequencies and acceptance criteria of the listed inspection and testing activities? | Licensee | The activities are part of the periodic testing programs during the lifetime of the NPP. Acceptance criteria are given by standards or the manufacturers specifications.
DE-175 | DE - 175 | EC | Germany | 03. Electrical cables | 37, 39 | Does the cable sample depository contain all cable types used in harsh environmental conditions at German NPPs? Is it representative also for BWRs? | Licensee | The cable sample depository contains all safety-related standard-cables (electrical and I&C). Special cables are added to the depository for pre-ageing during qualifying-procedures. It is representative for BWR.
DE-176 | DE - 176 | EC | Germany | 03. Electrical cables | Generic 32-46 | Comment: The NAR should list the groups of electrical cables included within the AM. Such list cannot be found. | Licensee | Categories of cables are defined in 3.1.1a. Insulation-materials are listed in 3.1.2a
DE-177 | DE - 177 | EC | Germany | 05. Reactor Pressure Vessels | Chapter 5.1.1.a , page 68 | Correct KTA 1430. It should be KTA 1403. | - | Thank you for this comment.
DE-178 | DE - 178 | EC | Germany | 05. Reactor Pressure Vessels | Chapter 5.1.1.b, page 70. Chapter 5.1.2.b, page 77. Chapter 5.1.3.b, page 87. Chapter 5.2.b, page 88. Chapter 5.3.b, page 90. | An explanation should be given why all these chapters are not applicable to the research reactors. For example, it may be the case that the vessel is not a pressure vessel. | Licensee/Regulator | The research reactors FRM-II, BER II and FMRZ are swimming pool reactors and do not have a reactor pressure vessel. Thus, the question as regards ageing management does not apply in these cases.
DE-179 | DE - 179 | EC | Germany | 07. Concrete containment structures | 105 | According to p105 'all relevant ageing phenomena of concrete structures are first manifested by cracking. The general condition of the concrete surfaces with regard to cracks, spalling, and damage is visually checked during regular inspections.' In the case of corrosion of reinforcement steel, cracking would only be observed after corrosion has already progressed to a certain extent. Would this not give rise to loss of strength and/or difficulties to repair? Are there any provisions in the inspection programme to detect issues having potential to lead to corrosion of the reinforcement steel before it occurs? | Licensee | In section 7.1.2a is written: " As long as crack widths are small (depending on the component and the ambient conditions: 0.2 mm to 0.5 mm), a corrosion-induced reduction of the planned service life of the relevant component is not expected." This means that corrosion processes are detected in a very early stage, long before any significant damage to the reinforcement steel. These small cracks would lead to further investigations.
DE-180 | DE - 180 | EC | Germany | 07. Concrete containment structures | 105 | Are pressure tests and integral leak tightness tests performed at the German NPPs and RRs? What are the acceptable leak rates? Is there any noticeable deterioration of the leak rates with ageing of the plants? | Licensee/Regulator | Yes, there are integral pressure tests for NPP in combination with leak tightness tests performed. The tests are carried out in accordance to KTA 3405 "Leakage Test of the Reactor Containment Vessel" and KTA 3401.4 "Steel Containment Vessels; Part 4: In-service Inspections". The FRM-II has no concrete containment "designed to withstand the pressure associated with a significant leakage of coolant from the reactor cooling system … [or] … a concrete structure that surrounds [it] …[nor a] a (self-standing) steel containment designed to withstand the pressure associated with a significant leakage from the reactor cooling system"; only such systems had to be examined according to the WENRA "Technical Specification for the National Assessment Reports". Since the FRM-II does not have a containment as referred to therein, there are no tests that relate to these parameters.
DE-181 | DE - 181 | EC | Germany | 07. Concrete containment structures | 107 | It is written 'The secondary concrete shell of the BWR is protected from the weather by a facade construction and thermal insulation, so that regular checking can be dispensed with here'. Are there any checks performed to ensure that the facade is functioning correctly and that there is no ingress of elements of the weather that could give rise to ageing degradation of the concrete? | Licensee | Within 10-year regular visual inspection of the building, also facade elements are inspected. There is no indicator that the facade elements are not working proper.
DE-182 | DE - 182 | EC | Germany | 07. Concrete containment structures | 107 | There are no provisions in the ageing management programme for testing the pre-stressing systems of the BWR containments for any unexpected degradations that could lead to loss of adequate tensioning. It is mentioned that a one-off test was performed at one plant in 2002 where strain measurements were carried out. Could you give some more details of this test. Are there any plans to perform similar tests at other plants to confirm the expected behaviour of the pre-stressing systems? | Licensee | Please see answer to questions DE-15 and DE-22. There is just one NPP with a pre-stressed concrete containment in operation. | ref to DE-15 & DE-22
DE-183 | DE - 183 | EC | Germany | 07. Concrete containment structures | 107, 109 | It is written 'All structures are subject to a regular visual inspection in accordance with KTA 1403' (p107) and 'Some elements, such as visual inspections and settlement measurements, have been performed and documented at the plants since commissioning.' (page 109). Please could you provide more information on the frequency of these inspections and the extent of the visual inspections. | Licensee | The regular visual inspections in accordance with KTA 1403 have to be done once in ten years. Within these inspections, the crack patterns, including the crack width and length on the component surface, are determined and documented. The documentation of the position and orientation in the structural element is done systematically. Additional visual inspection on containment coats are done every two years. Furthermore for settlement measurements see question DE-74. | ref to DE-74
DE-184 | DE - 184 | EC | Germany | 07. Concrete containment structures | General | Are there parts of the containment structures included in the AMPs for which potential degradation mechanisms have been identified but which are not accessible for inspection? How is the demonstration made for these structures that no degradation has occurred that can affect their ability to perform their required functions? | Licensee | Structural elements are sufficiently accessible to judge the impact of all possible ageing mechanisms by visual inspections.

## IT_Figs & Refs
copied from file LENA_references.pdf
copied from file RC-1_figures ageing.pdf

## FR_Figs & Tables
Table 1 | Figure 1
Table 2
NOTE: "the French Excel file only contains 232 answers to the 233 questions posed to France because Slovenia had twice posted the same question on chapter 4 - section 4.1.2 - page 105 (“What R&D programmes are used, if any ?”), that only requires one answer."